| Sl. No. | Reference Clause | Bidder's Query | POWERGRID REPLY |
| --- | --- | --- | --- |
|  | SECTION- PROJECT_MGIS-113 | SECTION- PROJECT_MGIS-113 Please clarify the interface between protection panel on mobile substation and SAS panel on existing substation is not contractor’s scope. | Interface between protection panel on mobile substation and SAS panel on existing substation is not under present scope. |
|  |  | Annexure-I MGIS-SLD Please clarify whether it is acceptable that CT would be placed right in front of and behind of CB like DS/ES-CT-CB-CT-DS/ES. | Placement of CTs adjacent to CB is also acceptable. |
|  |  | VOLUME II-P3 –TECHNICAL SPECIFICATIONS Kindly provide detailed technical specifications for Container . | Bidder to quote as per requirement of Technical Specification. |
|  | Vol-II/Section-Project/Sl. no. O/Trailer/Page no. 8of 16 | We have got the inputs from renowned trailer manufacture that all the prime movers / puller jeep has got the pneumatic brake connection and airline couplings are easier to attach and detach, compatibility is very easy and Pneumatic Brake is used in all heavy load vehicles. In this regard, we request you to kindly amend the breaking system as Pneumatic. Kindly Confirm. | Pneumatic type Trailer Brakes also acceptable. |
|  | Registration & Permit | We understand that Trailer registration & permits shall be in the scope of M/s PGCIL. Kindly Confirm. | First time Trailer Registration & permits (in the name of POWERGRID) is in the scope of contractor. POWERGRID shall provide necessary document for registration & permits. |