| Sl. No. | Reference Clause | Bidder's Query | POWERGRID REPLY |
| --- | --- | --- | --- |
|  | SECTION- PROJECT | We understand that Mixed Technology Gas Insulated Switchgear is acceptable. Please clarify whether the AIS-type surge arrester on both sides is acceptable, not assembled on GIS. | In respect of Mixed Technology Switchgear, please refer Section Project clause No. 2-I-a. AIS-type surge arrestor not envisaged under present scope. |
|  |  | For transportation, please clarify SF6/Air bushing could be delivered on separate packing, not mounted on GIS. | SF6/Air bushings shall remain pre-mounted during transportation of MGIS bay. Refer clause 2 of Section Project. |
|  |  | The number of axles on the trailer could be decided as per payload on the trailer and allowable maximum weight per Axles. Please clarify allowable maximum weight per Axles on trailer. | Allowable maximum weight per Axles shall depend upon the MGIS bay configuration (GIS assembly and trailer) offered by the bidder. |
|  |  | Please clarify whether the Flat-bed trailer is acceptable, not low-bed trailer. | Bidder to quote as per requirement of Technical Specification. |
|  |  | Please clarify whether multi-leaf or air suspension type trailer is acceptable, not Hydraulic. | Bidder to quote as per requirement of Technical Specification. |
|  |  | Regarding the AC/DC converter, there is no requirement in detail. Please clarify the one battery and one battery charger could be acceptable, not redundant system. | Bidder to quote as per requirement of Technical Specification. Battery and Battery charger not envisaged under present scope. |
|  |  | We understand that allowable dimensional Limits for transportation is 12m(L) x 3m(W) x 5m(H) as following. However, please clarify whether SF6/air bushing part should be considered for limit length 12m. | The specified dimensional limits are for complete MGIS bay including SF6/air bushing. |
|  |  | Regarding Air Conditioning System, there is no requirement for the containerized room so the vendor’s standard would be proposed. Otherwise, please clarify the detailed requirement for the containerized room. | Bidder to quote as per requirement of Technical Specification. |
|  |  | Regarding Fire Protection System, there is no requirement for the containerized room so the vendor’s standard would be proposed. Otherwise, please clarify the detailed requirement for the containerized room. | Bidder to quote as per requirement of Technical Specification. |
|  |  | Regarding the lighting system, there is no requirement for the containerized room so the vendor’s standard for the lighting system would be proposed. Otherwise, please clarify the detailed lighting requirement including the emergency system for the containerized room | Bidder to quote as per requirement of Technical Specification. |
|  |  | The Line protection and transformer protection is required but there is no information about SAS and RTU. Please clarify whether the RTU or SAS panel is not included for this project. Otherwise, please provide detail information about RTU or SAS. | SAS and RTU not envisaged under present scope. |
|  | Section-III/BDS/Sl. No. 44 | We would like to bring in your kind notice that considering scope composition we required minimum 12 Months from the date of NOA for Ex-Works readiness & 3 Months for transportation due to route hindrance. Considering above, we request you to kindly amend completion period as 15 Months from the date of NOA, for enabling us to participation in this bid | Refer Amendment No-I |