## Service BoQ for empanelling
Bill of Material
S.No | Item Description | Unit | Qty
A | Route Alignment,Survey & Soil investigation
1 | Route Allignment | kms | The applicable quantity shall be decided at the time of Finalization of Individual Tenders to be floated at a later stage among the Empaneled Agencies.
2 | Detailed survey including profiling and tower spotting using mordern survey techniques. | kms
3 | Check Survey | kms
4 | Detailed Soil Investigation: All kinds of soils except Fissured rock and hard rock | EA
B | Excavation
1 | WET soil | M3
2 | WFR Soil | M3
3 | DRY soil | M3
4 | DFR soil | M3
C | Concreting and Reinforcement steel
1 | Concreting(including all associated works related to foundation not covered in excavation & reinforcement steel works: concreting(1:1.5:3) | M3
2 | Concreting(including all associated works related to foundation not covered in excavation & reinforcement steel works: Lean concreting(1:3:6) | M3
3 | Reinforcement Steel:Supply & Placement | MT
D | Installation
1 | Installation of stub including Bolts & Nuts :for normal towers using template | MT
2 | Erection of various types of towers, tower extensions, (complete), Bolts & nuts, hangers, D-shackles, step bolts, pack washers, etc. including tack welding& supply & application of zinc rich paint : Single ckt/Double ckt/Multi ckt towers | MT
3 | Installation of Earthing of towers:C P earthing | SET
4 | Installation of Earthing of towers:Pipe type earthing including rod type earthing | Set
E | Tower Accessories
1 | Danger plate | EA
2 | Number plate | EA
3 | Phase plate (Set of three) | SET
4 | Circuit plate (Set of two) | SET
5 | Anticlimbing device) | EA
6 | Bird Guard | SET
F | Stringing
1 | Installation of Insulator strings complete with arcing horns & necessary hardware, installing & stringing of conductor including fixing of conductor accessories, installing & stringing of earthwire/OPGW including fixing of earthwire/OPGW accessories for 765/400/200kV Single Ckt/Double Ckt/Multi Ckt tower with Twin/Quad/Hexa conductor | KM
2 | Power Line crossing Under Live Line Conditions(765/400/200kV Single Ckt/Double Ckt/Multi Ckt tower with Twin/Quad/Hexa conductor) | Each
3 | Instllation of OPGW Joint Box (including Splicing & Testing ) 24 fibres-Joint Box Testing | Each
G | De-Stringing of Existing Line and transportation to store for 765/400/200kV Single Ckt/Double Ckt/Multi Ckt tower with Twin/Quad/Hexa conductor | KM
1 | Installation of Insulator strings complete with arcing horns & necessary hardware, installing & stringing of conductor including fixing of conductor accessories, installing & stringing of earthwire/OPGW including fixing of earthwire/OPGW accessories for 765/400/200kV Single Ckt/Double Ckt/Multi Ckt tower with Twin/Quad/Hexa conductor | KM
2 | Power Line crossing Under Live Line Conditions(765/400/200kV Single Ckt/Double Ckt/Multi Ckt tower with Twin/Quad/Hexa conductor) | Each
3 | Instllation of OPGW Joint Box (including Splicing & Testing ) 24 fibres-Joint Box Testing | Each
H | Installation of Following items for Aviation requirements
1 | Span Markers | Nos
2 | Obsturction Lights 1 Med+2 Low intensity | SET
3 | Obsturction Lights 1 Med+4 Low intensity | SET
4 | Aviation Painting of Towers (Including Paint supply) | MT

## TS-244-251_Bottom (hidden)
TOWER SCHEDULE
400kV S/C LINE HOSUR-SALEM LINE
SLNO | AP NO | TOWER TYPE | ANGLE | SPAN | Section Length (m) | Section Chainage (m) | Wind Span (m) | Adjacent Span |  |  | Weight Span (Cold) |  |  | Weight Span (Hot) |  |  | Major Crossings (with in 23m either side from CL)/Remarks | Easting | Northing | Elevation | Twr Extn
[8 empty] | Left | Right | Total | Left | Right | Total | Left | Right | Total
| TWR 244 | D+0 | 0°00'00" |  |  |  | 194 | 0 | 388 | 388 | 0 | 209.7359 | 209.7359 | 0 | 205.4746 | 205.4746 |  | 179272.959 | 1375482.626 | 589.709
|  |  |  | 388 | [12 empty] | 11kV LINE, LT LINE, NALA |  |  |  |  | Formula Check
| TWR 245 new | DA+0 |  |  |  |  | 319 | 388 | 250 | 638 | 178.2641 | 100.1146 | 278.3787 | 182.5254 | 106.8535 | 289.3789 |  | 179088.356 | 1375164.044 | 586.757 | 0 | 388 | OK
|  |  |  | 250 | [12 empty] | METALLED ROAD, LT LINE
| TWR 246 new | DD+3 | 5°10'08"(LT) |  | 638 | 638 | 247.5 | 250 | 245 | 495 | 149.8854 | 116.0082 | 265.8936 | 143.1465 | 117.7662 | 260.9126 |  | 178953.148 | 1374930.706 | 586.765 | 3 | 250 | OK
|  |  |  | 245 | [12 empty] | NALA, RING ROAD
| TWR 247 new | DD+6 | 48°24'59"(LT) |  | 298 | 936 | 365.5 | 245 | 486 | 731 | 128.9918 | 274.5517 | 403.5436 | 127.2338 | 266.0076 | 393.2414 |  | 178827.608 | 1374660.516 | 584.534 | 6 | 245 | OK
|  |  |  | 486 | [12 empty] | METALLED ROAD, LT LINE, 11kV LINE
| TWR 248 new | DD+6 | 6°09'11"(LT) |  | 381 | 1317 | 368 | 486 | 250 | 736 | 211.4483 | 145.8481 | 357.2964 | 219.9924 | 140.2025 | 360.1949 | RING ROAD, 11kV LINE, LT LINE | 178979.559 | 1374310.969 | 577.12 | 6 | 486 | OK
|  |  |  | 250 | [12 empty] | RING ROAD, LT LINE, 11kV LINE
| TWR 249 new | DD+6 | 3°35'45"(RT) |  | 295 | 1612 | 293 | 250 | 336 | 586 | 104.1519 | 227.0441 | 331.196 | 109.7975 | 211.0551 | 320.8526 |  | 179125.714 | 1374054.193 | 574.6 | 6 | 250 | OK
|  |  |  | 336 | [12 empty] | METALLED ROAD
| TWR 250 New | A+0 |  |  |  |  | 339 | 336 | 342 | 678 | 108.9559 | 184.7582 | 293.7141 | 124.9449 | 181.0325 | 305.9775 |  | 179273.187 | 1373752.528 | 571.008 | 0 | 336 | OK
|  |  |  | 342 | [12 empty] | NILL
| TWR 251 | A+0 | 0°00'00" |  | 678 | 2290 | 171 | 342 | 0 | 342 | 157.2418 | 0 | 157.2418 | 162.8855 | 0 | 162.8855 |  | 179423.568 | 1373444.915 | 568.733 | 0
| New Conductor Leng |  | Old Stringing |  | New stringing | Length
| 2659 |  | Span | L | Span | L
|  |  | 244 D | 610 | 244 D | 388
|  |  | 246 C | 313 | 245 New A | 250
|  |  | 247 D | 342 | 246 New D | 245
|  |  | 248 A | 330 | 247 New D | 486
|  |  | 249 A | 370 | 248 New D | 250
|  |  | 250 A | 350 | 249 D New | 336
|  |  | 251 A | 362 | 250 A New | 342
|  |  | 252 C |  | 251 A | 362
|  |  |  | 2677 |  | 2659

## TS_Hosur-Salem Old (hidden)
400KV HOSUR - SALEM-II (Hosur jurisdiction HSR Gantry - Loc 255)
Tower No. | Type of tower | Tower extn | Angle of Deviation | Forward span (mtr.) | Cum Length ex Hosur | Percentage ex Hosur | Type of Foundation | Earthing | Crossing | Remarks | Category | Terrain | Name of crossing | Nearest Village | Vulnerability if any | Wind Zone | GPS North | GPS East | Make of Tower
CHAR
8
Hosur Gantry |  |  | 020 00' LT | 112 | 0 | 0.06176%
535 | DDE | 6 | 02°34'27" RT | 294 | 112 | 0.2239% | DFR | CP |  |  | Normal |  |  |  |  | II | 12°40'18.3" N | 77°59'31.7" E | M/s NCC Ltd
534 | DD | 18 | 0°0'0" | 455 | 406 | 0.4748% | DFR | CP | 230kv line | Metal road | Normal |  | 230Kv S/CShoolagiri -Singarpet Power line crossing | Maruthandapalli |  | II | 12°40'18.6" N | 77°59'23.9" E | M/s NCC Ltd
533 | DD | 6 | 26°26'25" RT | 413 | 861 | 0.7025% | DFR | CP |  |  | Normal |  |  | Maruthandapalli |  | II | 12°40'23.6" N | 77°59'10.9" E | M/s NCC Ltd
532 | DD | 6 | 58°07'15" RT | 250 | 1274 | 0.8403% | DFR | CP | LT Line |  | Normal |  |  | Gurubarathapalli |  | II | 12°40'20.3" N | 77°58'57.8" E | M/s NCC Ltd
531 | DD | 3 | 10°18'34" RT | 234 | 1524 | 0.9694% | PS/WFR | P | 33kV Line |  | Normal | Water course |  | ChinnaChappadi |  | II | 12°40'13.8" N | 77°58'55.6" E | M/s NCC Ltd
530 | DA | 6 |  | 282 | 1758 | 1.125% | WFR | P | 11kv NH crossing |  | Normal |  | NH Crossing | ChinnaChappadi |  | II | 12°40'06.4" N | 77°58'54.4" E | M/s NCC Ltd
529 | DB | 9 | 0°45'51" LT | 261 | 2040 | 1.269% | DFR | CP |  |  | Normal |  |  | ChinnaChappadi |  | II | 12°39'55.8" N | 77°58'52.8" E | M/s NCC Ltd
528 | DC | 9 | 18°35'28" RT | 501 | 2301 | 1.545% | WET/WFR | CP | 110&230KV lines |  | Normal |  | 110kv s/c Hosur Karimangalam &230 s/c Hosur-Shoolagiri line | ChinnaChappadi |  | II | 12°39'47.7" N | 77°58'51.5" E | M/s NCC Ltd
527 | DD | 9 | 32°59'09" RT | 264 | 2802 | 1.691% | DFR | CP |  | Metal road | Normal |  |  | ChinnaChappadi |  | II | 12°39'31.7" N | 77°58'54.2" E | M/s NCC Ltd
526 | DA | 18 |  | 246 | 3066 | 1.826% | WET/WFR | CP | 230KVLINE |  | Normal |  | 230kv S/C Shoolagiri-Karimangalam line | Samanapaali |  | II | 12°39'25.3" N | 77°59'00.2" E | M/s NCC Ltd
525 | DB | 3 | 00°51'17" LT | 256 | 3312 | 1.967% | DFR | CP |  |  | Normal |  |  | Gambeeranapalli |  | II | 12°39'19.7" N | 77°59'05.5" E | M/s NCC Ltd
524 | DA | 0 |  | 352 | 3568 | 2.161% | WET/WFR | CP |  |  | Normal |  |  | Gambeeranapalli |  | II | 12°39'12.9" N | 77°59'11.6" E | M/s NCC Ltd
523 | DA | 0 |  | 350 | 3920 | 2.354% | DFR | CP | LT Line |  | Normal |  |  | Bellati |  | II | 12°39'04.8" N | 77°59'19.0" E | M/s NCC Ltd
522 | DD | 0 | 34°52'27" LT | 329 | 4270 | 2.536% | WET/WFR | CP |  | Metal road | Normal |  |  | Bellatti |  | II | 12°38'56.3" N | 77°59'26.8" E | M/s NCC Ltd
521 | DA | 0 |  | 376 | 4599 | 2.743% | DFR | CP | 33KV Line |  | Normal |  |  | Bellatti |  | II | 12°38'45.8" N | 77°59'28.1" E | M/s NCC Ltd
520 | DA | 0 |  | 400 | 4975 | 2.964% | DFR | CP | 11KV | Metal road | Normal |  |  | Bellatti |  | II | 12°38'33.6" N | 77°59'29.7" E | M/s NCC Ltd
519 | DA | 0 |  | 340 | 5375 | 3.151% | DFR | CP | LT Line |  | Normal |  |  | Tyagaradsanapalli |  | II | 12°38'20.9" N | 77°59'31.4" E | M/s NCC Ltd
518 | DA | 3 |  | 375 | 5715 | 3.358% | DFR | CP |  | Metal road | Normal |  |  | Tyagaradsanapalli |  | II | 12°38'09.7" N | 77°59'32.8" E | M/s NCC Ltd
517 | DA | 0 |  | 383 | 6090 | 3.569% | DFR | CP |  |  | Normal | Rocky & Boulders |  | Tyagaradsanapalli |  | II | 12°37'57.7" N | 77°59'34.4" E | M/s NCC Ltd
516 | DA | 3 |  | 413 | 6473 | 3.797% | DFR | CP |  |  | Normal |  |  | Tyagaradsanapalli |  | II | 12°37'44.6" N | 77°59'36.1" E | M/s NCC Ltd
515 | DA | 9 |  | 288 | 6886 | 3.956% | DFR | CP |  |  | Normal |  |  | Ettipalli |  | II | 12°37'32.0" N | 77°59'37.7" E | M/s NCC Ltd
514 | DD | 6 | 32°35'05" LT | 394 | 7174 | 4.173% | DFR | CP |  | Metal road | Normal | Rocky & Boulders |  | Ettipalli |  | II | 12°37'22.5" N | 77°59'39.0" E | M/s NCC Ltd
513 | DA | 3 |  | 326 | 7568 | 4.353% | DFR | CP |  |  | Normal |  |  | Ettipalli |  | II | 12°37'11.1" N | 77°59'33.4" E | M/s NCC Ltd
512 | DA | 0 | 0°25'51" LT | 324 | 7894 | 4.531% | DFR | CP | 11KV | Metal road | Normal |  |  | Ettipalli |  | II | 12°37'01.7" N | 77°59'28.8" E | M/s NCC Ltd
511 | DA | 0 |  | 370 | 8218 | 4.735% | DFR | CP |  |  | Normal |  |  | Ettipalli |  | II | 12°36'52.1" N | 77°59'24.2" E | M/s NCC Ltd
510 | DA | 0 |  | 397 | 8588 | 4.954% | DFR | CP |  |  | Normal |  |  | Thukandapalli |  | II | 12°36'41.3" N | 77°59'18.9" E | M/s NCC Ltd
509 | DC | 6 | 18°52'48" RT | 402 | 8985 | 5.176% | DFR | CP |  |  | Normal | Rocky & Boulders |  | Thukandapalli |  | II | 12°36'29.7" N | 77°59'13.2" E | M/s NCC Ltd
508 | DA | 6 |  | 361 | 9387 | 5.375% | DFR | CP |  |  | Normal | watercourse |  | Thukandapalli |  | II | 12°36'16.7" N | 77°59'11.6" E | M/s NCC Ltd
507 | DA | 0 |  | 437 | 9748 | 5.616% | WFR | CP | River |  | Normal | Water course |  | varadapuram |  | II | 12°35'52.7" N | 77°59'08.6" E | M/s NCC Ltd
506 | DA | 9 |  | 348 | 10185 | 5.808% | DFR | CP |  |  | Vulnerable | plain |  | varadapuram |  | II | 12°35'41.9" N | 77°59'07.2" E | M/s NCC Ltd
505 | DA | 9 |  | 441 | 10533 | 6.051% | DFR | CP | LT Line |  | Normal | plain |  | Ariyanahali |  | II | 12°35'29.0" N | 77°59'05.6" E | M/s NCC Ltd
504 | DA | 0 |  | 380 | 10974 | 6.261% | DFR | CP | LT Line | Metal road | Normal | plain |  | Bandarapalli |  | II | 12°35'16.0" N | 77°59'04.0" E | M/s NCC Ltd
503 | DA | 3 |  | 394 | 11354 | 6.478% | DFR | CP | LT Line | Metal road | Normal | plain |  | Bandarapalli |  | II | 12°35'08.8" N | 77°59'03.1" E | M/s NCC Ltd
502 | DA | 9 |  | 405 | 11748 | 6.701% | DFR | CP | LT Line | Metal road | Normal | plain |  | Bandarapalli |  | II | 12°34'56.8" N | 77°59'01.6" E | M/s NCC Ltd
501 | DDE | 0 | 04°02'30" LT | 146 | 12153 | 6.782% | DFR | CP | 11kV Line | Metal road | Normal | plain |  | Bandarapalli |  | II | 12°34'44.4" N | 77°59'00.0" E | M/s NCC Ltd
500 | DDE | 9 |  | 410 | 12299 | #REF! | DFR | CP | LT Line |  | Normal | plain |  | Bandarapalli |  | II | 12°34'41.4" N | 77°58'59.5" E | M/s NCC Ltd
187 |  |  |  | 340 | 12709
188 | A | 0 |  | 400 | 13049 | 7.195% | DFRU | CP |  |  | Normal | Water course |  | Bhatarapatti |  | II | 12°34’33”N | 077°59’22”E | M/s KEC International Ltd.
189 | A | 0 |  | 330 | 13449 | 7.416% | 2-DFRU 2-DFRA | P |  |  | Normal |  |  | Bhatarapatti |  | II | 12°34’26”N | 077°59’34”E | M/s KEC International Ltd.
190 | A | 0 |  | 345 | 13779 | 7.598% | DFRU | P |  |  | Normal |  |  | Bhatarapatti |  | II | 12°34’21”N | 077°59’43”E | M/s KEC International Ltd.
191 | A | 0 |  | 355 | 14124 | 7.788% | DFRU | P | LT Line |  | Normal |  |  | Bhatarapatti |  | II | 12°34’15”N | 077°59’53”E | M/s KEC International Ltd.
192 | A | 0 |  | 338 | 14479 | 7.984% | SFRU | P |  |  | Normal | Boulders |  | Bhatarapatti |  | II | 12°34’09”N | 078°00’03”E | M/s KEC International Ltd.
193 | B | 0 | 07°30' RT | 400 | 14817 | 8.17% | WBC | CP |  | Cart track | Normal |  |  | Agraharam |  | II | 12°34’04”N | 078°00’12”E | M/s KEC International Ltd.
194 | A | 0 |  | 354 | 15217 | 8.391% | DFRU | CP |  |  | Normal | Water course & Rocky |  | Agraharam |  | II | 12°33’56”N | 078°00’23”E | M/s KEC International Ltd.
195 | D | 0 | 31°57'20" LT | 280 | 15571 | 8.586% | DFRU | P |  | Cart track | Normal |  |  | Agraharam |  | II | 12°33’49”N | 078°00’32”E | M/s KEC International Ltd.
196 | A | 0 |  | 385 | 15851 | 8.74% | DFRU | P |  | Tar road | Normal |  |  | Agraharam |  | II | 12°33’48”N | 078°00’41”E | M/s KEC International Ltd.
197 | C | 6 | 20°06' RT | 475 | 16236 | 8.953% | Dry | P | 33kV Line | Lake | Normal |  |  | Balampatti |  | II | 12°33’46”N | 078°00’54”E | M/s KEC International Ltd.
198 | D | 0 | 42°20' RT | 384 | 16711 | 9.214% | SFRU | P |  |  | Normal |  |  | Balampatti |  | II | 12°33’40”N | 078°01’07”E | M/s KEC International Ltd.
199 | B | 3 | 3°10' RT | 450 | 17095 | 9.426% | SFRU | P | 33kV Line |  | Normal |  |  | Balampatti |  | II | 12°33’28”N | 078°01’12”E | M/s KEC International Ltd.
200 | B | 3 | 9°10' LT | 320 | 17545 | 9.674% | DFRU | CP | 33kV Line |  | Normal |  |  | Balampatti |  | II | 12°33’14”N | 078°01’17”E | M/s KEC International Ltd.
201 | A | 0 |  | 300 | 17865 | 9.851% | DFRU | P | 11kV Line |  | Normal | Undulated area |  | Balampatti |  | II | 12°33’05”N | 078°01’22”E | M/s KEC International Ltd.
202 | A | 0 |  | 322 | 18165 | 10.02% | DFRU | P |  |  | Normal |  |  | Mugalure, Rayakottai, Krishnagiri Dt. |  | II | 12°32’56”N | 078°01’26”E | M/s KEC International Ltd.
203 | D | 0 | 49°25' LT | 380 | 18487 | 10.19% | Dry | P | 33kV Line |  | Normal |  |  | Mugalure |  | II | 12°32’47”N | 078°01’31”E | M/s KEC International Ltd.
204 | A | 3 |  | 420 | 18867 | 10.4% | DFRU | CP |  |  | Normal | Boulders |  | Mugalure |  | II | 12°32’44”N | 078°01’43”E | M/s KEC International Ltd.
205 | A | 0 |  | 352 | 19287 | 10.63% | 3-DFRU 1-DFRA | CP |  |  | Normal | Water course & Rocky |  | Pudupatti Rayakottai, Krishnagiri Dt. |  | II | 12°32’41”N | 078°01’57”E | M/s KEC International Ltd.
206 | D | 0 | 30°50'40" RT | 310 | 19639 | 10.83% | DFRU | P |  |  | Normal | Water course |  | Pudupatti |  | II | 12°32’39”N | 078°02’08”E | M/s KEC International Ltd.
207 | A | 0 |  | 270 | 19949 | 11% | DFRU | P |  |  | Normal |  |  | Pudupatti |  | II | 12°32’32”N | 078°02’15”E | M/s KEC International Ltd.
208 | A | 0 |  | 320 | 20219 | 11.15% | DFRU | CP |  |  | Normal |  |  | Pudupatti |  | II | 12°32’26”N | 078°02’22”E | M/s KEC International Ltd.
209 | A | 0 |  | 408 | 20539 | 11.33% | DFRU | P |  |  | Normal | Water course |  | Pudupatti |  | II | 12°32’18”N | 078°02’30”E | M/s KEC International Ltd.
210 | D | 0 | 31°30' RT | 284 | 20947 | 11.55% | DFRU | CP |  |  | Normal | Hilly area |  | Thotlampatti Rayakottai, Krishnagiri Dt. |  | II | 12°32’09”N | 078°02’39”E | M/s KEC International Ltd.
211 | A | 6 |  | 356 | 21231 | 11.71% | DFRU | P | LT Line |  | Normal | Hilly area |  | Thotlampatti |  | II | 12°32’00”N | 078°02’41”E | M/s KEC International Ltd.
212 | A | 0 |  | 355 | 21587 | 11.9% | DFRU | P | LT Line |  | Normal |  |  | Thotlampatti |  | II | 12°31’49”N | 078°02’44”E | M/s KEC International Ltd.
213 | B | 0 |  | 327 | 21942 | 12.1% | DFRU | CP |  |  | Normal |  |  | Thotlampatti |  | II | 12°31’38”N | 078°02’47”E | M/s KEC International Ltd.
214 | C | 0 | 20°24'20" RT | 220 | 22269 | 12.28% | DFRU | CP |  |  | Normal | Hilly area |  | Thotlampatti |  | II | 12°31’28”N | 078°02’49”E | M/s KEC International Ltd.
215 | A | 0 |  | 335 | 22489 | 12.4% | DFRU | CP |  |  | Normal | Boulders |  | Thotlampatti |  | II | 12°31’21”N | 078°02’49”E | M/s KEC International Ltd.
216 | A | 3 |  | 405 | 22824 | 12.59% | DFRU | CP |  |  | Normal |  |  | Thotlampatti |  | II | 12°31’10”N | 078°02’47”E | M/s KEC International Ltd.
217 | B | 6 |  | 340 | 23229 | 12.81% | DFRU | P |  |  | Normal | Hilly area |  | Thotlampatti |  | II | 12°30’57”N | 078°02’46”E | M/s KEC International Ltd.
218 | A | 0 |  | 410 | 23569 | 13% | Dry | CP |  |  | Normal | Hilly area |  | Thotlampatti |  | II | 12°30’46”N | 078°02’44”E | M/s KEC International Ltd.
219 | A | 6 |  | 430 | 23979 | 13.22% | 3-DFRU 1-Dry | CP |  |  | Normal | Hilly area |  | Thotlampatti |  | II | 12°30’33”N | 078°02’43”E | M/s KEC International Ltd.
220 | B | 6 |  | 464 | 24409 | 13.46% | DFRU | CP | LT Line | Tar road | Normal | Hilly area |  | Bodinaikanpatti , Rayakottai, Krishnagiri Dt. |  | II | 12°30’19”N | 078°02’41”E | M/s KEC International Ltd.
221 | A | 3 |  | 266 | 24873 | 13.71% | DFRU | CP |  |  | Normal | Rocky area |  | Bodinaikanpatti |  | II | 12°30’05”N | 078°02’39”E | M/s KEC International Ltd.
222 | A | 0 |  | 310 | 25139 | 13.86% | 2-DFRU 2-Dry | P |  |  | Normal | Water course |  | Bodinaikanpatti |  | II | 12°29’56”N | 078°02’39”E | M/s KEC International Ltd.
223 | A | 0 |  | 326 | 25449 | 14.03% | DFRU | CP |  | Tar road | Normal |  |  | Bodinaikanpatti |  | II | 12°29’46”N | 078°02’37”E | M/s KEC International Ltd.
224 | B | 0 | 7°55' LT | 380 | 25775 | 14.21% | DFRU | CP | 2 Nos. LT Line |  | Normal | Water course |  | Bodinaikanpatti |  | II | 12°29’36”N | 078°02’36”E | M/s KEC International Ltd.
225 | A | 0 |  | 340 | 26155 | 14.42% | DFRU | P |  |  | Normal | Boulders & Water course |  | Bodinaikanpatti |  | II | 12°29’24”N | 078°02’36”E | M/s KEC International Ltd.
226 | A | 0 |  | 370 | 26495 | 14.61% | FS | CP |  |  | Normal | Water course |  | Bodinaikanpatti |  | II | 12°29’12”N | 078°02’36”E | M/s KEC International Ltd.
227 | A | 0 |  | 340 | 26865 | 14.81% | DFRU | CP |  |  | Normal | Boulders |  | Kulikadu, Rayakottai, Krishnagiri Dt. |  | II | 12°29’00”N | 078°02’36”E | M/s KEC International Ltd.
228 | A | 0 |  | 396 | 27205 | 15% | DFRU | CP |  |  | Normal | Water course |  | Kulikadu |  | II | 12°28’48”N | 078°02’37”E | M/s KEC International Ltd.
229 | B | 0 | 3°19' RT | 320 | 27601 | 15.22% | DFRU | CP |  |  | Normal | Undulated area with boulders |  | Kulikadu |  | II | 12°28’32”N | 078°02’37”E | M/s KEC International Ltd.
230 | B | 9 |  | 490 | 27921 | 15.4% | DFRU | CP |  | Nala | Normal |  |  | Kulikadu |  | II | 12°28’20”N | 078°02’37”E | M/s KEC International Ltd.
231 | B | 6 | 8°17' LT | 230 | 28411 | 15.67% | SRFU | CP | 33kV Line |  | Normal |  |  | Kulikadu |  | II | 12°28’11”N | 078°02’34”E | M/s KEC International Ltd.
232 | B | 0 |  | 427 | 28641 | 15.79% | 3-DFRU 1-DFRA | CP |  |  | Normal | Undulated land |  | Kulikadu |  | II | 12°28’04”N | 078°02’35”E | M/s KEC International Ltd.
233 | B | 3 |  | 441 | 29068 | 16.03% | DFRU | P | LT Line | Nala & Lake | vulnerable |  |  | Kulikadu |  | II | 12°27’49”N | 078°02’36”E | M/s KEC International Ltd.
234 | B | 6 | 8°10' RT | 430 | 29509 | 16.27% | PS | P | LT Line | Lake | vulnerable |  |  | Kulikadu |  | II | 12°27’36”N | 078°02’37”E | M/s KEC International Ltd.
235 | A | 6 |  | 416 | 29939 | 16.51% | FS | P |  |  | Normal | Water course |  | Chinnampatti, Rayakottai, Krishnagiri Dt. |  | II | 12°27’23”N | 078°02’39”E | M/s KEC International Ltd.
236 | B | 3 | 6°44' LT | 450 | 30355 | 16.74% | WBC | P | LT Line |  | Normal | Water course |  | Chinnampatti |  | II | 12°27’10”N | 078°02’41”E | M/s KEC International Ltd.
237 | A | 6 |  | 350 | 30805 | 16.99% | PS | P | 11kV Line |  | Normal |  |  | Chinnampatti |  | II | 12°26’56”N | 078°02’46”E | M/s KEC International Ltd.
238 | B | 0 | 6°14' RT | 350 | 31155 | 17.18% | WBC | P |  |  | Normal |  |  | Chinnampatti |  | II | 12°26’45”N | 078°02’49”E | M/s KEC International Ltd.
239 | A | 0 |  | 370 | 31505 | 17.37% | Wet | P | LT Line |  | Normal | Water course |  | Chinnampatti |  | II | 12°26’34”N | 078°02’50”E | M/s KEC International Ltd.
240 | A | 0 |  | 390 | 31875 | 17.58% | WBC | P |  |  | Normal | Water course |  | Jitttandahalli, Dharmapuri |  | II | 12°26’22”N | 078°02’53”E | M/s KEC International Ltd.
241 | A | 0 |  | 380 | 32265 | 17.79% | DFRU | P |  |  | Normal |  |  | Jitttandahalli |  | II | 12°26’10”N | 078°02’55”E | M/s KEC International Ltd.
242 | A | 0 |  | 370 | 32645 | 18% | DFRU | P |  |  | Normal |  |  | Jitttandahalli |  | II | 12°25’58”N | 078°02’57”E | M/s KEC International Ltd.
243 | A | 0 |  | 340 | 33015 | 18.2% | DFRU | P |  |  | Normal |  |  | Jitttandahalli |  | II | 12°25’46”N | 078°02’59”E | M/s KEC International Ltd.
244 | D | 0 | 38°54' RT | 370 | 33355 | 18.39% | DFRU | P | 11kV,LT Line | Nala | Normal |  |  | Jitttandahalli |  | II | 12°25’35”N | 078°03’01”E | M/s KEC International Ltd.
245 | C | 0 |  | 240 | 33725 | 18.6% | SFRU | P |  | State Highway | vulnerable |  |  | Jitttandahalli |  | II | 12°25’24”N | 078°02’55”E | M/s KEC International Ltd.
246 | C | 0 |  | 313 | 33965 | 18.73% | FS | P |  |  | vulnerable | Water course |  | Singeri, Dharmapur Dt. |  | II | 12°25’18”N | 078°02’51”E | M/s KEC International Ltd.
247 | D | 0 | 55°43' LT | 342 | 34278 | 18.9% | Wet | CP |  | Tar road | Normal |  |  | Singeri |  | II | 12°25’09”N | 078°02’46”E | M/s KEC International Ltd.
248 | A | 0 |  | 330 | 34620 | 19.09% | DFRU | P | 11kV Line | Cart road | Normal |  |  | Singeri |  | II | 12°24’59”N | 078°02’51”E | M/s KEC International Ltd.
249 | A | 0 |  | 370 | 34950 | 19.27% | WBC | P | LT Line |  | Normal |  |  | Singeri |  | II | 12°24’49”N | 078°02’56”E | M/s KEC International Ltd.
250 | A | 0 |  | 350 | 35320 | 19.48% | WBC | P | 11kV, 3 Nos. LT Line |  | vulnerable |  |  | Jackasamudiram Dharmapuri Dt. |  | II | 12°24’39”N | 078°03’01”E | M/s KEC International Ltd.
251 | A | 0 |  | 362 | 35670 | 19.67% | WBC | P |  |  | vulnerable |  |  | Jackasamudiram |  | II | 12°24’29”N | 078°03’06”E | M/s KEC International Ltd.
252 | C | 0 | 17°30' RT | 420 | 36032 | 19.87% | WBC | P |  |  | vulnerable |  |  | Jackasamudiram |  | II | 12°24’18”N | 078°03’12”E | M/s KEC International Ltd.
253 | A | 3 |  | 420 | 36452 | 20.1% | WBC | P | LT Line | Tar road | vulnerable |  |  | Jackasamudiram |  | II | 12°24’05”N | 078°03’14”E | M/s KEC International Ltd.
254 | A | 6 |  | 420 | 36872 | 20.33% | FS | P |  | Nala | vulnerable | Water course |  | Jackasamudiram |  | II | 12°23’51”N | 078°03’16”E | M/s KEC International Ltd.
255 | C | 0 | 20°41' LT | 380 | 37292 | 20.56% | WBC | P | 2 Nos. LT Line |  | vulnerable | Water course |  | Jackasamudiram |  | II | 12°23’38”N | 078°03’19”E | M/s KEC International Ltd.
256 | A | 0 |  | 430 | 37672 | 20.77% | WBC | P | LT Line |  | Normal | Water course |  | Jackasamudiram |  | II | 12°23’28”N | 078°03’25”E | M/s KEC International Ltd.
257 | A | 6 |  | 320 | 38102 | 21.01% | WBC | P |  |  | Normal |  |  | Jackasamudiram |  | II | 12°23’15”N | 078°03’32”E | M/s KEC International Ltd.
258 | A | 0 |  | 320 | 38422 | 21.19% | 2-SFRU 2-WBC | CP | 11kV Line |  | Normal |  |  | Jackasamudiram |  | II | 12°23’06”N | 078°03’37”E | M/s KEC International Ltd.
259 | A | 0 |  | 320 | 38742 | 21.36% | DFRU | CP |  | Cart track | Normal | Boulders |  | Jackasamudiram |  | II | 12°22’57”N | 078°03’42”E | M/s KEC International Ltd.
260 | A | 0 |  | 314 | 39062 | 21.54% | DFRU | CP |  |  | vulnerable | Boulders |  | Jackasamudiram |  | II | 12°22’48”N | 078°03’47”E | M/s KEC International Ltd.
261 | D | 0 | 45°00' RT | 420 | 39376 | 21.71% | DFRU | CP |  |  | vulnerable |  |  | Jackasamudiram |  | II | 12°22’40”N | 078°03’52”E | M/s KEC International Ltd.
262 | A | 0 |  | 330 | 39796 | 21.94% | SFRU | CP |  |  | Normal |  |  | Vellichandai Palkode, Dharmapuri |  | II | 12°22’26”N | 078°03’49”E | M/s KEC International Ltd.
263 | A | 3 |  | 394 | 40126 | 22.13% | DFRU | CP | LT Line | Tar road | Normal |  |  | Vellichandai Palkode |  | II | 12°22’16”N | 078°03’46”E | M/s KEC International Ltd.
264 | A | 0 |  | 346 | 40520 | 22.34% | DFRU | P | 11kV Line |  | Normal |  |  | Vellichandai Palkode |  | II | 12°22’04”N | 078°03’43”E | M/s KEC International Ltd.
265 | A | 0 |  | 380 | 40866 | 22.53% | SFRU | CP | 33kV Line |  | Normal |  |  | Vellichandai Palkode |  | II | 12°21’53”N | 078°03’40”E | M/s KEC International Ltd.
266 | A | 0 |  | 380 | 41246 | 22.74% | DFRU | P |  |  | Normal |  |  | Vellichandai Palkode |  | II | 12°21’41”N | 078°03’36”E | M/s KEC International Ltd.
267 | A | 0 |  | 290 | 41626 | 22.95% | DFRU | P |  |  | Normal |  |  | Vellichandai Palkode |  | II | 12°21’29”N | 078°03’33”E | M/s KEC International Ltd.
268 | A | 0 |  | 330 | 41916 | 23.11% | SFRU | P |  |  | Normal |  |  | Vellichandai Palkode |  | II | 12°21’20”N | 078°03’31”E | M/s KEC International Ltd.
269 | A | 3 |  | 382 | 42246 | 23.29% | WBC | P | LT Line |  | Normal |  |  | Vellichandai Palkode |  | II | 12°21’10”N | 078°03’28”E | M/s KEC International Ltd.
270 | C | 0 | 17°37' LT | 340 | 42628 | 23.51% | DFRU | P | 11kV, 2 Nos. LT Line |  | Normal |  |  | Palakode Dharmapuri Dt. |  | II | 12°20’58”N | 078°03’25”E | M/s KEC International Ltd.
271 | A | 0 |  | 330 | 42968 | 23.69% | DFRU | P | 230kV Line |  | vulnerable |  |  | Palakode |  | II | 12°20’46”N | 078°03’25”E | M/s KEC International Ltd.
272 | A | 0 |  | 328 | 43298 | 23.87% | SFRU | P | 230kV Line |  | vulnerable |  |  | Palakode |  | II | 12°20’36”N | 078°03’26”E | M/s KEC International Ltd.
273 | A | 0 |  | 382 | 43626 | 24.06% | DFRU | P | LT Line |  | vulnerable | Boulders |  | Palakode |  | II | 12°20’25”N | 078°03’26”E | M/s KEC International Ltd.
274 | A | 3 |  | 340 | 44008 | 24.27% | SFRU | P | 2 Nos. LT Line |  | Normal |  |  | Palakode |  | II | 12°20’13”N | 078°03’27”E | M/s KEC International Ltd.
275 | A | 0 |  | 370 | 44348 | 24.45% | FS | P | LT Line | Tar road | Normal |  |  | Palakode |  | II | 12°20’02”N | 078°03’27”E | M/s KEC International Ltd.
276 | A | 0 |  | 290 | 44718 | 24.66% | FS | P |  |  | Normal |  |  | Palakode |  | II | 12°19’50”N | 078°03’28”E | M/s KEC International Ltd.
277 | A | 3 |  | 390 | 45008 | 24.82% | FS | P |  |  | Normal |  |  | Palakode |  | II | 12°19’41”N | 078°03’28”E | M/s KEC International Ltd.
278 | A | 6 |  | 430 | 45398 | 25.03% | WBC | P |  | Lake | Normal |  |  | Palakode |  | II | 12°19’28”N | 078°03’29”E | M/s KEC International Ltd.
279 | A | 6 |  | 410 | 45828 | 25.27% | SFRU | P |  | Nala | Normal |  |  | Palakode |  | II | 12°19’14”N | 078°03’30”E | M/s KEC International Ltd.
280 | A | 0 |  | 290 | 46238 | 25.5% | 2-SFRU 2-WBC | P |  |  | vulnerable | Water course |  | Palakode |  | II | 12°19’01”N | 078°03’30”E | M/s KEC International Ltd.
281 | B | 0 | 9°05' RT | 352 | 46528 | 25.66% | 3-SFRU 1-FS | P |  |  | vulnerable |  |  | Palakode |  | II | 12°18’52”N | 078°03’31”E | M/s KEC International Ltd.
282 | D | 3 | 43°23' RT | 242 | 46880 | 25.85% | FS | P | 11kV, LT Line | Railway line | Normal |  |  | Palakode |  | II | 12°18’40”N | 078°03’29”E | M/s KEC International Ltd.
283 | D | 6 | 54°47' LT | 400 | 47122 | 25.98% | FS | P |  |  | Normal |  |  | Palakode |  | II | 12°18’35”N | 078°03’23”E | M/s KEC International Ltd.
284 | A | 0 |  | 410 | 47522 | 26.2% | FS | CP | LT Line |  | Normal |  |  | Palakode |  | II | 12°18’23”N | 078°03’24”E | M/s KEC International Ltd.
285 | A | 6 |  | 415 | 47932 | 26.43% | SFRU | P | 11kV Line |  | Normal |  |  | Palakode |  | II | 12°18’09”N | 078°03’26”E | M/s KEC International Ltd.
286 | B | 0 | 5°35'20" RT | 350 | 48347 | 26.66% | SFRU | P | 11kV, LT Line | Tar road, Nala | Normal |  |  | Palakode |  | II | 12°17’56”N | 078°03’27”E | M/s KEC International Ltd.
287 | A | 0 |  | 380 | 48697 | 26.85% | SFRU | P |  | Nala, Canal | Normal |  |  | Palakode |  | II | 12°17’45”N | 078°03’27”E | M/s KEC International Ltd.
288 | A | 0 |  | 400 | 49077 | 27.06% | SFRU | P |  | Cart track | Normal |  |  | Palakode |  | II | 12°17’33”N | 078°03’26”E | M/s KEC International Ltd.
289 | A | 0 |  | 400 | 49477 | 27.28% | DFRU | P | LT Line |  | Normal |  |  | Palakode |  | II | 12°17’20”N | 078°03’26”E | M/s KEC International Ltd.
290 | A | 6 |  | 400 | 49877 | 27.5% | DFRU | CP |  |  | Normal |  |  | Palakode |  | II | 12°17’07”N | 078°03’26”E | M/s KEC International Ltd.
291 | A | 0 |  | 400 | 50277 | 27.72% | SFRU | P |  | 2 Nos. Cart track | Normal |  |  | Palakode |  | II | 12°16’54”N | 078°03’26”E | M/s KEC International Ltd.
292 | A | 0 |  | 290 | 50677 | 27.94% | DFRU | P |  | Nala | Normal |  |  | Palakode |  | II | 12°16’42”N | 078°03’26”E | M/s KEC International Ltd.
293 | A | 0 |  | 390 | 50967 | 28.1% | DFRU | P |  | Nala | Normal |  |  | Palakode |  | II | 12°16’32”N | 078°03’26”E | M/s KEC International Ltd.
294 | A | 0 |  | 290 | 51357 | 28.32% | 2-DFRU 2-Dry | P |  |  | Normal |  |  | Palakode |  | II | 12°16’20”N | 078°03’26”E | M/s KEC International Ltd.
295 | A | 0 |  | 365 | 51647 | 28.48% | DFRU | P |  | Canal, Nala | Normal |  |  | Palakode |  | II | 12°16’10”N | 078°03’26”E | M/s KEC International Ltd.
296 | A | 0 |  | 325 | 52012 | 28.68% | DFRU | P |  |  | Normal |  |  | Palakode |  | II | 12°15’59”N | 078°03’26”E | M/s KEC International Ltd.
297 | A | 0 |  | 320 | 52337 | 28.86% | DFRU | P |  |  | Normal |  |  | Palakode |  | II | 12°15’48”N | 078°03’26”E | M/s KEC International Ltd.
298 | C | 0 | 26°01'40" RT | 400 | 52657 | 29.03% | DFRU | P |  | Metal road | Normal |  |  | Palakode |  | II | 12°15’38”N | 078°03’26”E | M/s KEC International Ltd.
299 | A | 3 |  | 370 | 53057 | 29.26% | DFRU | P | LT Line | Nala | Normal |  |  | Palakode |  | II | 12°15’26”N | 078°03’20”E | M/s KEC International Ltd.
300 | A | 0 |  | 410 | 53427 | 29.46% | DFRU | P |  | Nala | Normal |  |  | Paparapatti, Dharmapuri Dt. |  | II | 12°15’16”N | 078°03’15”E | M/s KEC International Ltd.
301 | A | 0 |  | 377 | 53837 | 29.69% | DFRU | P | LT Line |  | Normal | Boulders |  | Paparapatti |  | II | 12°15’04”N | 078°03’09”E | M/s KEC International Ltd.
302 | C | 6 | 15°06' LT | 380 | 54214 | 29.89% | DFRU | P | LT Line | Cart track, Nala | Normal |  |  | Paparapatti |  | II | 12°14’53”N | 078°03’03”E | M/s KEC International Ltd.
303 | A | 6 |  | 410 | 54594 | 30.1% | DFRU | P |  | Nala | Normal |  |  | Paparapatti |  | II | 12°14’42”N | 078°03’01”E | M/s KEC International Ltd.
304 | A | 0 |  | 380 | 55004 | 30.33% | Dry | P | LT Line | Metal road, Nala | Normal |  |  | Paparapatti |  | II | 12°14’28”N | 078°02’58”E | M/s KEC International Ltd.
305 | A | 3 |  | 340 | 55384 | 30.54% | Dry | P | 3 Nos. LT Line | Nala | Normal |  |  | Paparapatti |  | II | 12°14’17”N | 078°02’55”E | M/s KEC International Ltd.
306 | B | 0 | 6°26'40" RT | 320 | 55724 | 30.73% | Dry | P |  | Nala | Normal |  |  | Paparapatti |  | II | 12°14’06”N | 078°02’53”E | M/s KEC International Ltd.
307 | A | 0 |  | 320 | 56044 | 30.9% | Wet | P | 11kV, LT Line |  | Normal |  |  | Paparapatti |  | II | 12°13’57”N | 078°02’49”E | M/s KEC International Ltd.
308 | A | 0 |  | 360 | 56364 | 31.08% | Wet | P | LT Line | Metal road | Normal |  |  | Paparapatti |  | II | 12°13’47”N | 078°02’46”E | M/s KEC International Ltd.
309 | A | 0 |  | 380 | 56724 | 31.28% | WBC | P | LT Line | Nala | Normal |  |  | Paparapatti |  | II | 12°13’36”N | 078°02’42”E | M/s KEC International Ltd.
310 | A | 0 |  | 360 | 57104 | 31.49% | WBC | P |  |  | Normal |  |  | Paparapatti |  | II | 12°13’25”N | 078°02’38”E | M/s KEC International Ltd.
311 | A | 6 |  | 335 | 57464 | 31.69% | FS | P |  | Nala | Normal |  |  | Paparapatti |  | II | 12°13’14”N | 078°02’35”E | M/s KEC International Ltd.
312 | D | 0 | 30°13'20" LT | 400 | 57799 | 31.87% | FS | P | 11kV, LT Line |  | Normal |  |  | Paparapatti |  | II | 12°13’04”N | 078°02’31”E | M/s KEC International Ltd.
313 | A | 3 |  | 430 | 58199 | 32.09% | WBC | P | 11 kV Line |  | Normal |  |  | Paparapatti |  | II | 12°12’51”N | 078°02’34”E | M/s KEC International Ltd.
314 | A | 0 |  | 350 | 58629 | 32.33% | WBC | P |  |  | Normal |  |  | Paparapatti |  | II | 12°12’38”N | 078°02’36”E | M/s KEC International Ltd.
315 | A | 0 |  | 380 | 58979 | 32.52% | DFRU | CP |  | Cart track | Normal |  |  | Paparapatti |  | II | 12°12’27”N | 078°02’39”E | M/s KEC International Ltd.
316 | A | 0 |  | 360 | 59359 | 32.73% | DFRU | P | LT Line | Lake | Normal |  |  | Paparapatti |  | II | 12°12’14”N | 078°02’41”E | M/s KEC International Ltd.
317 | B | 0 | 9°45' LT | 360 | 59719 | 32.93% | DFRU | P | LT Line |  | Normal |  |  | Paparapatti |  | II | 12°12’03”N | 078°02’44”E | M/s KEC International Ltd.
318 | A | 0 |  | 370 | 60079 | 33.13% | SFRU | P | 2 Nos. 11kV Line | Tar road | Normal |  |  | Paparapatti |  | II | 12°11’52”N | 078°02’48”E | M/s KEC International Ltd.
319 | C | 0 | 18°30' RT | 300 | 60449 | 33.33% | DFRU | CP | 33kV Line |  | Normal |  |  | Paparapatti |  | II | 12°11’42”N | 078°02’52”E | M/s KEC International Ltd.
320 | A | 6 |  | 400 | 60749 | 33.5% | DFRU | CP | 3 Nos.LT Line | Cart track | Normal |  |  | Paparapatti |  | II | 12°11’32”N | 078°02’53”E | M/s KEC International Ltd.
321 | A | 3 |  | 400 | 61149 | 33.72% | DFRU | P |  |  | Normal |  |  | Paparapatti |  | II | 12°11’19”N | 078°02’53”E | M/s KEC International Ltd.
322 | A | 0 |  | 390 | 61549 | 33.94% | DFRU | P |  |  | Normal |  |  | Paparapatti |  | II | 12°11’06”N | 078°02’54”E | M/s KEC International Ltd.
323 | A | 0 |  | 430 | 61939 | 34.15% | Dry | P |  |  | Normal |  |  | Paparapatti |  | II | 12°10’53”N | 078°02’55”E | M/s KEC International Ltd.
324 | A | 3 |  | 350 | 62369 | 34.39% | DFRU | P |  |  | Normal |  |  | Paparapatti |  | II | 12°10’40”N | 078°02’55”E | M/s KEC International Ltd.
325 | C | 0 | 17°18' 20" LT | 340 | 62719 | 34.58% | DFRU | CP |  |  | Normal |  |  | Indoore, Dharmapuri Dt. |  | II | 12°10’29”N | 078°02’56”E | M/s KEC International Ltd.
326 | A | 0 |  | 310 | 63059 | 34.77% | SFRU | CP |  |  | Normal | Boulders |  | Indoore |  | II | 12°10’18”N | 078°03’00”E | M/s KEC International Ltd.
327 | A | 0 |  | 410 | 63369 | 34.94% | 2-SFRU 2-FS | CP |  | Nala | Normal |  |  | Indoore |  | II | 12°10’09”N | 078°03’03”E | M/s KEC International Ltd.
328 | A | 0 |  | 320 | 63779 | 35.17% | 2-SFRU 2-DRFU | P |  |  | Normal |  |  | Indoore |  | II | 12°09’57”N | 078°03’08”E | M/s KEC International Ltd.
329 | A | 0 |  | 374 | 64099 | 35.34% | DFRU | CP |  | Tar road | Normal |  |  | Indoore |  | II | 12°09’48”N | 078°03’11”E | M/s KEC International Ltd.
330 | A | 3 |  | 396 | 64473 | 35.55% | DFRU | CP | 400kV Line |  | vulnerable |  |  | Indoore |  | II | 12°09’36”N | 078°03’16”E | M/s KEC International Ltd.
331 | A | 0 |  | 360 | 64869 | 35.77% | SFRU | P |  |  | vulnerable | Boulders |  | Indoore |  | II | 12°09’24”N | 078°03’20”E | M/s KEC International Ltd.
332 | C | 0 | TRANSPOSITION | 380 | 65229 | 35.97% | DFRU | P |  |  | Normal |  |  | Indoore |  | II | 12°09’13”N | 078°03’24”E | M/s KEC International Ltd.
333 | A | 0 |  | 400 | 65609 | 36.18% | DFRU | P |  | Cart track | Normal |  |  | Indoore |  | II | 12°09’02”N | 078°03’28”E | M/s KEC International Ltd.
334 | A | 0 |  | 390 | 66009 | 36.4% | DFRU | P |  | Metal road | Normal |  |  | Indoore |  | II | 12°08’50”N | 078°03’33”E | M/s KEC International Ltd.
335 | A | 0 |  | 350 | 66399 | 36.61% | DFRU | CP |  |  | Normal |  |  | Indoore |  | II | 12°08’38”N | 078°03’37”E | M/s KEC International Ltd.
336 | A | 0 |  | 396 | 66749 | 36.81% | Dry | P |  |  | Normal |  |  | Indoore |  | II | 12°08’27”N | 078°03’41”E | M/s KEC International Ltd.
337 | A | 0 |  | 425 | 67145 | 37.02% | DFRU | P | LT Line | Cart track | Normal |  |  | Indoore |  | II | 12°08’15”N | 078°03’46”E | M/s KEC International Ltd.
338 | D | 0 | 42°40'04" RT | 360 | 67570 | 37.26% | WBC | CP |  | Tar road | vulnerable |  |  | Indoore |  | II | 12°08’03”N | 078°03’51”E | M/s KEC International Ltd.
339 | A | 0 |  | 390 | 67930 | 37.46% | DFRU | P | LT Line | Lake, Canal | vulnerable |  |  | Indoore |  | II | 12°07’52”N | 078°03’46”E | M/s KEC International Ltd.
340 | A | 3 |  | 425 | 68320 | 37.67% | Wet | P | LT Line |  | Normal |  |  | Indoore |  | II | 12°07’40”N | 078°03’41”E | M/s KEC International Ltd.
341 | A | 3 |  | 389 | 68745 | 37.91% | Wet | CP |  |  | Normal |  |  | Indoore |  | II | 12°07’28”N | 078°03’36”E | M/s KEC International Ltd.
342 | C | 0 | 21°35' RT | 370 | 69134 | 38.12% | FS | CP | LT Line |  | Normal |  |  | Indoore |  | II | 12°07’16”N | 078°03’31”E | M/s KEC International Ltd.
343 | A | 0 |  | 360 | 69504 | 38.32% | DFRU | CP |  |  | Normal |  |  | Indoore |  | II | 12°07’08”N | 078°03’22”E | M/s KEC International Ltd.
344 | A | 0 |  | 354 | 69864 | 38.52% | 2-Dry 2-DRFU | CP |  |  | Normal |  |  | Indoore |  | II | 12°07’00”N | 078°03’14”E | M/s KEC International Ltd.
345 | D | 0 | 32°12' LT | 346 | 70218 | 38.72% | 2-Dry 2-DRFU | CP |  |  | Normal |  |  | Indoore |  | II | 12°06’52”N | 078°03’06”E | M/s KEC International Ltd.
346 | D | 0 | 39°00' LT | 275 | 70564 | 38.91% | DFRU | CP |  |  | Normal | Boulders, Rocky area |  | Nagarkoodal Near Nallapalli , Dharmapuri Dt, |  | II | 12°06’41”N | 078°03’04”E | M/s KEC International Ltd.
347 | A | 3 |  | 325 | 70839 | 39.06% | DFRU | CP |  | Nala | Normal | Boulders |  | Nagarkoodal Near Nallapalli |  | II | 12°06’33”N | 078°03’07”E | M/s KEC International Ltd.
348 | A | 3 |  | 240 | 71164 | 39.24% | DFRU | CP |  | Nala | Normal | Boulders |  | Nagarkoodal Near Nallapalli |  | II | 12°06’24”N | 078°03’11”E | M/s KEC International Ltd.
349 | B | 0 | 1°32' LT | 530 | 71404 | 39.37% | DFRU | CP |  | Nala | Normal | Boulders |  | Nagarkoodal Near Nallapalli |  | II | 12°06’17”N | 078°03’14”E | M/s KEC International Ltd.
350 | B | 0 | 3°04' RT | 392 | 71934 | 39.66% | DFRU | CP |  | Nala | Normal | Hilly area |  | Nagarkoodal Near Nallapalli |  | II | 12°06’01”N | 078°03’21”E | M/s KEC International Ltd.
351 | C | 0 | 19°16' RT | 320 | 72326 | 39.88% | DFRU | CP |  |  | Normal |  |  | Nagarkoodal Near Nallapalli |  | II | 12°05’50”N | 078°03’26”E | M/s KEC International Ltd.
352 | B | 0 |  | 360 | 72646 | 40.06% | DFRU | P |  | Nala | Normal |  |  | Nagarkoodal Near Nallapalli |  | II | 12°05’39”N | 078°03’26”E | M/s KEC International Ltd.
353 | A | 0 |  | 276 | 73006 | 40.26% | DFRU | P |  |  | Normal |  |  | Nagarkoodal Near Nallapalli |  | II | 12°05’28”N | 078°03’27”E | M/s KEC International Ltd.
354 | D | 0 | 31°55' LT | 390 | 73282 | 40.41% | 2-Dry 2-DRFU | P | 2 Nos. LT Line | Nala | Normal |  |  | Nagarkoodal Near Nallapalli |  | II | 12°05’19”N | 078°03’27”E | M/s KEC International Ltd.
355 | A | 3 |  | 415 | 73672 | 40.62% | Wet | P | LT Line | Nagavathi river, Canal | Normal |  |  | Nagarkoodal Near Nallapalli |  | II | 12°05’10”N | 078°03’35”E | M/s KEC International Ltd.
356 | A | 6 |  | 419 | 74087 | 40.85% | FS | CP |  | Nala | Normal |  |  | Nagarkoodal Near Nallapalli |  | II | 12°04’59”N | 078°03’43”E | M/s KEC International Ltd.
357 | B | 9 | 13°38' RT | 330 | 74506 | 41.08% | Dry | CP | 11kV Line | 2 Nos. Nala, Tar road | Normal |  |  | Nagarkoodal Near Nallapalli |  | II | 12°04’49”N | 078°03’52”E | M/s KEC International Ltd.
358 | B | 6 |  | 330 | 74836 | 41.26% | DFRU | CP |  | Nala | Normal |  |  | Nagarkoodal Near Nallapalli |  | II | 12°04’39”N | 078°03’56”E | M/s KEC International Ltd.
359 | C | 0 | 23°01'40" RT | 350 | 75166 | 41.45% | DFRU | CP |  |  | Normal |  |  | Nagarkoodal Near Nallapalli |  | II | 12°04’30”N | 078°04’01”E | M/s KEC International Ltd.
360 | A | - |  | 374 | 75516 | 41.64% | DFRU | CP |  |  |  | Hilly Area |  | Nagrkoodal |  | II | 12° 04′ 19 N | 078° 04′ 01 E | M/s KEC International Ltd.
361 | C | - | 18° 09' RT | 250 | 75890 | 41.85% | DFRU | CP |  |  |  | Hilly Area |  | Nagrkoodal |  | II | 12° 04′ 07 N | 078° 04′ 02 E | M/s KEC International Ltd.
362 | A | 6 |  | 466 | 76140 | 41.98% | DFRU | CP |  |  |  | Hilly Area |  | Nagrkoodal |  | II | 12° 04′ 00 N | 078° 03′ 59 E | M/s KEC International Ltd.
363 | A | 3 |  | 384 | 76606 | 42.24% | DFRU | CP |  |  |  | Hilly Area |  | Nagrkoodal |  | II | 12° 03′ 45 N | 078° 03′ 55 E | M/s KEC International Ltd.
364 | A | - |  | 396 | 76990 | 42.45% | DFRU | CP |  |  |  | Hilly Area |  | Nagrkoodal |  | II | 12° 03′ 33 N | 078° 03′ 52 E | M/s KEC International Ltd.
365 | A | 6 |  | 414 | 77386 | 42.67% | DFRU | CP |  |  |  | Plain |  | Nagrkoodal |  | II | 12° 03′ 21 N | 078° 03′ 49 E | M/s KEC International Ltd.
366 | A | - |  | 330 | 77800 | 42.9% | DFRU | CP |  |  |  | Plain |  | Nagrkoodal |  | II | 12° 03′ 09 N | 078° 03′ 45 E | M/s KEC International Ltd.
367 | A | - |  | 400 | 78130 | 43.08% | DRY | P |  |  |  | Plain |  | Nagrkoodal |  | II | 12° 02′ 59 N | 078° 03′ 42 E | M/s KEC International Ltd.
368 | A | 3 |  | 340 | 78530 | 43.3% | 3DFRU,1DRY | CP |  |  |  | Plain |  | Nagrkoodal |  | II | 12° 02′ 46 N | 078° 03′ 39 E | M/s KEC International Ltd.
369 | A | - |  | 410 | 78870 | 43.49% | DFRU | CP |  |  |  | Plain |  | Nagrkoodal |  | II | 12° 02′ 36 N | 078° 03′ 35 E | M/s KEC International Ltd.
370 | A | 6 |  | 440 | 79280 | 43.71% | DFRU | CP |  |  |  | Plain |  | Samisettipatti |  | II | 12° 02′ 23 N | 078° 03′ 32 E | M/s KEC International Ltd.
371 | A | - |  | 394 | 79720 | 43.96% | 2DFRU,2 DRY | CP |  |  |  | Plain |  | Samisettipatti |  | II | 12° 02′ 13 N | 078° 03′ 29 E | M/s KEC International Ltd.
372 | C | - | 19° 46' RT | 360 | 80114 | 44.17% | DFRU | CP |  |  |  | Plain |  | Samisettipatti |  | II | 12° 01′ 58 N | 078° 03′ 24 E | M/s KEC International Ltd.
373 | A | - |  | 360 | 80474 | 44.37% | 2DFRU,2 DRY | P |  |  |  | Plain |  | Samisettipatti |  | II | 12° 01′ 49 N | 078° 03′ 18 E | M/s KEC International Ltd.
374 | B | - | 03° 06' RT | 350 | 80834 | 44.57% | DFRU | CP |  |  |  | Plain |  | Samisettipatti |  | II | 12° 01′ 39 N | 078° 03′ 11 E | M/s KEC International Ltd.
375 | A | - |  | 350 | 81184 | 44.76% | DFRU | CP |  |  |  | Plain |  | Samisettipatti |  | II | 12° 01′ 30 N | 078° 03′ 04 E | M/s KEC International Ltd.
376 | A | - |  | 360 | 81534 | 44.96% | 3DFRU,1DRY | CP |  |  |  | Plain |  | Samisettipatti |  | II | 12° 01′ 22 N | 078° 02′ 59 E | M/s KEC International Ltd.
377 | A | - |  | 360 | 81894 | 45.16% | DFRU | CP |  |  |  | Plain |  | Samisettipatti |  | II | 12° 01′ 12 N | 078° 02′ 49 E | M/s KEC International Ltd.
378 | A | - |  | 290 | 82254 | 45.35% | 2DFRU,2 DRY | CP |  |  |  | Plain |  | Dasayam Kottai |  | II | 12° 01′ 03 N | 078° 02′ 42 E | M/s KEC International Ltd.
379 | D | - | 39° 00' LT | 430 | 82544 | 45.51% | DFRU | CP |  |  |  | Plain |  | Dasayam Kottai |  | II | 12° 00′ 56 N | 078° 02′ 36 E | M/s KEC International Ltd.
380 | A | - |  | 280 | 82974 | 45.75% | DRY | P |  |  |  | Plain |  | Dasayam Kottai |  | II | 12° 00′ 43 N | 078° 02′ 31 E | M/s KEC International Ltd.
381 | A | - |  | 390 | 83254 | 45.91% | DFRU | CP |  |  |  | Plain |  | Dasayam Kottai |  | II | 12° 00′ 35 N | 078° 02′ 29 E | M/s KEC International Ltd.
382 | A | - |  | 360 | 83644 | 46.12% | DFRU | CP |  |  |  | Plain |  | Dasayam Kottai |  | II | 12° 00′ 23 N | 078° 02′ 25 E | M/s KEC International Ltd.
383 | A | - |  | 360 | 84004 | 46.32% | 2DFRU,2 DRY | CP |  |  |  | Plain |  | Dasayam Kottai |  | II | 12° 00′ 12 N | 078° 02′ 21 E | M/s KEC International Ltd.
384 | A | - |  | 320 | 84364 | 46.52% | DFRU | CP |  |  |  | Plain |  | Dasayam Kottai |  | II | 12° 00′ 01 N | 078° 02′ 18 E | M/s KEC International Ltd.
385 | A | - |  | 324 | 84684 | 46.69% | DRY | P |  |  |  | Plain |  | Manikam Pudur |  | II | 11° 59′ 51 N | 078° 02′ 15 E | M/s KEC International Ltd.
386 | B | - | 05° 45' LT | 446 | 85008 | 46.87% | DFRU | CP |  |  |  | Plain |  | Manikam Pudur |  | II | 11° 59′ 41 N | 078° 02′ 11 E | M/s KEC International Ltd.
387 | A | 3 |  | 334 | 85454 | 47.12% | DRY | CP |  |  |  | Plain |  | Manikam Pudur |  | II | 11° 59′ 28 N | 078° 02′ 08 E | M/s KEC International Ltd.
388 | A | - |  | 466 | 85788 | 47.3% | DFRU | CP |  |  |  | Plain |  | Manikam Pudur |  | II | 11° 59′ 17 N | 078° 02′ 06 E | M/s KEC International Ltd.
389 | A | 3 |  | 374 | 86254 | 47.56% | DFRU | CP |  |  |  | Plain |  | Manikam Pudur |  | II | 11° 59′ 03N | 078° 02′ 03 E | M/s KEC International Ltd.
390 | A | - |  | 400 | 86628 | 47.77% | DFRU | CP |  |  |  | Plain |  | Manikam Pudur |  | II | 11° 58′ 51 N | 078° 02′ 00 E | M/s KEC International Ltd.
391 | A | - |  | 400 | 87028 | 47.99% | DFRU | CP |  |  |  | Plain |  | Manikam Pudur |  | II | 11° 58′ 38 N | 078° 01′ 57 E | M/s KEC International Ltd.
392 | A | - |  | 330 | 87428 | 48.21% | DFRU | CP |  |  |  | Plain |  | Manikam Pudur |  | II | 11° 58′ 26 N | 078° 01′ 54 E | M/s KEC International Ltd.
393 | A | - |  | 500 | 87758 | 48.39% | DRY | P |  |  |  | Plain |  | Manikam Pudur |  | II | 11° 58′ 15 N | 078° 01′ 52 E | M/s KEC International Ltd.
394 | B | - | 00° 00' | 480 | 88258 | 48.67% | DFRU | CP |  |  |  | Plain |  | Manikam Pudur |  | II | 11° 57′ 59 N | 078° 01′ 49 E | M/s KEC International Ltd.
395 | A | 6 |  | 302 | 88738 | 48.93% | 3FS,1SFRU | P |  |  |  | Plain |  | Malayappa Nagar |  | II | 11° 57′ 45 N | 078° 01′ 45 E | M/s KEC International Ltd.
396 | D | - | 34° 45' LT | 460 | 89040 | 49.1% | DFRU | CP |  |  |  | Plain |  | Malayappa Nagar |  | II | 11° 57′ 35 N | 078° 01′ 43 E | M/s KEC International Ltd.
397 | A | 6 |  | 266 | 89500 | 49.35% | DFRU | CP |  |  |  | Plain |  | Malayappa Nagar |  | II | 11° 57′ 21 N | 078° 01′ 49 E | M/s KEC International Ltd.
398 | B | 6 | 00° 00' | 284 | 89766 | 49.5% | DFRU | CP |  |  |  | Hilly Area |  | Malayappa Nagar |  | II | 11° 57′ 13 N | 078° 01′ 51 E | M/s KEC International Ltd.
399 | D | 9 | 00° 00' | 590 | 90050 | 49.65% | DFRU | CP |  |  |  | Hilly Area |  | Parigam |  | II | 11° 57′ 05 N | 078° 01′ 56 E | M/s KEC International Ltd.
400 | B | 6 | 00° 00' | 240 | 90640 | 49.98% | DFRU | CP |  |  |  | Hilly Area |  | Parigam |  | II | 11° 56′ 48 N | 078° 02′ 03 E | M/s KEC International Ltd.
401 | D | 6 | 26° 17' RT | 298 | 90880 | 50.11% | DFRU | CP+15m |  |  |  | Hilly Area |  | Parigam |  | II | 11° 56′ 42 N | 078° 02′ 06 E | M/s KEC International Ltd.
402 | D | 9 | 07° 30' RT | 312 | 91178 | 50.28% | DFRU | CP |  |  |  | Hilly Area |  | Parigam |  | II | 11° 56′ 31 N | 078° 02′ 05 E | M/s KEC International Ltd.
403 | C | - | 19° 36' RT | 360 | 91490 | 50.45% | DFRU | CP |  |  |  | Hilly Area |  | Parigam |  | II | 11° 56′ 22 N | 078° 02′ 03 E | M/s KEC International Ltd.
404 | A | 3 |  | 350 | 91850 | 50.65% | WET | P |  |  |  | Hilly Area |  | Parigam |  | II | 11° 56′ 12 N | 078° 01′ 56 E | M/s KEC International Ltd.
405 | A | - |  | 370 | 92200 | 50.84% | DRY | P |  |  |  | Plain |  | Parigam |  | II | 11° 56′ 02 N | 078° 01′ 51 E | M/s KEC International Ltd.
406 | A | - |  | 334 | 92570 | 51.04% | DFRU | CP |  |  |  | Plain |  | Parigam |  | II | 11° 55′ 52 N | 078° 01′ 45 E | M/s KEC International Ltd.
407 | A | - |  | 346 | 92904 | 51.23% | DRY | P |  |  |  | Plain |  | Parigam |  | II | 11° 55′ 43 N | 078° 01′ 39 E | M/s KEC International Ltd.
408 | A | - |  | 331 | 93250 | 51.42% | WET | P |  |  |  | Plain |  | Parigam |  | II | 11° 55′ 33 N | 078° 01′ 33 E | M/s KEC International Ltd.
409 | D | - | 55° 55' LT | 450 | 93581 | 51.6% | WET | P |  |  |  | Plain |  | Parigam |  | II | 11° 55′ 24 N | 078° 01′ 28 E | M/s KEC International Ltd.
410 | B | 9 | 00° 00' | 210 | 94031 | 51.85% | WET | P |  |  |  | Plain | Thoppur-Mettur SH crossing | Sentrayareddiyur |  | II | 11° 55′ 11 N | 078° 01′ 36 E | M/s KEC International Ltd.
411 | D | 9 | 00° 00' | 260 | 94241 | 51.96% | SFRU | P |  |  |  | Hilly Area | Singarapet-Mettur 230KV line | Sentrayareddiyur |  | II | 11° 55′ 05 N | 078° 01′ 36 E | M/s KEC International Ltd.
412 | D | 9 | 00° 00' | 328 | 94501 | 52.11% | 3DFRU,1DRY | P |  |  |  | Hilly Area |  | Sentrayareddiyur |  | II | 11° 54′ 58 N | 078° 01′ 41 E | M/s KEC International Ltd.
413 | C | - | 04° 58' RT | 380 | 94829 | 52.29% | DFRU | CP |  |  |  | Hilly Area |  | Sentrayareddiyur |  | II | 11° 54′ 47 N | 078° 01′ 44 E | M/s KEC International Ltd.
414 | A | - |  | 310 | 95209 | 52.5% | DFRU | CP |  |  |  | Hilly Area |  | Sentrayareddiyur |  | II | 11° 54′ 36 N | 078° 01′ 49 E | M/s KEC International Ltd.
415 | A | - |  | 370 | 95519 | 52.67% | DFRU | CP |  |  |  | Plain |  | Sentrayareddiyur |  | II | 11° 54′ 27 N | 078° 01′ 52 E | M/s KEC International Ltd.
416 | A | 3 |  | 239 | 95889 | 52.87% | DFRU | P |  |  |  | Plain |  | Pairan Kottai |  | II | 11° 54′ 16 N | 078° 01′ 55 E | M/s KEC International Ltd.
417 | D | - | 57° 26' RT | 380 | 96128 | 53% | DFRU | P |  |  |  | Plain |  | Pairan Kottai |  | II | 11° 54′ 09 N | 078° 01′ 58 E | M/s KEC International Ltd.
418 | A | 6 |  | 440 | 96508 | 53.21% | 2DRY, 2DFRU | P |  |  |  | Plain |  | Pairan Kottai |  | II | 11° 53′ 59 N | 078° 01′ 51 E | M/s KEC International Ltd.
419 | A | 3 |  | 410 | 96948 | 53.46% | 2DRY, 2DFRU | P |  |  |  | Plain |  | Pairan Kottai |  | II | 11° 53′ 48 N | 078° 01′ 42 E | M/s KEC International Ltd.
420 | A | - |  | 360 | 97358 | 53.68% | DFRU | CP |  |  |  | Plain |  | Pairan Kottai |  | II | 11° 53′ 37 N | 078° 01′ 34 E | M/s KEC International Ltd.
421 | A | 3 |  | 480 | 97718 | 53.88% | DRY | P |  |  |  | Plain |  | Thasanur |  | II | 11° 53′ 28 N | 078° 01′ 27 E | M/s KEC International Ltd.
422 | D | 9 | 05° 00' RT | 200 | 98198 | 54.15% | DFRU | P |  |  |  | Plain | 110kv Erumapatti-Thumpipadi line | Thasanur |  | II | 11° 53′ 16 N | 078° 01′ 17 E | M/s KEC International Ltd.
423 | D | 9 | 04° 40' LT | 456 | 98398 | 54.26% | SFRU | P |  |  |  | Plain |  | Thasanur |  | II | 11° 53′ 11 N | 078° 01′ 13 E | M/s KEC International Ltd.
424 | A | - |  | 344 | 98854 | 54.51% | DFRU | P |  |  |  | Plain |  | Thasanur |  | II | 11° 53′ 00 N | 078° 01′ 04 E | M/s KEC International Ltd.
425 | A | - |  | 430 | 99198 | 54.7% | DFRU | CP |  |  |  | Plain |  | Thasanur |  | II | 11° 52′ 51 N | 078° 00′ 57 E | M/s KEC International Ltd.
426 | A | 6 |  | 340 | 99628 | 54.93% | 2DRY, 2DFRU | P |  |  |  | Plain |  | Thasanur |  | II | 11° 52′ 40 N | 078° 00′ 49 E | M/s KEC International Ltd.
427 | C | - | 20° 38' LT | 360 | 99968 | 55.12% | DFRU | CP |  |  |  | Plain |  | Thasanur |  | II | 11° 52′ 31 N | 078° 00′ 42 E | M/s KEC International Ltd.
428 | A | - |  | 450 | 100328 | 55.32% | DFRU | CP |  |  |  | Plain |  | Thasanur |  | II | 11° 52′ 20 N | 078° 00′ 38 E | M/s KEC International Ltd.
429 | A | - |  | 380 | 100778 | 55.57% | DFRU | CP |  |  |  | Plain |  | Thasanur |  | II | 11° 52′ 06 N | 078° 00′ 34 E | M/s KEC International Ltd.
430 | A | - |  | 410 | 101158 | 55.78% | DFRU | CP |  |  |  | Plain |  | Thasanur |  | II | 11° 51′ 55 N | 078° 00′ 31 E | M/s KEC International Ltd.
431 | A | 3 |  | 320 | 101568 | 56% | DFRU | CP |  |  |  | Plain |  | Maniyakaranur |  | II | 11° 51′ 42 N | 078° 00′ 27 E | M/s KEC International Ltd.
432 | A | - |  | 410 | 101888 | 56.18% | DFRU | CP |  |  |  | Plain |  | Maniyakaranur |  | II | 11° 51′ 32 N | 078° 00′ 24 E | M/s KEC International Ltd.
433 | A | - |  | 350 | 102298 | 56.41% | DFRU | CP |  |  |  | Plain |  | Maniyakaranur |  | II | 11° 51′ 20 N | 078° 00′ 20 E | M/s KEC International Ltd.
434 | A | 6 |  | 410 | 102648 | 56.6% | DFRU | CP |  |  |  | Plain |  | Maniyakaranur |  | II | 11° 51′ 09 N | 078° 00′ 17 E | M/s KEC International Ltd.
435 | B | 3 | 06° 40' LT | 364 | 103058 | 56.83% | DFRU | CP |  |  |  | Hilly Area |  | Maniyakaranur |  | II | 11° 50′ 57 N | 078° 00′ 13 E | M/s KEC International Ltd.
436 | A | 6 |  | 451 | 103422 | 57.03% | DFRU | CP |  |  |  | Hilly Area |  | Maniyakaranur |  | II | 11° 50′ 46 N | 078° 00′ 11 E | M/s KEC International Ltd.
437 | B | 9 | 11° 07' RT | 350 | 103873 | 57.28% | DFRU | CP |  |  |  | Hilly Area |  | Maniyakaranur |  | II | 11° 50′ 32 N | 078° 00′ 08 E | M/s KEC International Ltd.
438 | A | - |  | 310 | 104223 | 57.47% | DFRU | CP |  |  |  | Hilly Area |  | Marakottai |  | II | 11° 50′ 21 N | 078° 00′ 04 E | M/s KEC International Ltd.
439 | A | 3 |  | 320 | 104533 | 57.64% | DFRU | CP |  |  |  | Hilly Area |  | Marakottai |  | II | 11° 50′ 12 N | 078° 00′ 00 E | M/s KEC International Ltd.
440 | A | 3 |  | 360 | 104853 | 57.82% | DFRU | CP |  |  |  | Hilly Area |  | Marakottai |  | II | 11° 50′ 02 N | 077° 59′ 57 E | M/s KEC International Ltd.
441 | B | - | 02° 08' LT | 360 | 105213 | 58.01% | DFRU | CP |  |  |  | Hilly Area |  | Marakottai |  | II | 11° 49′ 52 N | 077° 59′ 53 E | M/s KEC International Ltd.
442 | A | 3 |  | 390 | 105573 | 58.21% | DFRU | CP |  |  |  | Hilly Area |  | Marakottai |  | II | 11° 49′ 41 N | 077° 59′ 49 E | M/s KEC International Ltd.
443 | A | - |  | 350 | 105963 | 58.43% | DFRU | CP |  |  |  | Hilly Area |  | Marakottai |  | II | 11° 49′ 29 N | 077° 59′ 45 E | M/s KEC International Ltd.
444 | A | - |  | 300 | 106313 | 58.62% | DFRU | CP |  |  |  | Hilly Area |  | Marakottai |  | II | 11° 48′ 57 N | 077° 59′ 34 E | M/s KEC International Ltd.
445 | A | - |  | 400 | 106613 | 58.79% | DFRU | CP |  |  |  | Hilly Area |  | Semmanur |  | II | 11° 48′ 45 N | 077° 59′ 30 E | M/s KEC International Ltd.
446 | A | - |  | 400 | 107013 | 59.01% | DFRU | CP |  |  |  | Plain |  | Semmanur |  | II | 11° 48′ 39 N | 077° 59′ 37 E | M/s KEC International Ltd.
447 | A | - |  | 374 | 107413 | 59.23% | DFRU | CP |  |  |  | Plain |  | Semmanur |  | II | 11° 48′ 37 N | 077° 59′ 35 E | M/s KEC International Ltd.
448 | A | - |  | 326 | 107787 | 59.43% | DFRU | CP |  |  |  | Plain |  | Semmanur |  | II | 11° 48′ 34 N | 077° 59′ 26 E | M/s KEC International Ltd.
449 | A | - |  | 410 | 108113 | 59.61% | DFRU | CP |  |  |  | Plain |  | Semmanur |  | II | 11° 48′ 24 N | 077° 59′ 22 E | M/s KEC International Ltd.
450 | A | - |  | 370 | 108523 | 59.84% | DFRU | CP |  |  |  | Plain |  | Semmanur |  | II | 11° 48′ 11 N | 077° 59′ 18 E | M/s KEC International Ltd.
451 | A | - |  | 315 | 108893 | 60.04% | DFRU | CP |  |  |  | Plain |  | Semmanur |  | II | 11° 48′ 00 N | 077° 59′ 14 E | M/s KEC International Ltd.
452 | D | - | 32° 30' RT | 390 | 109208 | 60.22% | DFRU | CP |  |  |  | Plain |  | Semmanur |  | II | 11° 47′ 51 N | 077° 59′ 11 E | M/s KEC International Ltd.
453 | A | 6 |  | 422 | 109598 | 60.43% | DFRU | CP |  |  |  | Plain | Omallur-Mecherry SH crossing | Kamaneri |  | II | 11° 47′ 43 N | 077° 59′ 01 E | M/s KEC International Ltd.
454 | D | - | 39° 00' LT | 310 | 110020 | 60.66% | DFRU | CP |  |  |  | Plain |  | Kamaneri |  | II | 11° 47′ 34 N | 077° 58′ 50 E | M/s KEC International Ltd.
455 | A | 3 |  | 494 | 110330 | 60.84% | DRY | P |  |  |  | Plain |  | Kamaneri |  | II | 11° 47′ 25 N | 077° 58′ 48 E | M/s KEC International Ltd.
456 | A | 3 |  | 316 | 110824 | 61.11% | DFRU | P |  |  |  | Plain |  | Kamaneri |  | II | 11° 47′ 09 N | 077° 58′ 44 E | M/s KEC International Ltd.
457 | A | 6 |  | 436 | 111140 | 61.28% | DFRU | P |  |  |  | Plain |  | Kamaneri |  | II | 11° 47′ 00 N | 077° 58′ 41 E | M/s KEC International Ltd.
458 | D | - | 45° 15' LT | 360 | 111576 | 61.52% | DFRU | CP |  |  |  | Plain |  | Naikanur |  | II | 11° 46′ 46 N | 077° 58′ 38 E | M/s KEC International Ltd.
459 | A | - |  | 370 | 111936 | 61.72% | WET | P |  |  |  | Plain |  | Naikanur |  | II | 11° 46′ 36 N | 077° 58′ 44 E | M/s KEC International Ltd.
460 | A | - |  | 330 | 112306 | 61.93% | DFRU | P |  |  |  | Plain |  | Naikanur |  | II | 11° 46′ 26 N | 077° 58′ 50 E | M/s KEC International Ltd.
461 | A | - |  | 360 | 112636 | 62.11% | WET | P |  |  |  | Plain |  | Naikanur |  | II | 11° 46′ 17 N | 077° 58′ 56 E | M/s KEC International Ltd.
462 | C | - | 15° 30' LT | 398 | 112996 | 62.31% | DFRU | P |  |  |  | Plain |  | Naikanur |  | II | 11° 45′ 49 N | 077° 59′ 21 E | M/s KEC International Ltd.
463 | A | 6 |  | 440 | 113394 | 62.53% | 2DRY,2DFRU | P |  |  |  | Plain |  | Naikanur |  | II | 11° 45′ 49 N | 077° 59′ 21 E | M/s KEC International Ltd.
464 | B | 3 | 00° 00' | 458 | 113834 | 62.77% | WET | P |  |  |  | Plain |  | Naikanur |  | II | 11° 45′ 49 N | 077° 59′ 21 E | M/s KEC International Ltd.
465 | D | - | 52° 40' RT | 225 | 114292 | 63.02% | FS | 2P |  |  |  | Plain | Railway crossing | Naikanur |  | II | 11° 45′ 38 N | 077° 59′ 32 E | M/s KEC International Ltd.
466 | D | 6 | 09° 47' LT | 370 | 114517 | 63.14% | FS | 2P |  |  |  | Plain |  | Thulasampatty |  | II | 11° 45′ 31 N | 077° 59′ 31 E | M/s KEC International Ltd.
467 | A | - |  | 410 | 114887 | 63.35% | DFRU | CP |  |  |  | Plain |  | Thulasampatty |  | II | 11° 45′ 20 N | 077° 59′ 32 E | M/s KEC International Ltd.
468 | A | - |  | 345 | 115297 | 63.57% | 2DRY,2DFRU | CP |  |  |  | Plain | 110kv S/C crossing | Thulasampatty |  | II | 11° 45′ 06 N | 077° 59′ 32 E | M/s KEC International Ltd.
469 | C | - | 26° 40' LT | 402 | 115642 | 63.76% | 2DRY,2DFRU | CP |  |  |  | Plain |  | Thulasampatty |  | II | 11° 44′ 55 N | 077° 59′ 39 E | M/s KEC International Ltd.
470 | C | - | 22° 00' RT | 440 | 116044 | 63.99% | DFRU | CP |  |  |  | Plain |  | Thulasampatty |  | II | 11° 44′ 44 N | 077° 59′ 39 E | M/s KEC International Ltd.
471 | A | 6 |  | 393 | 116484 | 64.23% | DFRU | CP |  |  |  | Plain |  | Thulasampatty |  | II | 11° 44′ 30 N | 077° 59′ 41 E | M/s KEC International Ltd.
472 | C | - | 17° 43' LT | 345 | 116877 | 64.45% | DFRU | CP |  |  |  | Plain |  | Thulasampatty |  | II | 11° 44′ 18 N | 077° 59′ 43 E | M/s KEC International Ltd.
473 | A | - |  | 335 | 117222 | 64.64% | DFRU | CP |  |  |  | Plain |  | Reddipatty |  | II | 11° 44′ 08 N | 077° 59′ 47 E | M/s KEC International Ltd.
474 | A | - |  | 380 | 117557 | 64.82% | DFRU | CP |  |  |  | Plain |  | Reddipatty |  | II | 11° 43′ 58 N | 077° 59′ 52 E | M/s KEC International Ltd.
475 | C | - | 27° 20' RT | 315 | 117937 | 65.03% | DFRU | P |  |  |  | Plain |  | Reddipatty |  | II | 11° 43′ 47 N | 077° 59′ 57 E | M/s KEC International Ltd.
476 | A | - |  | 355 | 118252 | 65.2% | DRY | CP |  |  |  | Plain |  | Reddipatty |  | II | 11° 43′ 37 N | 077° 59′ 57 E | M/s KEC International Ltd.
477 | A | - |  | 390 | 118607 | 65.4% | DRY | CP |  |  |  | Plain |  | Reddipatty |  | II | 11° 43′ 25 N | 077° 59′ 59 E | M/s KEC International Ltd.
478 | A | - |  | 367 | 118997 | 65.61% | WET | P |  |  |  | Plain |  | Reddipatty |  | II | 11° 43′ 13 N | 077° 59′ 56 E | M/s KEC International Ltd.
479 | B | - | 05° 20' LT | 250 | 119364 | 65.82% | WET | P |  |  |  | Plain |  | Thottiyanur |  | II | 11° 43′ 01 N | 077° 59′ 55 E | M/s KEC International Ltd.
480 | A | 3 |  | 410 | 119614 | 65.95% | FS | P |  |  |  | Plain |  | Thottiyanur |  | II | 11° 42′ 53 N | 077° 59′ 56 E | M/s KEC International Ltd.
481 | A | - |  | 340 | 120024 | 66.18% | DFRU | P |  |  |  | Plain |  | Thottiyanur |  | II | 11° 42′ 30 N | 077° 59′ 56 E | M/s KEC International Ltd.
482 | A | - |  | 300 | 120364 | 66.37% | DFRU | P |  |  |  | Plain |  | Thottiyanur |  | II | 11° 42′ 29 N | 077° 59′ 56 E | M/s KEC International Ltd.
483 | D | - | 37° 50' RT | 300 | 120664 | 66.53% | DFRU | CP |  |  |  | Plain |  | Thottiyanur |  | II | 11° 42′ 20 N | 077° 59′ 57 E | M/s KEC International Ltd.
484 | A | - |  | 360 | 120964 | 66.7% | FS | P |  |  |  | Plain |  | Thottiyanur |  | II | 11° 42′ 12 N | 077° 59′ 51 E | M/s KEC International Ltd.
485 | D | - | 56° 20' LT | 420 | 121324 | 66.9% | DFRU | CP |  |  |  | Plain |  | Thottiyanur |  | II | 11° 42′ 02 N | 077° 59′ 45 E | M/s KEC International Ltd.
486 | A | 6 |  | 396 | 121744 | 67.13% | WET | P |  |  |  | Plain |  | Thottiyanur |  | II | 11° 41′ 49 N | 077° 59′ 49 E | M/s KEC International Ltd.
487 | D | - | 55° 05' RT | 410 | 122140 | 67.35% | DFRU | CP |  |  |  | Plain |  | Thottiyanur |  | II | 11° 41′ 38 N | 077° 59′ 54 E | M/s KEC International Ltd.
488 | A | 6 |  | 381 | 122550 | 67.57% | 2DRY,2DFRU | CP |  |  |  | Plain |  | Thottiyanur |  | II | 11° 41′ 27 N | 077° 59′ 47 E | M/s KEC International Ltd.
489 | D | 3 | 39° 45' LT | 310 | 122931 | 67.78% | DFRU | CP |  |  |  | Plain |  | Athikattanur |  | II | 11° 41′ 16 N | 077° 59′ 40 E | M/s KEC International Ltd.
490 | A | - |  | 360 | 123241 | 67.95% | DRY | P |  |  |  | Plain |  | Athikattanur |  | II | 11° 40′ 55 N | 077° 59′ 42 E | M/s KEC International Ltd.
491 | C | - | 00° 00' | 355 | 123601 | 68.15% | DFRU | P |  |  |  | Plain |  | Athikattanur |  | II | 11° 40′ 40 N | 077° 59′ 45 E | M/s KEC International Ltd.
492 | D | 9 | 22° 02' LT | 152 | 123956 | 68.35% | FS | P |  |  |  | Plain | 230 kv crossing | Athikattanur |  | II | 11° 40′ 40 N | 077° 59′ 43 E | M/s KEC International Ltd.
493 | D | 9 | 02° 10' RT | 470 | 124108 | 68.43% | WBC | P |  |  |  | Plain |  | Athikattanur |  | II | 11° 40′ 26 N | 077° 59′ 52 E | M/s KEC International Ltd.
494 | D | - | 31° 23' 36"RT | 250 | 124578 | 68.69% | WET | P |  |  |  | Plain |  | Krishnampudur |  | II | 11° 40′ 18 N | 078° 00′ 10 E | M/s KEC International Ltd.
495 | C | 3 | 28° 20' LT | 357 | 124828 | 68.83% | WET | P |  |  |  | Plain |  | Krishnampudur |  | II | 11° 40′ 18 N | 077° 59′ 53 E | M/s KEC International Ltd.
496 | C | - | 23° 23' LT | 242 | 125185 | 69.03% | DFRU | P |  |  |  | Plain |  | Krishnampudur |  | II | 11° 40′ 08 N | 077° 59′ 58 E | M/s KEC International Ltd.
497 | D | - | 55° 50' LT | 115 | 125427 | 69.16% | DFRU | CP |  |  |  | Plain |  | Krishnampudur |  | II | 11° 40′ 07 N | 077° 59′ 41 E | M/s KEC International Ltd.
498 | D | - | 57° 46' 20" LT | 130 | 125542 | 69.22% | DFRU | CP |  |  |  | Plain |  | Krishnampudur |  | II | 11° 40′ 04 N | 078° 00′ 00 E | M/s KEC International Ltd.
499 | D | - | 00° 00' | 85 | 125672 | 69.3% | DFRU | CP |  |  |  | Plain |  | Krishnampudur |  | II | 11° 40′ 04 N | 078° 00′ 00 E | M/s KEC International Ltd.
SLM GTY |  |  | 2˚ 42' LT |  | 125757

## T Sch_ (hidden)
PROPOSED NEW ALIGHNMENT TOWER SCHEDULE BETWEEN TOWER NO 141-157 OF 400 KV NNTPS-PONDY SINGLE CIRCUIT LINE
SLNO | AP NO | TOWER TYPE | ANGLE | SPAN | Section Length (m) | Section Chainage (m) | Wind Span (m) | Adjacent Span |  |  | Weight Span (Cold) |  |  | Weight Span (Hot) |  |  | Easting | Northing | Elevation | Twr Extn | Major Crossings (with in 23m either side from CL)/Remarks
[8 empty] | Left | Right | Total | Left | Right | Total | Left | Right | Total
1 | 138 | B
330
2 | 139 | K
380
3 | 140 | K
330
4 | NYV-MDS-141 | K | 0°00'00" |  |  |  | 174.5 | 0 | 349 | 349 | 0 | 173.74 | 173.74 | 0 | 173.995 | 173.995 | 345159.427 | 1315317.367 | 28.033
|  |  |  | 349 | [16 empty] | 11KV LINE, 11KV LINE
5 | NYV-MDS-142 | K |  |  |  |  | 354.5 | 349 | 360 | 709 | 175.038 | 135.485 | 310.523 | 174.783 | 154.035 | 328.818 | 345278.365 | 1315645.238 | 28.121
|  |  |  | 360 | [16 empty] | METALLED ROAD, 11KV LINE
6 | NYV-MDS-143 NEW | DD+6 |  |  |  |  | 339 | 360 | 318 | 678 | 224.197 | 159.604 | 383.801 | 205.647 | 159.449 | 365.096 | 345401.022 | 1315983.36 | 28.296
|  |  |  | 318 | [16 empty] | VILLUPURAM TO NAGAPATTINAM HIGHWAY
7 | NYV-MDS-144-NEW | DD+6 |  |  |  |  | 358.5 | 318 | 399 | 717 | 158.866 | 201.632 | 360.498 | 159.021 | 200.731 | 359.752 | 345509.625 | 1316282.741 | 28.251
|  |  |  | 399 | [16 empty] | 11kV LINE, METALLED ROAD, 11kV LINE
8 | NYV-MDS-145 | K+6 |  |  |  |  | 408.5 | 399 | 418 | 817 | 197.322 | 206.479 | 403.801 | 198.223 | 207.473 | 405.696 | 345645.674 | 1316657.78 | 27.917
|  |  |  | 418 | [16 empty] | NILL
9 | NYV-MDS-146 | K+6 |  |  |  |  | 398 | 418 | 378 | 796 | 211.247 | 230.772 | 442.019 | 210.253 | 213.175 | 423.428 | 345788.125 | 1317050.467 | 28.304
|  |  |  | 378 | [16 empty] | NILL
10 | NYV-MDS-147 | D | 0°02'16"(LT) |  | 2222 | 2222 | 273 | 378 | 168 | 546 | 146.589 | 0 | 146.589 | 164.186 | 21.574 | 185.76 | 345916.81 | 1317405.208 | 28.153
|  |  |  | 168 | [16 empty] | METALLED, RAILWAY TRACK
11 | NYV-MDS-148 | D+6 | 40°21'41"(RT) |  | 168 | 2390 | 227.5 | 168 | 287 | 455 | 167.593 | 189.899 | 357.492 | 146.029 | 177.259 | 323.288 | 345973.862 | 1317562.803 | 29.079
|  |  |  | 287 | [16 empty] | 11KV LINE
12 | NYV-MDS-149 | K |  |  |  |  | 303.5 | 287 | 320 | 607 | 96.937 | 159.545 | 256.482 | 109.577 | 159.701 | 269.278 | 346222.923 | 1317705.082 | 28.628
|  |  |  | 320 | [16 empty] | METALLED ROAD
13 | NYV-MDS-150-NEW | DD+0 | 28°00'36"(RT) |  | 607 | 2997 | 294 | 320 | 268 | 588 | 160.836 | 114.26 | 275.096 | 160.68 | 119.626 | 280.306 | 346501.111 | 1317864 | 28.728
|  |  |  | 268 | [16 empty] | LT LINE, METALLED ROAD, LT LINE, 11kV LINE
14 | NYV-MDS-150A-NEW | DD+3 |  |  |  |  | 211.5 | 268 | 155 | 423 | 153.749 | 87.509 | 241.258 | 148.383 | 84.717 | 233.1 | 346768.999 | 1317872.081 | 28.289
|  |  |  | 155 | [16 empty] | VILLUPURAM TO NAGAPATTINAM HIGHWAY
15 | NYV-MDS-151-NEW | DD+3 | 56°10'07"(LT) |  | 423 | 3420 | 178.5 | 155 | 202 | 357 | 67.023 | 0 | 67.023 | 69.815 | 0 | 69.815 | 346923.46 | 1317876.74 | 27.524
|  |  |  | 202 | [16 empty] | METALLED ROAD
16 | NYV-MDS-151A-NEW | DD+18 | 37°58'41"(RT) |  | 202 | 3622 | 167.5 | 202 | 133 | 335 | 202.088 | 65.847 | 267.935 | 202.088 | 66.075 | 268.163 | 347030.866 | 1318047.937 | 27.958
|  |  |  | 133 | [16 empty] | 230kV LINE, LT LINE
17 | NYV-MDS-152-NEW | DD+18 | 24°01'28"(LT) |  | 133 | 3755 | 211 | 133 | 289 | 422 | 67.376 | 212.616 | 279.992 | 67.148 | 194.074 | 261.222 | 347156.12 | 1318093.324 | 28.006
|  |  |  | 289 | [16 empty] | 11kV LINE, 11kV LINE, METALLED ROAD, 11kV LINE
18 | NYV-MDS-153-NEW | DD+9 | 30°58'37"(LT) |  | 289 | 4044 | 303.5 | 289 | 318 | 607 | 76.159 | 221.79 | 297.949 | 94.701 | 204.707 | 299.408 | 347364.047 | 1318293.717 | 27.47
|  |  |  | 318 | [16 empty] | VILLUPURAM TO NAGAPATTINAM HIGHWAY, METALLED ROAD, 11kV LINE
19 | NYV-MDS-154 | D | 13°30'27"(RT) |  | 318 | 4362 | 286 | 318 | 254 | 572 | 96.268 | 125.344 | 221.612 | 113.351 | 125.715 | 239.066 | 347446.796 | 1318600.821 | 26.807
|  |  |  | 254 | [16 empty] | NILL
20 | NYV-MDS-155 | K |  |  |  |  | 250 | 254 | 246 | 500 | 128.098 | 142.329 | 270.427 | 127.727 | 137.127 | 264.854 | 347568.069 | 1318823.365 | 26.974
|  |  |  | 246 | [16 empty] | 11KV LINE
21 | NYV-MDS-156 | D | 34°10'51"(LT) |  | 499 | 4861 | 267.5 | 246 | 289 | 535 | 103.992 | 102.62 | 206.612 | 109.194 | 113.969 | 223.163 | 347685.934 | 1319039.656 | 24.69
|  |  |  | 289 | [16 empty] | 33KV LINE, 11KV LINE
22 | NYV-MDS-157 | K+6 | 0°00'00" |  | 289 | 5150 | 144.5 | 289 | 0 | 289 | 186.119 | 0 | 186.119 | 174.77 | 0 | 174.77 | 347657.793 | 1319327.021 | 24.521
New Towers
[5 empty] | New Tower | Qty
[5 empty] | DD+0 | 1
[5 empty] | DD+3 | 2
[5 empty] | DD+6 | 2
[5 empty] | DD+9 | 1
[5 empty] | DD+18 | 2
[5 empty] | Total | 8
[5 empty] | Dismantling Tower | Qty
[5 empty] | K | 3
[5 empty] | K+3 | 2
[5 empty] | D+0 | 1
[5 empty] | Total | 6
[5 empty] | NH Clearance. | span -Mtrs | Clearance
[5 empty] | 143 New-144 New | 318 | 18
[5 empty] | 150 A-151 New. | 155 | 17.9
[5 empty] | 153-154 | 318 | 16
| Pilot fittings |  | 0
| Suspension Fittings |  | 0
| Tension Fittings-Twin |  | 0
| Rigid Spacers-Twin |  | 18
| Line Spacers-Twin |  | 0
| 120 kn Insulator |  | 0
| 160 Kn Insulator |  | 0
| Conductor |  | 0
| Earthwire |  | 0
| MSCJ for Conductor |  | 0
| Repair Sleeve for Conductor |  | 0
| Tconn_C |  | 0
| FL_Al_Bond for EW |  | 2
| VD for EW |  | 4
| Suspension clamp for EW |  | 0
| Tension Claimp For EW |  | 2
| MSCJ for EW |  | 0

## Twer Wt Ariyalur (hidden)
POWER GRID CORPORATION OF INDIA LIMITED
Project Name:- 400KV D/C NNTPS-Ariyalur Transmission Line
Project Code:-UP-225
[5 empty] | STUB FOR TOWER | [5 empty] | SUPER STRUCTURE
SL. No. | Loc No | Tower Type | Span | SECTION LENGTH(M) | HT | MS | Nuts & Bolts | Pack Washer | ACC | Total | HT | MS | Nuts & Bolts | Pack Washer | ACC | Total
| TAPING POINT | MD+3
|  |  | 226.5 | 226.5
1 | AP1/0 | DD+9 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 19345.61 | 16190.28 | 1575.43 | 77.2 | 14.04 | 37202.56
|  |  | 232.8 | 232.8
2 | AP2/0 | DD+9 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 19345.61 | 16190.28 | 1575.43 | 77.2 | 14.04 | 37202.56
|  |  | 300.9 | 655.9
3 | 2/1 | DA+6 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4533.16 | 10314.29 | 672.02 | 7.28 | 16.8 | 15543.55
355
4 | AP3/0 | DD+18 |  |  | 1339.28 | 0 | 30.21 | 0 | 0 | 1369.49 | 22496.01 | 24518.42 | 1938.89 | 91.12 | 14.04 | 49058.48
|  |  | 157.1 | 157.1
5 | AP4/0 | DD+18 |  |  | 1339.28 | 0 | 30.21 | 0 | 0 | 1369.49 | 22496.01 | 24518.42 | 1938.89 | 91.12 | 14.04 | 49058.48
|  |  | 274.2 | 274.2
6 | AP5/0 | DD+3 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 18730.53 | 10141.76 | 1290.87 | 55.58 | 14.04 | 30232.78
|  |  | 159.2 | 159.2
7 | AP6/0 | DD+3 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 18730.53 | 10141.76 | 1290.87 | 55.58 | 14.04 | 30232.78
|  |  | 235.1 | 235.1
8 | AP7/0 | DD+25 |  |  | 1339.28 | 0 | 30.21 | 0 | 0 | 1369.49 | 24809.65 | 34369.86 | 2195.98 | 105.48 | 14.04 | 61495.01
|  |  | 136.2 | 136.2
9 | AP8/0 | DD+18 |  |  | 1339.28 | 0 | 30.21 | 0 | 0 | 1369.49 | 22496.01 | 24518.42 | 1938.89 | 91.12 | 14.04 | 49058.48
|  |  | 153.6 | 153.6
10 | AP9/0 | DD+0 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 16415.01 | 10718.52 | 1272.94 | 57.69 | 14.04 | 28478.2
|  |  | 291.7 | 291.7
11 | AP10/0 | DD+9 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 19345.61 | 16190.28 | 1575.43 | 77.2 | 14.04 | 37202.56
|  |  | 235.4 | 235.4
12 | AP11/0 | DB+6 |  |  | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 14354.36 | 11492.6 | 1238.95 | 76.89 | 0 | 27162.8
|  |  | 336.6 | 681.6
13 | 11/1 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
345
14 | AP12/0 | DB+3 |  |  | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 13901.56 | 8699 | 1114.9 | 64.13 | 0 | 23779.59
|  |  | 386 | 1533
15 | 12/1 | DA+6 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4533.16 | 10314.29 | 672.02 | 7.28 | 16.8 | 15543.55
385
16 | 12/2 | DA+6 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4533.16 | 10314.29 | 672.02 | 7.28 | 16.8 | 15543.55
385
17 | 12/3 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
377
18 | AP13/0 | DC+3 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 15864.24 | 8424.81 | 1199.12 | 36.09 | 0 | 25524.26
|  |  | 315.3 | 748.7
19 | 13/1 | DB+6 |  |  | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 14354.36 | 11492.6 | 1238.95 | 76.89 | 0 | 27162.8
433.4
20 | AP14/0 | DD+6 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 18481.09 | 15064.6 | 1498.65 | 72.49 | 14.04 | 35130.87
|  |  | 325 | 1016.5
21 | 14/1 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
330
22 | 14/2 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
361.5
23 | AP15/0 | DD+18 |  |  | 1339.28 | 0 | 30.21 | 0 | 0 | 1369.49 | 22496.01 | 24518.42 | 1938.89 | 91.12 | 14.04 | 49058.48
|  |  | 236.1 | 236.1
24 | AP16/0 | DD+18 |  |  | 1339.28 | 0 | 30.21 | 0 | 0 | 1369.49 | 22496.01 | 24518.42 | 1938.89 | 91.12 | 14.04 | 49058.48
|  |  | 248.226 | 248.226
25 | AP17/0 | DD+3 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 18730.53 | 10141.76 | 1290.87 | 55.58 | 14.04 | 30232.78
|  |  | 387.331 | 387.331
26 | AP18/0 | DC+3 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 15864.24 | 8424.81 | 1199.12 | 36.09 | 0 | 25524.26
|  |  | 400 | 400
27 | 18/1 | DA+6 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4533.16 | 10314.29 | 672.02 | 7.28 | 16.8 | 15543.55
|  |  | 401 | 401
28 | AP19/0 | DC+9 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 19007.84 | 10765.75 | 1461.12 | 45.22 | 0 | 31279.93
|  |  | 462.407 | 462.407
29 | AP20/0 | DD+6 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 18481.09 | 15064.6 | 1498.65 | 72.49 | 14.04 | 35130.87
|  |  | 395.003 | 740.703
30 | 20/1 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
345.7
31 | AP21/0 | DB+3 |  |  | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 13901.56 | 8699 | 1114.9 | 64.13 | 0 | 23779.59
|  |  | 370 | 1479
32 | 21/1 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
380
33 | 21/2 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
367
34 | 21/3 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
362
35 | AP22/0 | DC+3 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 15864.24 | 8424.81 | 1199.12 | 36.09 | 0 | 25524.26
|  |  | 380 | 1855.504
36 | 22/1 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
380.004
37 | 22/2 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
330
38 | 22/3 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
400
39 | 22/4 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
365.5
40 | AP23/0 | DD+3 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 18730.53 | 10141.76 | 1290.87 | 55.58 | 14.04 | 30232.78
|  |  | 390 | 1512
41 | 23/1 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
400
42 | 23/2 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
325
43 | 23/3 | DA+6 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4533.16 | 10314.29 | 672.02 | 7.28 | 16.8 | 15543.55
397
44 | AP24/0 | DC+6 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 16850.4 | 11216.29 | 1372.8 | 44.38 | 0 | 29483.87
|  |  | 400 | 816
45 | 24/1 | DB+6 |  |  | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 14354.36 | 11492.6 | 1238.95 | 76.89 | 0 | 27162.8
416
46 | AP25/0 | DC+6 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 16850.4 | 11216.29 | 1372.8 | 44.38 | 0 | 29483.87
|  |  | 383.2 | 383.2
47 | AP26/0 | DD+25 |  |  | 1339.28 | 0 | 30.21 | 0 | 0 | 1369.49 | 24809.65 | 34369.86 | 2195.98 | 105.48 | 14.04 | 61495.01
|  |  | 211.3 | 211.3
48 | AP27/0 | DD+18 |  |  | 1339.28 | 0 | 30.21 | 0 | 0 | 1369.49 | 22496.01 | 24518.42 | 1938.89 | 91.12 | 14.04 | 49058.48
|  |  | 315.8 | 315.8
49 | AP28/0 | DC+0 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 15060.76 | 7928.65 | 1176.64 | 35.17 | 0 | 24201.22
|  |  | 300 | 681.4
50 | 28/1 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
381.4
51 | AP29/0 | DD+3 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 18730.53 | 10141.76 | 1290.87 | 55.58 | 14.04 | 30232.78
|  |  | 379.4 | 1689.406
52 | 29/1 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
375
53 | 29/2 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
315.006
54 | 29/3 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
300
55 | 29/4 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
320
56 | AP30/0 | DD+3 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 18730.53 | 10141.76 | 1290.87 | 55.58 | 14.04 | 30232.78
|  |  | 378 | 1552
57 | 30/1 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
398
58 | 30/2 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
388
59 | 30/3 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
388
60 | AP 31 | DB+0 |  |  | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 12787.4 | 8121.44 | 1065.59 | 65.61 | 0 | 22040.04
|  |  | 350 | 1516
61 | 31/1 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
390
62 | 31/2 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
390
63 | 31/3 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
386
64 | AP 32 | DB+0 |  |  | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 12787.4 | 8121.44 | 1065.59 | 65.61 | 0 | 22040.04
|  |  | 384 | 2271
65 | 32/1 | DA+6 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4533.16 | 10314.29 | 672.02 | 7.28 | 16.8 | 15543.55
390
66 | 32/2 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
370
67 | 32/3 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
327
68 | 32/4 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
400
69 | 32/5 | DA+6 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4533.16 | 10314.29 | 672.02 | 7.28 | 16.8 | 15543.55
400
70 | AP-33/0 | DB+0 |  |  | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 12787.4 | 8121.44 | 1065.59 | 65.61 | 0 | 22040.04
|  |  | 360 | 2200
71 | 33/1 | DA+6 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4533.16 | 10314.29 | 672.02 | 7.28 | 16.8 | 15543.55
400
72 | 33/2 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
350
73 | 33/3 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
370
74 | 33/4 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
370
75 | 33/5 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
350
76 | AP-34/0 | DD+0 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 16415.01 | 10718.52 | 1272.94 | 57.69 | 14.04 | 28478.2
|  |  | 320 | 1103
77 | 34/1 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
400
78 | 34/2 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
383
79 | AP-35/0 | DC+0 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 15060.76 | 7928.65 | 1176.64 | 35.17 | 0 | 24201.22
|  |  | 397 | 1160
80 | 35/1 | DA+6 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4533.16 | 10314.29 | 672.02 | 7.28 | 16.8 | 15543.55
398
81 | 35/2 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
365
82 | AP-36/0 | DC+0 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 15060.76 | 7928.65 | 1176.64 | 35.17 | 0 | 24201.22
|  |  | 400 | 400
83 | AP-37/0 | DD+6 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 18481.09 | 15064.6 | 1498.65 | 72.49 | 14.04 | 35130.87
|  |  | 243 | 243
84 | AP-38/0 | DD+9 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 19345.61 | 16190.28 | 1575.43 | 77.2 | 14.04 | 37202.56
|  |  | 226 | 226
85 | AP 39 | DD+6 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 18481.09 | 15064.6 | 1498.65 | 72.49 | 14.04 | 35130.87
|  |  | 395 | 1786
86 | 39/1 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
349
87 | 39/2 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
348
88 | 39/3 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
373
89 | 39/4 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
321
90 | AP 40 | DB+0 |  |  | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 12787.4 | 8121.44 | 1065.59 | 65.61 | 0 | 22040.04
|  |  | 427 | 1552
91 | 40/1 | DB+9 |  |  | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 16104.08 | 10967.56 | 1320.31 | 87.76 | 0 | 28479.71
400
92 | 40/2 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
400
93 | 40/3 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
325
94 | AP 41 | DB+6 |  |  | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 14354.36 | 11492.6 | 1238.95 | 76.89 | 0 | 27162.8
|  |  | 235 | 235
95 | AP 42 | DC+3 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 15864.24 | 8424.81 | 1199.12 | 36.09 | 0 | 25524.26
|  |  | 395 | 1454
96 | 42/1 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
365
97 | 42/2 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
360
98 | 42/3 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
334
99 | AP 43 | DC+0 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 15060.76 | 7928.65 | 1176.64 | 35.17 | 0 | 24201.22
|  |  | 320 | 2171
100 | 43/1 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
398
101 | 43/2 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
398
102 | 43/3 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
389
103 | 43/4 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
340
104 | 43/5 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
326
105 | AP 44 | DC+0 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 15060.76 | 7928.65 | 1176.64 | 35.17 | 0 | 24201.22
|  |  | 345 | 1871
106 | 44/1 | DD+18 |  |  | 1339.28 | 0 | 30.21 | 0 | 0 | 1369.49 | 22496.01 | 24518.42 | 1938.89 | 91.12 | 14.04 | 49058.48
188
107 | 44/1A | DD+25 |  |  | 1339.28 | 0 | 30.21 | 0 | 0 | 1369.49 | 24809.65 | 34369.86 | 2195.98 | 105.48 | 14.04 | 61495.01
281
108 | 44/2 | DB+3 |  |  | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 13901.56 | 8699 | 1114.9 | 64.13 | 0 | 23779.59
330
109 | 44/3 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
337
110 | 44/4 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
390
111 | AP 45 | DB+0 |  |  | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 12787.4 | 8121.44 | 1065.59 | 65.61 | 0 | 22040.04
|  |  | 338 | 3027.73
112 | 45/1 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
375
113 | 45/2 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
395
114 | 45/3 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
375
115 | 45/4 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
375
116 | 45/5 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
398
117 | 45/6 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
400
118 | 45/7 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
371.73
119 | AP 46 | DD+0 |  |  | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 16415.01 | 10718.52 | 1272.94 | 57.69 | 14.04 | 28478.2
|  |  | 375 | 1846.1
120 | 46/1 | DA+6 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4533.16 | 10314.29 | 672.02 | 7.28 | 16.8 | 15543.55
370
121 | 46/2 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
390
122 | 46/3 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
380
123 | 46/4 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
331.1
124 | AP47/0 | DC+0 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 15060.76 | 7928.65 | 1176.64 | 35.17 | 0 | 24201.22
|  |  | 340 | 2789.2
125 | 47/1 | DA+3 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7
400
126 | 47/2 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
355
127 | 47/3 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
325
128 | 47/4 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
284
129 | 47/5 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
376
130 | 47/6 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
350
131 | 47/7 | DA+6 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 4533.16 | 10314.29 | 672.02 | 7.28 | 16.8 | 15543.55
359.2
132 | AP48/0 | DC+0 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 15060.76 | 7928.65 | 1176.64 | 35.17 | 0 | 24201.22
|  |  | 295 | 628.1
133 | 48/1 | DA+0 |  |  | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47
333.1
134 | AP49/0 | DC+0 |  |  | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 15060.76 | 7928.65 | 1176.64 | 35.17 | 0 | 24201.22
|  |  | 400 | 1507.5
135 | 49/1 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
340
136 | 49/2 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
380
137 | 49/3 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
387.5
138 | AP50/0 | DD+0 |  |  | 683.2 | 219.84 | 8.3 | 0 | 0 | 911.34 | 6515.38 | 14162.89 | 635.48 | 6.08 | 4.68 | 21324.51
|  |  | 390 | 1505.82
139 | 50/1 | DA+9 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3607.86 | 9680.16 | 632.56 | 5.72 | 16.8 | 13943.1
365
140 | 50/2 | DA+6 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3387.54 | 8958.06 | 590.64 | 5.84 | 16.8 | 12958.88
395
141 | 50/3 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
355.82
142 | AP51/0 | DB+6 |  |  | 365.64 | 64.32 | 8.87 | 0 | 0 | 438.83 | 9220.75 | 9363.38 | 586.85 | 4.91 | 0 | 19175.89
|  |  | 390 | 1174.9
143 | 51/1 | DA+6(1mR.C) |  |  | 311.32 | 32.16 | 7.06 | 0 | 0 | 350.54 | 3387.54 | 8958.06 | 590.64 | 5.84 | 16.8 | 12958.88
400
144 | 51/2 | DA+6 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3387.54 | 8958.06 | 590.64 | 5.84 | 16.8 | 12958.88
384.9
145 | AP52/0 | DD+6 |  |  | 683.2 | 219.84 | 8.3 | 0 | 0 | 911.34 | 7698.82 | 17626.45 | 738.23 | 7.5 | 4.68 | 26075.68
|  |  | 395 | 1799.2
146 | 52/1 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
350
147 | 52/2 | DA+6 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3387.54 | 8958.06 | 590.64 | 5.84 | 16.8 | 12958.88
370
148 | 52/3 | DA+6 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3387.54 | 8958.06 | 590.64 | 5.84 | 16.8 | 12958.88
360
149 | 52/4 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
324.2
150 | AP53/0 | DD+3 |  |  | 683.2 | 219.84 | 8.3 | 0 | 0 | 911.34 | 7150.02 | 16706.89 | 724.22 | 7.76 | 4.68 | 24593.57
|  |  | 405 | 825
151 | 53/1 | DB+6 |  |  | 365.64 | 64.32 | 8.87 | 0 | 0 | 438.83 | 9220.75 | 9363.38 | 586.85 | 4.91 | 0 | 19175.89
420
152 | AP54/0 | DC+3 |  |  | 601.68 | 0 | 9.35 | 0 | 0 | 611.03 | 10218.65 | 9375.32 | 623.05 | 6.54 | 0 | 20223.56
|  |  | 343.4 | 1757.1
153 | 54/1 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
352.7
154 | 54/2 | DA+6 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3387.54 | 8958.06 | 590.64 | 5.84 | 16.8 | 12958.88
331.2
155 | 54/3 | DA+6 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3387.54 | 8958.06 | 590.64 | 5.84 | 16.8 | 12958.88
353.3
156 | 54/4 | DB+6 |  |  | 365.64 | 64.32 | 8.87 | 0 | 0 | 438.83 | 9220.75 | 9363.38 | 586.85 | 4.91 | 0 | 19175.89
376.5
157 | AP55/0 | DB+6 |  |  | 365.64 | 64.32 | 8.87 | 0 | 0 | 438.83 | 9220.75 | 9363.38 | 586.85 | 4.91 | 0 | 19175.89
|  |  | 353 | 1698.3
158 | 55/1 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
343
159 | 55/2 | DA+0(2mR.C) |  |  | 406.96 | 32.16 | 19.14 | 0 | 0 | 458.26 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
339.3
160 | 55/3 | DA+0(1mR.C) |  |  | 311.32 | 32.16 | 7.06 | 0 | 0 | 350.54 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
348
161 | 55/4 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
315
162 | AP56/0 | DB+0 |  |  | 365.64 | 64.32 | 8.87 | 0 | 0 | 438.83 | 8321.59 | 6300.22 | 485.49 | 4.35 | 0 | 15111.65
|  |  | 340 | 3411.5
163 | 56/1 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
400
164 | 56/2 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
400
165 | 56/3 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
360
166 | 56/4 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
400
167 | 56/5 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
344
168 | 56/6 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
371
169 | 56/7 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
386
170 | 56/8 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
410.5
171 | AP57/0 | DC+3 |  |  | 601.68 | 0 | 9.35 | 0 | 0 | 611.03 | 10218.65 | 9375.32 | 623.05 | 6.54 | 0 | 20223.56
|  |  | 380 | 2671.9
172 | 57/1 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
390
173 | 57/2 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
385
174 | 57/3 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
405
175 | 57/4 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
380
176 | 57/5 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
360
177 | 57/6 | DA+6 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3387.54 | 8958.06 | 590.64 | 5.84 | 16.8 | 12958.88
371.9
178 | AP58/0 | DB+6 |  |  | 365.64 | 64.32 | 8.87 | 0 | 0 | 438.83 | 9220.75 | 9363.38 | 586.85 | 4.91 | 0 | 19175.89
|  |  | 400 | 1538.3
179 | 58/1 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
380
180 | 58/2 | DA+0(0.5R.C) |  |  | 277.64 | 32.16 | 7.06 | 0 | 0 | 316.86 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
400
181 | 58/3 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
358.3
182 | AP59/0 | DB+0 |  |  | 365.64 | 64.32 | 8.87 | 0 | 0 | 438.83 | 8321.59 | 6300.22 | 485.49 | 4.35 | 0 | 15111.65
|  |  | 390 | 2307.2
183 | 59/1 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
405
184 | 59/2 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
380
185 | 59/3 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
372
186 | 59/4 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
360
187 | 59/5 | DA+6 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3387.54 | 8958.06 | 590.64 | 5.84 | 16.8 | 12958.88
400.2
188 | AP60/0 | DD+6 |  |  | 683.2 | 219.84 | 8.3 | 0 | 0 | 911.34 | 7698.82 | 17626.45 | 738.23 | 7.5 | 4.68 | 26075.68
|  |  | 203 | 203
189 | AP61/0 | DD+6 |  |  | 683.2 | 219.84 | 8.3 | 0 | 0 | 911.34 | 7698.82 | 17626.45 | 738.23 | 7.5 | 4.68 | 26075.68
|  |  | 413.1 | 413.1
190 | AP62/0 | DC+0 |  |  | 601.68 | 0 | 9.35 | 0 | 0 | 611.03 | 9171.69 | 7423 | 539.5 | 5.88 | 0 | 17140.07
|  |  | 325 | 2076.1
191 | 62/1 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
326
192 | 62/2 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
354
193 | 62/3 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
325
194 | 62/4 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
359
195 | 62/5 | DA+6 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3387.54 | 8958.06 | 590.64 | 5.84 | 16.8 | 12958.88
387.1
196 | AP63/0 | DD+18 |  |  | 968.88 | 219.84 | 10.38 | 0 | 0 | 1199.1 | 10792.34 | 25037.21 | 940.43 | 7.9 | 4.68 | 36782.56
|  |  | 247.1 | 247.1
197 | AP64/0 | DD+18 |  |  | 968.88 | 219.84 | 10.38 | 0 | 0 | 1199.1 | 10792.34 | 25037.21 | 940.43 | 7.9 | 4.68 | 36782.56
|  |  | 267 | 1022.1
198 | 64/1 | DB+0 |  |  | 365.64 | 64.32 | 8.87 | 0 | 0 | 438.83 | 8321.59 | 6300.22 | 485.49 | 4.35 | 0 | 15111.65
303
199 | 64/2 | DD+18 |  |  | 968.88 | 219.84 | 10.38 | 0 | 0 | 1199.1 | 10792.34 | 25037.21 | 940.43 | 7.9 | 4.68 | 36782.56
170
200 | 64/3 | DD+25 |  |  | 968.88 | 219.84 | 10.38 | 0 | 0 | 1199.1 | 12664.98 | 27979.21 | 1017.96 | 8.27 | 4.68 | 41675.1
282.1
201 | AP65/0 | DD+18 |  |  | 968.88 | 219.84 | 10.38 | 0 | 0 | 1199.1 | 10792.34 | 25037.21 | 940.43 | 7.9 | 4.68 | 36782.56
|  |  | 170 | 231
202 | AP66/0 | DD+25 |  |  | 968.88 | 219.84 | 10.38 | 0 | 0 | 1199.1 | 12664.98 | 27979.21 | 1017.96 | 8.27 | 4.68 | 41675.1
|  |  | 270 | 2143.4
203 | 66/1 | DB+3 |  |  | 365.64 | 64.32 | 8.87 | 0 | 0 | 438.83 | 8854.87 | 8481.46 | 566.34 | 4.91 | 0 | 17907.58
395
204 | 66/2 | DA+0(1mR.C) |  |  | 311.32 | 32.16 | 7.06 | 0 | 0 | 350.54 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
305
205 | 66/3 | DA+3 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68
265
206 | 66/4 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
310
207 | 66/5 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
305
208 | 66/6 | DA+0 |  |  | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97
293.4
209 | AP67/0 | DB+0 |  |  | 365.64 | 64.32 | 8.87 | 0 | 0 | 438.83 | 8321.59 | 6300.22 | 485.49 | 4.35 | 0 | 15111.65
|  |  | 225 | 225
210 | AP68/0 | DD+3 |  |  | 683.2 | 219.84 | 8.3 | 0 | 0 | 911.34 | 7150.02 | 16706.89 | 724.22 | 7.76 | 4.68 | 24593.57
|  |  | 158 | 158
211 | AP69 | DD+18 |  |  | 968.88 | 219.84 | 10.38 | 0 | 0 | 1199.1 | 10792.34 | 25037.21 | 940.43 | 7.9 | 4.68 | 36782.56
|  |  | 115 | 115
212 | AP70 | DD+9 |  |  | 683.2 | 219.84 | 8.3 | 0 | 0 | 911.34 | 8333.46 | 18715.41 | 784.75 | 7.58 | 4.68 | 27845.88
|  |  | 80 | 80
213 | AP71 | DD+3 |  |  | 683.2 | 219.84 | 8.3 | 0 | 0 | 911.34 | 7150.02 | 16706.89 | 724.22 | 7.76 | 4.68 | 24593.57
|  |  | 80 | 80
214 | GANTRY | GANTRY
[5 empty] | 113187.96 | 13258.76 | 2455.93 | 0 | 0 | 128902.65 | 1704111.4 | 2289887.21 | 173849.99 | 4571.77 | 2633.28 | 4175053.65
|  |  | Stub | [7 empty] | Tower
|  |  | HT |  |  | 113187.96 |  | KG. |  |  | HT |  | 1704111.4 |  | KG.
|  |  | MS(MS+P/W+ACC) |  |  | 13258.76 |  | KG. |  |  | MS(MS+P/W+ACC) |  | 2297092.26 |  | KG.
|  |  | N/B |  |  | 2455.93 |  | KG. |  |  | N/B |  | 173849.99 |  | KG.
[6 empty] | 128902.65 |  | KG. |  |  |  |  | 4175053.65 |  | KG.
Summary
|  | WZ-5 | [7 empty] | WZ-2
|  | Tower Type | Tower |  | Stub |  |  |  |  | Tower Type | Tower | Stub
|  | DA | 1091.55 |  | 32.846 |  |  |  |  | DA | 594.55 | 14.851
|  | DB | 318.67 |  | 10.521 |  |  |  |  | DB | 174.234 | 4.388
|  | DC | 385.954 |  | 14.499 |  |  |  |  | DC | 57.587 | 1.833
|  | DD | 1084.059 |  | 34.279 |  |  |  |  | DD | 468.441 | 15.684
|  | Total | 2880.233 |  | 92.145 |  |  |  |  | Total | 1294.812 | 36.756

## Tower wt sumry Ariyalur (hidden)
UNITECH POWER TRANSMISSION LIMITED
Project Name:- 400KV D/C NNTPS-Ariyalur Transmission Line
Project Code:-UP-225
TOWER WEIGHT CALCULATION
WZ-5
TYPE OF TOWER | DESCRIPTION | HT (MT) | MS(MT) | BOLT & NUTS (MT) | P/W | ACC | TOTAL WEIGHT (MT) | TOWER QTY | TOTAL HT (MT) | TOTAL MS(HT) | TOTAL BOLT & NUTS (MT) | P/W | ACC | Grand Total | REMARKS
DA-Type | +0MTR EXTN | 3929.84 | 7958.67 | 580.05 | 7.11 | 16.8 | 12492.47 | 35 | 137544.4 | 278553.45 | 20301.75 | 248.85 | 588 | 437236.45
| +3MTR EXTN | 4245.96 | 9727.85 | 648.9 | 7.19 | 16.8 | 14646.7 | 33 | 140116.68 | 321019.05 | 21413.7 | 237.27 | 554.4 | 483341.1
| +6MTR EXTN | 4533.16 | 10314.29 | 672.02 | 7.28 | 16.8 | 15543.55 | 11 | 49864.76 | 113457.19 | 7392.22 | 80.08 | 184.8 | 170979.05
| +9MTR EXTN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 327525.84 | 713029.69 | 49107.67 | 566.2 | 1327.2 | 1091556.6
DB-Type | +0MTR EXTN | 12787.4 | 8121.44 | 1065.59 | 65.61 | 0 | 22040.04 | 5 | 63937 | 40607.2 | 5327.95 | 328.05 | 0 | 110200.2
| +3MTR EXTN | 13901.56 | 8699 | 1114.9 | 64.13 | 0 | 23779.59 | 3 | 41704.68 | 26097 | 3344.7 | 192.39 | 0 | 71338.77
| +6MTR EXTN | 14354.36 | 11492.6 | 1238.95 | 76.89 | 0 | 27162.8 | 4 | 57417.44 | 45970.4 | 4955.8 | 307.56 | 0 | 108651.2
| +9MTR EXTN | 16104.08 | 10967.56 | 1320.31 | 87.76 | 0 | 28479.71 | 1 | 16104.08 | 10967.56 | 1320.31 | 87.76 | 0 | 28479.71
[9 empty] | 179163.2 | 123642.16 | 14948.76 | 915.76 | 0 | 318669.88
DC-Type | +0MTR EXTN | 15060.76 | 7928.65 | 1176.64 | 35.17 | 0 | 24201.22 | 8 | 120486.08 | 63429.2 | 9413.12 | 281.36 | 0 | 193609.76
| +3MTR EXTN | 15864.24 | 8424.81 | 1199.12 | 36.09 | 0 | 25524.26 | 4 | 63456.96 | 33699.24 | 4796.48 | 144.36 | 0 | 102097.04
| +6MTR EXTN | 16850.4 | 11216.29 | 1372.8 | 44.38 | 0 | 29483.87 | 2 | 33700.8 | 22432.58 | 2745.6 | 88.76 | 0 | 58967.74
| +9MTR EXTN | 19007.84 | 10765.75 | 1461.12 | 45.22 | 0 | 31279.93 | 1 | 19007.84 | 10765.75 | 1461.12 | 45.22 | 0 | 31279.93
[9 empty] | 236651.68 | 130326.77 | 18416.32 | 559.7 | 0 | 385954.47
DD-Type | +0MTR EXTN | 16415.01 | 10718.52 | 1272.94 | 57.69 | 14.04 | 28478.2 | 3 | 49245.03 | 32155.56 | 3818.82 | 173.07 | 42.12 | 85434.6
| +3MTR EXTN | 18730.53 | 10141.76 | 1290.87 | 55.58 | 14.04 | 30232.78 | 6 | 112383.18 | 60850.56 | 7745.22 | 333.48 | 84.24 | 181396.68
| +6MTR EXTN | 18481.09 | 15064.6 | 1498.65 | 72.49 | 14.04 | 35130.87 | 4 | 73924.36 | 60258.4 | 5994.6 | 289.96 | 56.16 | 140523.48
| +9MTR EXTN | 19345.61 | 16190.28 | 1575.43 | 77.2 | 14.04 | 37202.56 | 4 | 77382.44 | 64761.12 | 6301.72 | 308.8 | 56.16 | 148810.24
| +18MTR EXTN | 22496.01 | 24518.42 | 1938.89 | 91.12 | 14.04 | 49058.48 | 7 | 157472.07 | 171628.94 | 13572.23 | 637.84 | 98.28 | 343409.36
| +25MTR EXTN | 24809.65 | 34369.86 | 2195.98 | 105.48 | 14.04 | 61495.01 | 3 | 74428.95 | 103109.58 | 6587.94 | 316.44 | 42.12 | 184485.03
[9 empty] | 544836.03 | 492764.16 | 44020.53 | 2059.59 | 379.08 | 1084059.39
DA+DB+DC+DD | [8 empty] | 1288176.75 | 1459762.78 | 126493.28 | 4101.25 | 1706.28 | 2880240.34
WZ-2
TYPE OF TOWER | DESCRIPTION | HT (MT) | MS(MT) | BOLT & NUTS (MT) | P/W | ACC | TOTAL WEIGHT (MT) | TOWER QTY | TOTAL HT (MT) | TOTAL MS(MT) | TOTAL BOLT & NUTS (MT) | P/W | ACC | Grand Total | REMARKS
DA-Type | +0MTR EXTN | 2965.14 | 7192.36 | 499.26 | 5.41 | 16.8 | 10678.97 | 25 | 74128.5 | 179809 | 12481.5 | 135.25 | 420 | 266974.25
| +3MTR EXTN | 3185.46 | 8490.6 | 570.83 | 5.99 | 16.8 | 12269.68 | 15 | 47781.9 | 127359 | 8562.45 | 89.85 | 252 | 184045.2
| +6MTR EXTN | 3387.54 | 8958.06 | 590.64 | 5.84 | 16.8 | 12958.88 | 10 | 33875.4 | 89580.6 | 5906.4 | 58.4 | 168 | 129588.8
| +9MTR EXTN | 3607.86 | 9680.16 | 632.56 | 5.72 | 16.8 | 13943.1 | 1 | 3607.86 | 9680.16 | 632.56 | 5.72 | 16.8 | 13943.1
[9 empty] | 159393.66 | 406428.76 | 27582.91 | 289.22 | 856.8 | 594551.35
DB-Type | +0MTR EXTN | 8321.59 | 6300.22 | 485.49 | 4.35 | 0 | 15111.65 | 4 | 33286.36 | 25200.88 | 1941.96 | 17.4 | 0 | 60446.6
| +3MTR EXTN | 8854.87 | 8481.46 | 566.34 | 4.91 | 0 | 17907.58 | 1 | 8854.87 | 8481.46 | 566.34 | 4.91 | 0 | 17907.58
| +6MTR EXTN | 9220.75 | 9363.38 | 586.85 | 4.91 | 0 | 19175.89 | 5 | 46103.75 | 46816.9 | 2934.25 | 24.55 | 0 | 95879.45
| +9MTR EXTN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 88244.98 | 80499.24 | 5442.55 | 46.86 | 0 | 174233.63
DC-Type | +0MTR EXTN | 9171.69 | 7423 | 539.5 | 5.88 | 0 | 17140.07 | 1 | 9171.69 | 7423 | 539.5 | 5.88 | 0 | 17140.07
| +3MTR EXTN | 10218.65 | 9375.32 | 623.05 | 6.54 | 0 | 20223.56 | 2 | 20437.3 | 18750.64 | 1246.1 | 13.08 | 0 | 40447.12
| +6MTR EXTN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| +9MTR EXTN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 29608.99 | 26173.64 | 1785.6 | 18.96 | 0 | 57587.19
DD-Type | +0MTR EXTN | 6515.38 | 14162.89 | 635.48 | 6.08 | 4.68 | 21324.51 | 1 | 6515.38 | 14162.89 | 635.48 | 6.08 | 4.68 | 21324.51
| +3MTR EXTN | 7150.02 | 16706.89 | 724.22 | 7.76 | 4.68 | 24593.57 | 3 | 21450.06 | 50120.67 | 2172.66 | 23.28 | 14.04 | 73780.71
| +6MTR EXTN | 7698.82 | 17626.45 | 738.23 | 7.5 | 4.68 | 26075.68 | 3 | 23096.46 | 52879.35 | 2214.69 | 22.5 | 14.04 | 78227.04
| +9MTR EXTN | 8333.46 | 18715.41 | 784.75 | 7.58 | 4.68 | 27845.88 | 1 | 8333.46 | 18715.41 | 784.75 | 7.58 | 4.68 | 27845.88
| +18MTR EXTN | 10792.34 | 25037.21 | 940.43 | 7.9 | 4.68 | 36782.56 | 5 | 53961.7 | 125186.05 | 4702.15 | 39.5 | 23.4 | 183912.8
| +25MTR EXTN | 12664.98 | 27979.21 | 1017.96 | 8.27 | 4.68 | 41675.1 | 2 | 25329.96 | 55958.42 | 2035.92 | 16.54 | 9.36 | 83350.2
[9 empty] | 138687.02 | 317022.79 | 12545.65 | 115.48 | 70.2 | 468441.14
DA+DB+DC+DD | [8 empty] | 415934.65 | 830124.43 | 47356.71 | 470.52 | 927 | 1294813.31
[9 empty] | 1704.1114 | 2289.8872 | 173.85 | 4.5718 | 2.6333 | 4175.0536
2297.0923

## Stub weight Cal. Ariyalur (hidden)
UNITECH POWER TRANSMISSION LIMITED
Project Name:- 400KV D/C NNTPS-Ariyalur Transmission Line
Project Code:-UP-225
STUB WEIGHT CALCULATION
WZ-5
TYPE OF TOWER | DESCRIPTION | HT (MT) | MS(MT) | BOLT & NUTS (KG) | P/W | ACC | TOTAL WEIGHT (KG) | TOWER QTY | TOTAL HT (MT) | TOTAL MS(HT) | TOTAL BOLT & NUTS (MT) | P/W | ACC | Grand Total | REMARKS
DA-Type | +0,3,6,9MTR EXTN | 359.48 | 47.84 | 8.45 | 0 | 0 | 415.77 | 79 | 28398.92 | 3779.36 | 667.55 | 0 | 0 | 32845.83
DB-Type | +0,3,6,9MTR EXTN | 793.8 | 0 | 15.52 | 0 | 0 | 809.32 | 13 | 10319.4 | 0 | 201.76 | 0 | 0 | 10521.16
DC-Type | +0,3,6,9MTR EXTN | 949.88 | 0 | 16.73 | 0 | 0 | 966.61 | 15 | 14248.2 | 0 | 250.95 | 0 | 0 | 14499.15
DD-Type | +0,3,6,9MTR EXTN | 957.68 | 229.32 | 23.86 | 0 | 0 | 1210.86 | 17 | 16280.56 | 3898.44 | 405.62 | 0 | 0 | 20584.62
| +18/25MTR EXTN | 1339.28 | 0 | 30.21 | 0 | 0 | 1369.49 | 10 | 13392.8 | 0 | 302.1 | 0 | 0 | 13694.9
Grand Total | [8 empty] | 82639.88 | 7677.8 | 1827.98 | 0 | 0 | 92145.66
WZ-2
TYPE OF TOWER | DESCRIPTION | HT (MT) | MS(MT) | BOLT & NUTS (KG) | P/W | ACC | TOTAL WEIGHT (KG) | TOWER QTY | TOTAL HT (MT) | TOTAL MS(HT) | TOTAL BOLT & NUTS (MT) | P/W | ACC | Grand Total | REMARKS
DA-Type | +0,3,6,9MTR EXTN | 243.92 | 32.16 | 7.06 | 0 | 0 | 283.14 | 46 | 11220.32 | 1479.36 | 324.76 | 0 | 0 | 13024.44
| 1m R.C | 311.32 | 32.16 | 7.06 | 0 | 0 | 350.54 | 3 | 933.96 | 96.48 | 21.18 | 0 | 0 | 1051.62
| 2m R.C | 406.96 | 32.16 | 19.14 | 0 | 0 | 458.26 | 1 | 406.96 | 32.16 | 19.14 | 0 | 0 | 458.26
| 0.5m R.C | 277.64 | 32.16 | 7.06 | 0 | 0 | 316.86 | 1 | 277.64 | 32.16 | 7.06 | 0 | 0 | 316.86
[9 empty] | 12838.88 | 1640.16 | 372.14 | 0 | 0 | 14851.18
DB-Type | +0,3,6,9MTR EXTN | 365.64 | 64.32 | 8.87 | 0 | 0 | 438.83 | 10 | 3656.4 | 643.2 | 88.7 | 0 | 0 | 4388.3
DC-Type | +0,3,6,9MTR EXTN | 601.68 | 0 | 9.35 | 0 | 0 | 611.03 | 3 | 1805.04 | 0 | 28.05 | 0 | 0 | 1833.09
DD-Type | +0,3,6,9MTR EXTN | 683.2 | 219.84 | 8.3 | 0 | 0 | 911.34 | 8 | 5465.6 | 1758.72 | 66.4 | 0 | 0 | 7290.72
| +18/25MTR EXTN | 968.88 | 219.84 | 10.38 | 0 | 0 | 1199.1 | 7 | 6782.16 | 1538.88 | 72.66 | 0 | 0 | 8393.7
[9 empty] | 12247.76 | 3297.6 | 139.06 | 0 | 0 | 15684.42
Grand Total | [8 empty] | 30548.08 | 5580.96 | 627.95 | 0 | 0 | 36756.99

## LINE MATERIAL LILO (hidden)
POWER GRID CORPORATION OF INDIA LTD.
CONTRACTOR: |  |  | UNITECH POWER TRANSMISSION LTD.
PROJECT: LILO of Existing 400 kV S/C Neyveli TS II - Pondicherry Line
REQUIREMENT OF BOUGHT - OUT MATERIAL
SL No. | Loc. No. | Type of Tower | Etention | Span Length(m) | ACSR MOOSE CONDUCTOR | PIPE TYPE EARTHING INCLUDING ROD TYPE | DANGER PLATE | NUMBER PLATE | PHASE PLATE | CIRCUIT PLATE | ANTI-CLIMBING DEVICE | MID SPAN CONPRESSION JOINT FOR COND | REPAIR SLEEVE FOR CONDUCTOR | VIBRATION DAMPER FOR CONDUCTOR | BUNDLE SPACER FOR CONDUCTOR | RIGID SPACER FOR JUMPER | HARDWARE FITTINGSSINGLE ''I'' SUSPENSION STRING | HARDWARE FITTINGSSINGLE ''I'' SUSPENSION STRING(PILOT) | HARDWARE FITTINGS DOUBLE TENSION STRING | 120KN CLR INSULATOR | 160KN CLR INSULATOR | OPGW FIBER OPTIC CABLE | SUSPENSION CLAMP ASSY FOR OPGW | TENSION FITTINGS ASSMBLY FOR OPGW | VIBRATION DUMPER FOR OPGW | DOWN LEAD CLAMP FOR ASSMBLY FOR OPGW | JOINT BOX FOR 24 FIBER OPGW | TENSION ASSEMBLY FOR DEAD END FOR 24 OPGW | OPGW FIBER OPTIC DISRIBUTION PANEL | FIBRE OPTIC APPROCH CABLE | TENSION ASSEMBLY DOUBLE TENSION PASS THROUGH
| UNIT |  |  |  | MTR | SET | EA | EA | SET | SET | SET | EA | EA | EA | EA | EA |  | SET | SET | EA | EA
1 | GANTRY-2 | GTY | -2.7 | [8 empty] | 26 | 9 | 6 |  |  |  |  | 6 |  | 12 | 5 |  | 2 | 28 | 100 | 4 | 2 | 2 | 2
|  |  |  | 105 | 1260 | [9 empty] | 12
2 | DEAD END | DD+3 | 3 |  |  | 1 | 1 | 1 | 2 | 1 | 1 |  |  | 48 |  | 18 |  | 3 | 12 | 3 | 24
|  |  |  | 367 | 4404 | [9 empty] | 36
3 | AP-1/0 | MD+18 | 18 |  |  | 1 | 1 | 1 | 4 | 2 | 1 |  |  | 96 |  | 36 |  | 6 | 24 | 6 | 48
|  |  |  | 335 | 8040 | [9 empty] | 60
4 | AP-2/0 | MD+18 | 18 |  |  | 1 | 1 | 1 | 4 | 2 | 1 |  |  | 96 |  | 36 |  | 6 | 24 | 6 | 48
|  |  |  | 228 | 5472 | [9 empty] | 48
5 | AP-3/0 | MD+25 | 25 |  |  | 1 | 1 | 1 | 4 | 2 | 1 |  |  | 96 |  | 36 |  | 6 | 24 | 6 | 48
|  |  |  | 330 | 7920 | [9 empty] | 60
6 | 3/1 | MB+3 | 3 |  |  | 1 | 1 | 1 | 4 | 2 | 1 |  |  | 96 |  | 36 |  |  | 24 |  | 48
|  |  |  | 355 | 8520 | [9 empty] | 72
7 | AP-4/0 | MD+18 | 18 |  |  | 1 | 1 | 1 | 4 | 2 | 1 |  |  | 96 |  | 36 |  | 6 | 24 | 6 | 48
|  |  |  | 200 | 4800 | [9 empty] | 36
8 | AP-5/0 | MD+18 | 18 |  |  | 1 | 1 | 1 | 4 | 2 | 1 |  |  | 96 |  | 36 |  | 6 | 24 | 6 | 48
|  |  |  | 346 | 8304 | [9 empty] | 60
9 | AP-6/0 | MC+9 | 9 |  |  | 1 | 1 | 1 | 4 | 2 | 1 |  |  | 96 |  | 36 |  |  | 24 |  | 48
|  |  |  | 190 | 4560 | [9 empty] | 36
10 | LILO POINT | MD+3 | 3 |  |  | 1 | 1 | 1 | 4 | 2 | 1 |  |  | 72 |  | 18 |  | 6 | 24 | 6 | 48
130
11 | EXT. TW 16 | B+3 | 3
[19 empty] | 6 |  | 12
1 | GANTRY-4 | GTY | [11 empty] | 6
|  |  |  | 105 | 1260 | [9 empty] | 12
2 | DEAD END | DD+9 | 9 |  |  | 1 | 1 | 1 | 4 | 1 | 1 |  |  | 48 |  | 18 |  | 3 | 12 | 3 | 24
|  |  |  | 368 | 4416 | [9 empty] | 36
3 | AP-1/0 | MD+18 | 18
1 | LILO POINT | MD+3 | 0
165
2 | EXT. TW 17 | D+6 | 6
| TOTAL |  |  |  | 58956 | 10 | 10 | 10 | 38 | 18 | 10 | 26 | 9 | 852 | 468 | 306 | 0 | 42 | 228 | 42 | 456
WESTAGE |  |  |  |  | 589
| TOTAL REQUIRMENT |  |  |  | 59545

## Line Mat LILO (hidden)
POWER GRID CORPORATION OF INDIA LTD.
CONTRACTOR: UNITECH POWER TRANSMISSION LTD.
PROJECT: LILO of Existing 400 kV S/C Neyveli TS II - Pondicherry Line
REQUIREMENT OF BOUGHT -OUT MATERIAL | [21 empty] | SUPLY FOR | [9 empty] | For USE OPGW
SL No. | Loc. No. | Type of Tower | Etention | Span Length(m) | ACSR MOOSE CONDUCTOR | PIPE TYPE EARTHING INCLUDING ROD TYPE | DANGER PLATE | NUMBER PLATE | PHASE PLATE | CIRCUIT PLATE | ANTI-CLIMBING DEVICE | MID SPAN CONPRESSION JOINT FOR COND | REPAIR SLEEVE FOR CONDUCTOR | VIBRATION DAMPER FOR CONDUCTOR | BUNDLE SPACER FOR CONDUCTOR | RIGID SPACER FOR JUMPER | HARDWARE FITTINGSSINGLE ''I'' SUSPENSION STRING | HARDWARE FITTINGSSINGLE ''I'' SUSPENSION STRING(PILOT) | HARDWARE FITTINGS DOUBLE TENSION STRING | 120KN CLR INSULATOR | 160KN CLR INSULATOR | OPGW FIBER OPTIC CABLE | SUSPENSION CLAMP ASSY FOR OPGW | TENSION FITTINGS ASSMBLY FOR OPGW | VIBRATION DUMPER FOR OPGW | DOWN LEAD CLAMP FOR ASSMBLY FOR OPGW | JOINT BOX FOR 24 FIBER OPGW | TENSION ASSEMBLY FOR DEAD END FOR 24 OPGW | OPGW FIBER OPTIC DISRIBUTION PANEL | FIBRE OPTIC APPROCH CABLE | TENSION ASSEMBLY DOUBLE TENSION PASS THROUGH | VIBRATION DUMPER FOR EARTH WIRE | TENSION FITTING FOR EARTH WIRE | COPPER BOND EARTH WIRE | Span Length(m) | OPGW Drum Lenth | Tension Clamp for OPGW Dead end | Tension Assembly joint Box Location | PassThrough tension Assembly | Vibration Damper Including Reinforcing road | OPGW JOINT BOX | OPGW APPROACH CABLJOINT BOX | 3 way joint box | Downlead Clamp/Fastening Clamp | suspension clamp Assembly
| UNIT |  |  |  | MTR | SET | EA | EA | SET | SET | SET | EA | EA | EA | EA | EA |  | SET | SET | EA | EA
1 | GANTRY-2 | GTY | -2.7 | [10 empty] | 12 |  |  |  |  | 6 |  | 12 | 5 |  | 2 | 28 | 100 | 4 | 2 | 2 | 2 |  | 2 | 2 | 2 |  |  | 1 |  |  | 2 |  | 1 |  | 20
|  |  |  | 105 | 1260 | [29 empty] | 105
2 | DEAD END-1 | DD+3 | 3 |  |  | 1 | 1 | 1 | 2 | 1 | 1 |  |  | 36 |  | 18 |  | 6 | 12 | 6 | 24 | [10 empty] | 6 | 3 | 3 |  |  | 1 |  |  | 6
|  |  |  | 367 | 4404 | [9 empty] | 36 | [19 empty] | 367
3 | AP-1/0 | MD+18 | 18 |  |  | 1 | 1 | 2 | 4 | 2 | 1 |  |  | 48 |  | 18 |  | 12 | 12 | 12 | 24 | [10 empty] | 4 | 2 | 2 |  |  |  |  | 1 | 8
|  |  |  | 335 | 8040 | [7 empty] | 2 |  | 72 | [19 empty] | 335
4 | AP-2/0 | MD+18 | 18 |  |  | 1 | 1 | 2 | 4 | 2 | 1 |  |  | 96 |  | 36 |  | 18 | 24 | 18 | 48 | [17 empty] | 1 | 6
|  |  |  | 228 | 5472 | [9 empty] | 36 | [19 empty] | 225
5 | AP-3/0 | MD+25 | 25 |  |  | 1 | 1 | 2 | 4 | 2 | 1 |  |  | 96 |  | 36 |  | 18 | 24 | 18 | 48 | [17 empty] | 1 | 6
|  |  |  | 330 | 7920 | [9 empty] | 60 | [19 empty] | 330
6 | 3/1 | MB+3 | 3 |  |  | 1 | 1 | 2 | 4 | 2 | 1 |  |  | 96 |  | 36 |  |  | 24 |  | 48 | [17 empty] | 1 | 8
|  |  |  | 355 | 8520 | [9 empty] | 72 | [19 empty] | 356
7 | AP-4/0 | MD+18 | 18 |  |  | 1 | 1 | 2 | 4 | 2 | 1 |  |  | 96 |  | 36 |  | 18 | 24 | 18 | 48 | [17 empty] | 1 | 6
|  |  |  | 200 | 4800 | [9 empty] | 36 | [19 empty] | 196
8 | AP-5/0 | MD+18 | 18 |  |  | 1 | 1 | 2 | 4 | 2 | 1 |  |  | 96 |  | 36 |  | 18 | 24 | 18 | 48 | [17 empty] | 1 | 6
|  |  |  | 346 | 8304 | [9 empty] | 72 | [19 empty] | 350
9 | AP-6/0 | MC+9 | 9 |  |  | 1 | 1 | 2 | 4 | 2 | 1 |  |  | 96 |  | 36 |  |  | 24 |  | 48 | [17 empty] | 1 | 6
|  |  |  | 190 | 4560 | [9 empty] | 36 | [19 empty] | 190
10 | LILO POINT | MD+3 | 3 |  |  | 1 | 1 | 2 | 4 | 2 | 1 |  |  | 96 |  | 36 |  | 12 | 24 | 12 | 48 | [10 empty] | 2 | 2 | 2 |  |  |  |  | 1 | 4
|  |  |  | 130 | [10 empty] | 6 | [19 empty] | 130
11 | EXT. TW 16 | B+3 | 3 | [36 empty] | 2
1 | GANTRY-4 | GTY | [11 empty] | 12 |  |  |  |  | 6 |  | 12 | [10 empty] | 2 | 2 | 2
|  |  |  | 105 | 1260 | [9 empty] | 6
2 | DEAD END-2 | DD+9 | 9 |  |  | 1 | 1 | 1 | 2 | 1 | 1 |  |  | 36 |  | 18 |  | 6 | 12 | 6 | 24 | [10 empty] | 6 | 3 | 3
|  |  |  | 368 | 4416 | [9 empty] | 36
3 | AP-1/0 | MD+18 | 18 | [10 empty] | 48 |  | 18 |  | 6 | 12 | 6 | 24
1 | LILO POINT | MD+3 | 0 | [39 empty] | 1
165
2 | EXT. TW 17 | D+6 | 6 | [32 empty] | 2771 |  | 1 |  |  | 1 |  |  | 62
| TOTAL |  |  | 3224 | 58956 | 10 | 10 | 18 | 36 | 18 | 10 | 0 | 2 | 864 | 468 | 324 |  | 114 | 228 | 114 | 456 | [10 empty] | 22 | 14 | 14 | 2584 | 2771 | 2 | 1 | 8 | 60 | 1 | 1 | 1 | 82
WESTAGE |  |  |  |  | 589.56
| TOTAL REQUIRMENT |  |  |  | 59545.56
77376