| Sl. No. | Ref Section | Provision in bidding document | Bidders Queries | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| 1 | Section Project, 2.1.1.1 | The SF6 gas insulated switchgear (50 Hz) shall be of the indoor metal-enclosed type. The 765 kV GIS ICT-3 bay along with duct upto outside edge of GIS hall required for above augmentation work at Nizamabad GIS s/s is existing (M/s HYOSUNG make). | Please provide the cross sectional details / gas pressure details of 800 kV bus ducts of Hyosung’s at Nizamabad SS which is to be extended in the present scope. | Details of 800kV bus duct extension module of M/s Hyosung make GIS is attached as drawing no. PGCIL-10045403-A11-01,R0. The attached drawings are for reference only. Final drawings and details shall be shared during detailed engineering. For Gas pressures of existing 800 kV GIS bus duct (HYOSUNG make) please refer Gas SLD’s already enclosed with tender drawings |
| 2 | Section Project, 2.1.1.1 | The proposed 400 kV bays are to be extended from the existing 400 kV GIS system of M/s HYOSUNG make. | Please provide the cross sectional details / gas pressure of the bus bar of existing 400 kV GIS of Hyosung at Nizamabad SS which is to be extended | Details of 420kV bus bar extension module of M/s Hyosung make GIS is attached as drawing no.PGCIL-10045391-A11-01,R0. The attached drawings are for reference only. Final drawings and details shall be shared during detailed engineering. For Gas pressures of existing 420 kV GIS bus bar (HYOSUNG make) please refer Gas SLD’s already enclosed with tender drawings |
| 3 | Section Project . Clause no.2.1.3.1A | The proposed 400 kV bays are to be extended from the existing 400 kV GIS system of M/s GE make……… | We would like to inform you that as per the mentioned clause, we understand the existing GIS at 420kV Tuticorin is GE Make. In order to proceed with Interface module connection design and to determine the space requirement for the interface module, we required detailed Extension Module Drawing. | Details extension module for M/s GE make 420kV GIS bus bar is attached herewith. The attached drawings are for reference only. Final drawings and details shall be shared during detailed engineering. |