| Sl. No |  | Ref Section | Provision in bidding document | Bidders Queries | POWERGRID Reply |
| --- | --- | --- | --- | --- | --- |
| 1 |  | IFB and ITB | …………. | Due to the ongoing severe 3rd wave of the pandemic Covid – 19, it is extremely challenging and difficult to submit hard copies of our bids in the current scenario. We hence request you to kindly allow submission of all the bids online in soft format as was being allowed by M/s. POWERGRID till very recently. We trust you will consider our request and help us in safe submission of bids for all packages which would be due within next 1-2 months. | Provisions of the bidding document shall prevail and remain unaltered. |
| 2 |  | Section – VI, Forms and Procedures, Appendix –2, | The prices shall remain firm and fixed during the currency of the Contract. | We request you to allow price variation for GIS Modules, Power & Control Cables, Earthing material as per IEEMA formulae. | Refer Amendment No. I dated 12.02.2022. |
|  |  | Extn. of 765/400kV Nizamabad GIS substation under Augmentation of Transformation Capacity in Southern Region |  |  |  |
| 3 |  | Tender Drawings | Tender GA Drawing | We presume that there is sufficient space provision for C & R Panels of present scope in existing 765kV & 400kV GIS Hall Relay Panel Room. Please confirm | It is to confirm that sufficient space is available for accommodating the C&R panels of present scope under Augmentation of Transformation Capacity in Southern Region in existing 765kV & 400 kV GIS hall relay rooms. |
|  |  | Extn. of 400kV Nizamabad GIS substation under Consultancy services to TSTRANSCO |  |  |  |
| 4 |  | Tender Drawings | Tender GA Drawing | It is understood that the existing 400kV GIS Hall need to be extended by bidder as shown in the Tender Layout. Also request to indicate the Length of GIS Hall to be extended as the same is not mentioned in the Tender GA drawing | Exact length of 400kV GIS hall to be extended shall be finalized during detailed engineering based on dimensions of actual GIS to be supplied under subject project. However, it is to mention that as per Bid Price Schedules, the GIS Hall extension tentative area specified in square meters. Bidders requested to quote as per requirements of bidding documents. |
| 5 |  | General | EOT Crane | In Price Schedule there is no item for EOT Crane extension for extended 400kV GIS HALL. Please clarify. | Please refer clause no. 2.1.2.1b) of Technical specification, Section- Project for scope of EOT crane related work. The above-referred clause clearly states that “Girder extension of existing EOT crane for GIS hall extension area is under present scope. Cost of the same shall be deemed to be covered in the GIS building extension cost.” Accordingly, GIS hall extension works item specified in Bid price schedule-3 includes cost for the EOT girder extension. |
|  | Extn. of 400/230kV Tuticorin-II GIS S/S for installation of 4th ICT under Transmission System for Tirunelveli and Tuticorin Wind Energy Zone (Tamil Nadu) (500MW) |  |  |  |  |
| 6 |  | Vol. III Bid Price Schedule, Sl. No 158 | Air conditioning system for Switchyard Panel room of 6m length - 1 SET | As per Tender GA Layout there are no SPR rooms and it is understood that the 230kV C&R Panels shall be placed in existing Control room building. Please Clarify | C & R Panels for 230kV bays under present scope to be placed in a separate switchyard panel room to be constructed under present scope as per requirement of clause no. 2.1.3.3(v) of Technical specification, Section- Project. Location of the switchyard panel room shall be finalized during detailed engineering. |
| 7 |  | Vol II, Tender drawings | General Arrangement drawing | We presume that the 400kV C & R panels will be placed in the C & R panel room or GIS Building as shown in GA drawing. Please confirm. Also, the 220kV C & R panels are placed in the existing Control room where sufficient space is available for the present scope. Please confirm | 400kV bays C & R panels to be placed in the existing relay panel room in 400kV GIS Building. C & R Panels for 230kV bays under present scope to be placed in a separate switchyard panel room to be constructed under present scope. |
| 8 |  | General | General | Please provide the exiting 230kV Hybrid GIS make and model. | Existing 230kV Hybrid GIS at Tuticorin-II GIS S/s is of M/s ABB-Hitachi energy (erstwhile M/s ABB Limited). |
| 9 |  | Vol. II, Technical Specification Section: Project, Cl. No. 2.1.4.1 A, b) & Vol. II, Technical specification Section GIS (rev. 5A), Cl. No. 17.13. | Girder extension for existing EOT crane of GIS hall under present scope. Cost of the same shall be deemed to be covered in the GIS building extension cost. & In case the GIS hall is to be extended, the scope of work also involves extension of EOT crane girders and all necessary Electrical & Mechanical accessories to facilitate movement of existing EOT crane in the extended portion of GIS hall. Cost of the same shall be deemed to be covered in the building cost. | In Price Schedule there is no item for EOT Crane extension for extended 400kV GIS HALL under present scope. Please clarify. | For Extn. of 400/230kV Tuticorin-II GIS S/S for installation of 5th ICT, 400kV GIS hall extension is envisaged and existing EOT crane Girder arrangement is to be extended. Please refer clause no. 2.1.4.1A, b) of Technical specification, Section- Project for scope of EOT crane related work. The above-referred clause clearly states that “Girder extension of existing EOT crane for GIS hall extension area is under present scope. Cost of the same shall be deemed to be covered in the GIS building extension cost.” Accordingly, GIS hall extension works item specified in Bid price schedule-3 includes cost for the EOT girder extension. |
|  | Extn. of 400/230kV Tuticorin-II GIS S/S for installation of 5th ICT. |  |  |  |  |
| 10 |  | Vol II, Tender drawings | General Arrangement drawing | It is understood that the existing 400kV GIS Hall need to be extended by bidder as shown in the Tender Layout. Also request to indicate the Length of GIS Hall to be extended as the same is not mentioned in the Tender GA Drawing. | Exact length of 400kV GIS hall to be extended shall be finalized during detailed engineering based on dimensions of actual GIS to be supplied under subject project. However, it is to mention that as per Bid Price Schedules, the GIS Hall extension tentative area specified in square meters. Bidders requested to quote as per requirements of bidding documents. |
| 11 |  | Vol. III Bid Price Schedule, Schedule III, Sl. No 158 | PEB - Ext of 400 kV GIS - Civil Works. All civil works as per drawing and specifications complete, including - brickwork, finishing (external and internal), windows etc. However, excavation, PCC, RCC and reinforcement shall be paid separately as per BPS. – M2 - 700 | We presume that the 400kV C & R panels will be placed in the C & R panel room of GIS Building as shown in GA drawing. Please confirm. Also, the 220kV C & R panels are placed in the existing Control room where sufficient space is available for the present scope. Please confirm. | 400kV bays C&R panels to be placed in the existing relay panel room in 400kV GIS Building. C&R Panels for 230kV bays under present scope to be placed in a separate switchyard panel room to be constructed in present scope works under Extn. of 400/230kV Tuticorin-II GIS S/S for installation of 4th ICT. Location of the switchyard panel room shall be finalized during detailed engineering. |
| 12 |  | Vol. II, Technical Specification Section: Project, Cl. No. 2.1.4.1 A, b) & Vol. II, Technical specification Section GIS (rev. 5A), Cl. No. 17.13. | Girder extension for existing EOT crane of GIS hall under present scope. Cost of the same shall be deemed to be covered in the GIS building extension cost. & In case the GIS hall is to be extended, the scope of work also involves extension of EOT crane girders and all necessary Electrical & Mechanical accessories to facilitate movement of existing EOT crane in the extended portion of GIS hall. Cost of the same shall be deemed to be covered in the building cost. | In Price Schedule there is no item for EOT Crane extension for extended 400kV GIS HALL under present scope. Please clarify. | For Extn. of 400/230kV Tuticorin-II GIS S/S for installation of 5th ICT, 400kV GIS hall extension is envisaged and existing EOT crane Girder arrangement is to be extended. Please refer clause no. 2.1.4.1A, b) of Technical specification, Section- Project for scope of EOT crane related work. The above-referred clause clearly states that “Girder extension of existing EOT crane for GIS hall extension area is under present scope. Cost of the same shall be deemed to be covered in the GIS building extension cost.” Accordingly, GIS hall extension works item specified in Bid price schedule-3 includes cost for the EOT girder extension. |