| Sl. No | Clause No | Existing clause | Amended clause |
| --- | --- | --- | --- |
|  | Vol. II Part-A, Appendix-J, List of equipment for buy-back | List of Buy back | Added List of equipment for buy-back (NRLDC) Attached at Annexure-I |
|  | Vol. II Part-B, Section-2, Clause No.- 2.3.3, DTS model | DTS model shall be capable of representing the EMS/SCADA computer systems for which operators are being trained. | Replaced with DTS model shall be capable of representing the SCADA/EMS applications including AGC (excluding Load forecasting & DSA) for which operators are being trained. |
|  | Vol. II Part-B, Appendix-H-1, Software Specification, Table-16, ANTI-APT | Sr. No.; Minimum Required Specifications; Offered by the Contractor. 18.; Number of VM's/sandbox images should be more than 10 from day 1 and running simultaneously. 19.; It should support Sandbox Analysis for files which can run on multiple operating systems like Win7, Win8, Win10, Window Server 2008, 2012, 2016, 2019 and future version shall also be supported. If any additional licenses are required, same may be considered by bidder.. | Sr. No.; Minimum Required Specifications; Offered by the Contractor. 18.; Number of VM's/sandbox images should be more than 8 from day 1 and running simultaneously. 19.; It should support Sandbox Analysis for files: - Which can run on multiple operating systems of windows environment - Linux file types etc. The contractor shall supply all necessary licenses for above functionalities and future version shall also be supported. If any additional licenses are required, same may be considered by contractor.. Replaced with |
|  | Volume II, Part B, Appendix-H, Table-13, External Network Firewall with NIPS (For DMZ and RTU-ICCP Connectivity) | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 4 (f ); Proposed solution should support minimum 6 Gbps or more IPS throughput. 13; Supporting Protocols; FTP, SMTP, HTTP, HTTPS, SNMP, UDP, ICMP, RPC, DNS, DHCP, ARP, TCP, POP3, IGMP, PIM.. 17.; Filtering of packets based on Source address, destination address, protocol type, user, port number, URL.. | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 4 (f ); Firewall should have at least 1.5 Gbps of VPN throughput.. 13; Supporting Protocols; FTP, SFTP, SMTP, HTTP, HTTPS, SNMP, UDP, ICMP, RPC, DNS, DHCP, ARP, TCP, POP3, IGMP, PIM.. 17.; Filtering of packets based on Source address, destination address, protocol type, user, port number, URL. (Including URL blocking). Replaced with |
|  | Vol. II Part-B, Section-1, Clause No.- 1.3.3.8, Deviation Settlement (DSM) Charges | Deviation Settlement (DSM) Charges | Deleted |
|  | Volume II, Part B, Appendix-H Table-14, Internal Network Firewall with NIPS | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 4 (f); Proposed solution should support minimum 6 Gbps or more IPS throughput. 13; Supporting Protocols; FTP, SMTP, HTTP, HTTPS, SNMP, UDP, ICMP, RPC, DNS, DHCP, ARP, TCP, POP3, IGMP, PIM.. 17.; Filtering of packets based on Source address, destination address, protocol type, user, port number, URL.. | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 4 (f ); Firewall should have at least 1.5 Gbps of VPN throughput.. 13; Supporting Protocols; FTP, SFTP, SMTP, HTTP, HTTPS, SNMP, UDP, ICMP, RPC, DNS, DHCP, ARP, TCP, POP3, IGMP, PIM.. 17.; Filtering of packets based on Source address, destination address, protocol type, user, port number, URL. (Including URL blocking). Replaced with |
|  | Volume II, Part B, Appendix-H | --- | Added Table-39. DRS of LAN switch to be supplied along with terminal server and DCPC (as per BOQ) attached at Annexure-II |
|  | Volume II, Part B, Appendix-H Table-20, Video Projection System - LASER (VPS) | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 20.; Specint & Specfp; As per the base runtime requirements of SPEC CPU 2017 Benchmarking Standards.. 23.; Internal Auxiliary Memory; 500 GB SSD in RAID-1 configuration. 27.; Interface with VPS; Audio video signal input module with 2 video inputs, 2 audio inputs, 2 audio outputs for connecting speakers, 2 RGB inputs, 1 DVI input.. 28.; Types of video signal to be supported by VPS Controller; 1. RGB Analog up to 1920x1200 (up to 165 MHz pixel clock) 2. DVI up to 1920x1200 (up to 165 MHz pixel clock).. | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 20; Deleted. 23.; Internal Auxiliary Memory; 480 GB SSD in RAID-1 configuration. 27.; Interface with VPS; Audio video signal input module with 2 video inputs, 2 audio inputs, 2 audio outputs for connecting speaker, Minimum ports of type 2*DP-in, 2*HDMI, 1*DP-out. 28.; Types of video signal to be supported by VPS Controller; Video signals supporting through HDMI and DP interface. 36.; Graphic card; Min 8 GB. Replaced with |
|  | Volume II, Part B, Appendix-H Table-22, Video Wall - Floor / Wall Mounted (55’’ Diagonal) | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 8.; Contrast Ratio; Minimum 5000:1. 27.; Speakers; In built. 28.; Inputs; 2 HDMI, 1 DVI, 2USB. | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 8.; Contrast Ratio; Minimum 1500:1. 27.; Speakers; Yes. 28.; Inputs; 2 HDMI, 2 DP, 2 USB. Replaced with |
|  | Volume II, Part B, Appendix-H Table-33, 55” Video Wall with controller | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 23.; Internal Auxiliary Memory; 500 GB. | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 23.; Internal Auxiliary Memory; 480 GB. Replaced with |
|  | Vol. II Part-B Section-5, Clause 5.16, Furniture | 5.16 Furniture | Replaced with Clause 5.16 attached at Annexure-III |
|  | Volume II, Part C, Section 2, UPS requirements, 2.4.1.(d) | Capacity to recharge the batteries to 90% State of Charge from fully discharged state (i.e., ECV of 1.75 V) within 8 hrs while carrying full load where battery charging current shall be considered as at least 20% of Battery AH capacity. | Replaced with Capacity to recharge the batteries to 90% State of Charge from fully discharged state (i.e., ECV of 1.75 V) within 8 hrs while carrying full load where battery charging current shall be considered as at least 10% of Battery AH capacity. |
|  | Volume II, Part C, Section 3, Battery Requirements, Note: | Considering 20, 40, 60 & 80 kVA UPS design for 192 cells of 2 volts, 200, 300 & 400 AH each, the VAH capacity of battery bank shall be: 38400 VAH = 2 x 192 x 200 VAH = 38.4 kVAH 76800 VAH = 2 x 192 x 200 VAH = 76.8 kVAH 115200 VAH = 2 x 192 x 300 VAH = 115.2 kVAH 153600 VAH = 2 x 192 x 400 VAH = 153.6 kVAH In case of UPS design is different from 192 cells, then AH capacity of cells should be selected suitably to meet the total battery bank capacity requirement of 76.8 kVAH, 115.2 kVAH and 153.6 kVAH respectively. | Replaced with Considering 20, 40, 60, 80 & 120 kVA UPS design for 192 cells of 2 volts, 100, 200, 300, 400 & 600 AH respectively , the VAH capacity of battery bank shall be: 38400 VAH = 2 x 192 x 100 VAH for 20kVA UPS 76800 VAH = 2 x 192 x 200 VAH for 40kVA UPS 115200 VAH = 2 x 192 x 300 VAH for 60kVA UPS 153600 VAH = 2 x 192 x 400 VAH for 80kVA UPS 230400 VAH = 2 x 192 x 600 VAH for 120kVA UPS In case of UPS design is different from 192 cells, then AH capacity of cells should be selected suitably to meet the total battery bank capacity requirement of 38.4kVAH, 76.8 kVAH, 115.2 kVAH, 153.6 kVAH & 230.4 kVAH respectively. |
|  | Volume II, Part C, Appendix-A, Data Requirements Sheets | Sl No.; Description; Particulars. 11.; Overall efficiency of UPS (with battery fully charged and operating at full load of 64 KW for 80 KVA, 48 KW for 60 KVA, 32 KW for 40 KVA & 16 kW for 20 KVA UPS at unity power factor) >=90%; Yes/No. 12.; Suitable for operating ambient temperature of 0 to 50oC, 5 to 95% RH, non-condensing at full rated load of 64/48/32/16 kW; Yes/No. | Sl No.; Description; Particulars. 11.; Overall efficiency of UPS (with battery fully charged and operating at full load of 96 KW for 120 KVA, 64 KW for 80 KVA, 48 KW for 60 KVA, 32 KW for 40 KVA & 16 kW for 20 KVA UPS at unity power factor) >=90%; Yes/No. 12.; Suitable for operating ambient temperature of 0 to 50oC, 5 to 95% RH, non-condensing at full rated load of 96/64/48/32/16 kW; Yes/No. Replaced with |
|  | Volume II, Part C, Appendix-A, Data Requirements Sheets, ACDBs (Input & Output) | Sl No.; Description; Particulars. 11.; Input ACDB sized for 80kVA/60kVA/40kVA/20kVA etc. as applicable in BoQ; Yes/No. 12.; Input ACDB sized for 80kVA/60kVA/40kVA/20kVA etc. as applicable in BoQ; Yes/No. | Sl No.; Description; Particulars. 11.; Input ACDB sized for 120kVA/80kVA/60kVA/40kVA/20kVA etc. as applicable in BoQ; Yes/No. 12.; Input ACDB sized for 120kVA/80kVA/60kVA/40kVA/20kVA etc. as applicable in BoQ; Yes/No. Replaced with |
|  | Volume II, Part B, Appendix-F, System sizing | Appendix-F, System Sizing | Replaced with revised Appendix-F System Sizing attached as Annexure-IV |
|  | Volume II, Part D, Section 3, RTU |  | Inserted Appendix – B: Location of RTU sites at J&K attached at Annexure-V |
|  | Volume II, Part B, Section 5, Clause-5.3, Hardware Configuration | ….. The Typical hardware configuration is attached at Appendix- D of Part -A. | Replaced with …… The Typical hardware configuration is attached at Appendix- D of Part -A. The connectivity between networking devices shall be designed having mesh connectivity. |
|  | Volume II, Part B, Appendix-B, B30 | SAMPLE REPORTS AND DISPLAY FORMATS | Inserted Additional SLD & network diagram in B30 Sample Reports & Displays attached at Annexure-VI. |
|  | Volume II, Part A, Section 3, Clause-3.7.7, Type Testing | e.) Testing charges for all the type tests listed in the specifications shall be indicated separately for each item (excluding expenses of Inspector/ Employer’s representative) in the prescribed schedule of the bidding document. The total amount of these charges will be considered in the bid evaluation process. | Deleted |
|  | Volume II, Part A, Section 1, Clause-1.11, General Requirements | …. In this case Supplier has to deliver all the three options to the user. …. | Replaced with …. In this case Supplier has to deliver all the three options to the user. However, if 'or' OR '/' is mentioned in-lieu of certification/testing requirement for any of the items envisaged under the contract, in that case contractor has to meet minimum one requirement. …. |
|  | Volume II, Part A, Section 1, Clause-1.12.4, Owner’s Responsibilities and Obligations |  | Inserted - Internet connectivity of required bandwidth. - Email Server |
|  | Volume-II, Part- B, Section 9: CYBER SECURITY REQUIREMENT, Clause No. 9.1.1 Cyber Security Policy | Added new clause | Added new clause: • All the communication should be done through secure protocols such as SFTP, HTTPS etc. |
|  | Volume -II Part- B, Section 9: CYBER SECURITY REQUIREMENTS, Para 2 of 9.1.3.1 Firewall | - It should show policy traffic trend over the day with host and destination addresses by selecting on each policy. | Replaced with - It should show policy traffic trend over the day with host and destination addresses by selecting on each policy. - Geofencing shall be enabled in all the firewalls and security devices. |
|  | Vol. II Part-B, Section – 9, Clause no. –9.1.7, End Point Security (Antivirus) | ….. It shall log all USB port access events. (Capturing details of connected USB). It shall allow only identified USB devices to connect to a computer system. | Replaced with …….. It shall log all USB port access events (Capturing details of connected USB). It shall allow only identified USB devices to connect to a computer system. It shall have configurable firewall features. |
|  | Vol. II Part-B Appendix-G, Bill of Quantity Note e. & Vol-III, First Stage, Unpriced BoQ, Note e. | Commercial Off-The-Shelf (COTS) product means bidder has to quote product which is independently commercially available in the market. For all such products bidder has to provide at least five references in Govt/Public Listed companies at the time of bid submission and same shall have been sold as an independent product. | Replaced with Commercial Off-The-Shelf (COTS) product means bidder has to quote product which is independently commercially available in the market. For all such products bidder has to provide at least three references in Govt/Public Listed companies at the time of bid submission and same shall have been sold as an independent product and solution shall be in successful operation for at least three years at the time of bid submission. For that Bidder has to submit copy of PO/LOA and installation/completion/operational certificate issued by Customer for the relevant reference. |
|  | Volume II Part B, Appendix-H: HARDWARE SPECIFICATIONS 4. Servers: a. Server for Third Party Applications b. Servers for Management Applications c. Servers for Applications in Internal DMZ d. Servers for Applications in External DMZ | 10. Optical Drive: DVD RW | Deleted |
|  | Volume II Part B, Appendix-H: HARDWARE SPECIFICATIONS. 6.2 Network Attached Storage (NAS) | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 10; Heat Load. 11.; Interface Ports; 4*10G Base T ports. | Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 10; Heat Load. 11.; Interface Ports; Minimum 4*10G Base T ports (two ports per controller). 12.; Controller; Dual Controller. |
|  | Volume II Part B, Appendix-H: HARDWARE SPECIFICATIONS. 15.Centralized Management of Firewalls | --- | Added new point no. 15 15. Same OEM Firewalls located at main and back-up control centre shall be configured and managed by centralised management system located at both locations i.e., main and backup control centre. So that if there is problem in main control centre then all the firewalls from same OEM at both locations shall be managed centrally from backup control centre and vice versa. |
|  | Volume II Part-E VIDEO CONFERENCING EQUIPMENT | Volume II, Part-E VIDEO CONFERENCING EQUIPMENT | Replaced with Revised Volume II, Part-E VIDEO CONFERENCING EQUIPMENT attached at Annexure-VII. |
|  | Volume II Part-B Appendix-G, Bill of Quantity & Vol-III, First Stage, Unpriced BoQ | Table - RTU OF J&K PDD Table - RTU OF DTL | Replaced with Table - RTU OF J&K PDD Table - RTU OF DTL The BoQ of RTU of J&K and DTL is attached at Annexure-VIII. |
|  | Volume II Part-D, RTU | Appendix A: RTU I/O counts for JK PDD | Replaced with Appendix A: RTU I/O counts for JK PDD The revised Part-D, Appendix A: RTU I/O counts for JK PDD is attached at Annexure-IX. |
|  | Volume II Part-B Appendix-G, Bill of Quantity, List of Spare of RLDC/SLDCs | SPARES OF NRLDC, HVPNL, PTCUL, J&K, DTL, UP, PSTCL, BBMB, RRVPNL, HP SLDC List of Spare of RLDC/SLDCs , F. RTU Spares | Updated with SPARES OF NRLDC, HVPNL, PTCUL, J&K, DTL, UP, PSTCL, BBMB, RRVPNL, HP SLDC The RTU Spares are updated in Bill of Quantity, List of Spare of RLDC/SLDCs , F. RTU Spares (attached at Annexure-X). |
|  | Volume II Part-A, Section – 1, Clause no. –1.10, Scope of Work (b) | ……...Further, future bay integration shall not be treated as new RTU integration during AMC period, and any Bay extension during AMC shall be in the scope of the contractor without any commercial implication to the Owner. | Replaced with ……...Further, future bay integration shall not be treated as new RTU integration during AMC period, and any Bay extension during AMC shall be in the scope of the contractor without any commercial implication to the Owner. The term AMC in this Specification shall be read as AMC including extension if any. |
|  | Volume II Part-A, Section – 1, Clause no. –1.16, General Bidding Requirements | - A commitment and a clearly defined plan to develop a system support organization, based in India and capable of providing a full range of local - Services (including software and hardware maintenance and upgrade support) for the life of the delivered systems. | Replaced with - A commitment and a clearly defined plan to develop a system support organization, based in India and capable of providing a full range of local Services (including software and hardware maintenance and upgrade support) for the life of the delivered systems. |
|  | Vol. II Part-B, Section – 3, Clause no. – 3.11 | Sample Display building approved guidelines are attached at Annexure-B, the same shall be followed. | Replaced with Sample Display building approved guidelines are attached at Appendix-K, the same shall be followed. |
|  | Volume II, Part C, Section 3, Battery Requirements, Note:3. | The minimum capacity/rating is specified here for various equipments, the Bidder shall asses the adequacy of specified capacity/rating such that minimum Backup time delivered by battery bank shall not be less than 30 minutes at full load & if any additional hardware or higher capacity/rating equipments are required to meet the requirement, the same shall be included in the. | Replaced with The minimum capacity/rating is specified here for various equipments, the Bidder shall assess the adequacy of specified capacity/rating such that minimum Backup time delivered by battery bank shall not be less than 60 minutes at full load during entire project life cycle & if any additional hardware or higher capacity/rating equipments are required to meet the requirement, the same shall be offered by the Bidder. |