Annexure to Amendment No- II_Technical to Bidding Documents for Package: Bidding Documents for Package: “Implementation of Unified Load Despatch and Communication (ULDC) Phase-III SCADA/EMS Upgradation Project-Northern Region SLDCs and RLDC”; Specification no.: CC/NT/W-SCADA/DOM/A04/23/00902

Annexure-I

| Vol. II Part-A, Appendix-J: List of equipment for buy-back (NRLDC) - Added |  |  |  |  |
| --- | --- | --- | --- | --- |
| S.NO. | Equipment | Description | Qty-Main NRLDC | Qty-Backup NRLDC |
| 1 | Server | Dell R420, Processor 2 X Intel(R) Xeon(R) CPU E5-2407 @ 2.20 GHz 4C | 7 | 7 |
| 2 | Server | Dell R420, Processor 1 X Intel(R) Xeon(R) CPU E5-2407 @ 2.20 GHz 4C | 13 | 8 |
| 3 | SAN | SAN1 24X600GB HDD | 1 | 1 |
| 4 | SAN | SAN2 24X600GB HDD | 1 | 1 |
| 5 | NAS | Dell PowerVault NX300 2 X Intel(R) Xeon(R) CPU E5-2630 0 @ 2.30 GHz 2300 Mhz 6Core(s) 8x600GB HDD | 1 | 1 |
| 6 | Workstation | OPTIPLEX 3010 along with Monitors | 19 | 2 |
| 7 | Routers | Cisco 1900 Series | 9 | 6 |
| 8 | Switches | Cisco SG300 Gigabit Managed Switch | 16 | 13 |
| 9 | Terminal Servers | Advantech EXI-1526T | 20 | - |
| 10 | UPS | 2 * 40 KVA Delta UPS along with Battery Bank and Input/Ouput ACDB , Isolation Transfomers | 1 | 1 |
| 11 | VPS | 7 * 3 Barco VPS Screen along with Controllers at Main NRLDC | 1 | - |
| 11 | VPS | 4 * 3 Barco VPS Screen along with Controllers at Backup NRLDC | - | 1 |
| 12 | Furniture | Operator Consoles | 5 | 2 |
| 13 | Server Racks | 800*1200 mm Server Racks | 4 | 4 |
| 14 | Firewall | Fortinet 100D | 3 | 3 |
| 15 | Firewall | GajShield | 1 | 1 |
| 16 | KVM | KVM along with Monitores | 4 | 4 |
| 17 | Printers | Colour Later Printer | 2 | 2 |
| 18 | Printers | Multifunction B& W Printer | 2 | 2 |
| 19 | GPS Receiver | Sertel GPS Receiver | 1 | 1 |
| 20 | Displays | Frequency LED Display | 1 | 1 |
| 21 | Displays | Time LED Display | 1 | 1 |
| 22 | Displays | Day LED Display | 1 | 1 |
| 23 | Laptop | Maintenance Laptops | 2 | 2 |
| 24 | Tape Libraries | Tape Libraries | 1 | 1 |

NOTE :- This is tentative list of equipment to be buy-backed. During project execution, few items may not buy backed in case of utilization in any other project/work by respective SLDCs/RLDC. Final list shall be shared during detail engineering.

Annexure-II

# Volume II, Part B, Appendix-H: Table-39. Added

# 39.  LAN switch to be supplied along with terminal server and DCPC

| S.No | Description of the Features | Minimum Quantity of the features | Offered by the Contractor |
| --- | --- | --- | --- |
|  | Manufacturer |  |  |
|  | Model No. |  |  |
|  | Functions | For connecting with Terminal servers & DCPC |  |
|  | Conform to standards | ISO8802 or IEEE 802 Series Standards |  |
|  | Switching capability | Layer-3 switching & VLAN |  |
|  | Interface ports | Minimum 8- 10/100Mbps Ethernet ports (RJ45 connector) |  |
|  | Management Features | - Configuration through secure command-line interface (CLI) over Telnet and SSH - SNMPv3 - Network Time Protocol (NTP) or equivalent support. |  |
|  | Cable standard | Cat 6 or higher bandwidth cable |  |
|  | Mounting | Rack mountable |  |

Annexure-III

Volume II Part-B Section-5 Clause 5.16 is replaced with below clause :

5.16 	Furniture

The control room furniture, from reputed make, shall conform to high standard of engineering as mentioned in the document, meeting the specified codes, standards, and designs. It shall be capable of performing 24X7 operations under the specified environmental condition in compliance with control room ergonomic norms i.e., ISO 11064. However, the specific design, finish and color of all furniture shall be subject to Employer/Owner’s approval.

General requirement for Workstation Desk (both type)

- Structure

Made of heavy duty extruded vertical and horizontal aluminum profiles of 6005 grade duly powder coated.

- Tabletop

The material of the working surface shall be minimum 25 mm thick MDF with High Pressure ANSI/NEMA LD3 certified scratch-resistant laminate and having balancing laminate of minimum 0.5 mm thickness other side. The proposed desk life cycle shall be assessed for environmental impacts associated with all the stages of a product's life for cradle to grave analysis.

- Slat Wall

Slat wall shall be made of approximately 2mm thick extruded aluminum (aluminum alloy).

- Front Edge

UL/ Intertek/NABL certified Lab audit certified design feature on front modular Polyurethane (PU) Edge. High density Poly Urethane Foam molded on industrial grade aluminum core to form minimum 50mm deep tapered edge to be installed on worktop.

- Shutters & Side Legs

Front and back shutters shall be of 18 mm Laminated MDF Board with premium finish. The side leg shall be of 25mm of the same finish.

- Hardware

All bolts shall be of SS material to avoid rust due to environment. Remaining hardware shall be Nickel Plated MS.

- Table shall have been provided with sufficient number of power sockets, LAN ports, door-lights, sliding trolley for CPU, soft-door closure etc. Number of sliding trollies, LAN port and power sockets may be provided as per the owner additional requirement.

- Workstation Desk: Motorized

Each workstation shall be provided with a suitable desk as follows:

- Sectional frame suitably clad with hardwood or hard wearing material.

- Desktops of a durable, scratch resistant, non-reflecting finish of suitable thickness.

- Proper Channels for Power, LAN and Telephone cabling with 100% spare capacity i.e., integrated cable management system shall be in place.

- Adequate space shall be provided on the desktop for the writing area, to accommodate the operator workstation, mouse, telephone and other miscellaneous items.

- Drawers, shelves, and miscellaneous fittings.

- Access shall be allowed for maintenance to equipment mounted on or in the desk. Pull out Drawer, Doors or removable panels shall be provided for this purpose.

- Adjustable (height) desks (sit-and-stand with step-less automatic height adjustment).

- Independent electronic powered height adjustment of monitors platform and workspace.

- Table shall have been provided with sufficient number of power sockets, LAN ports, door-lights, sliding trolley for CPU, soft-door closure etc. Number of sliding trollies, LAN port and power sockets may be provided as per the owner additional requirement.

- Monitor tilt variation with motorized height/tilt/depth adjustment. Monitor screens’ tilt shall be adjusted with electrical drive at desired angle, depth & curvilinear arrangement of screens depending on the operator's ease of working. All the monitor screens must have synchronized tilting with 0 to 60ᵒ from vertical plane by single control, customizable.

- Programmable touch screen controls for operator desk movements with auto-save PRESET options related to desk movements/position. Embedded screen option can be explored.

- The programmable touch screen shall have at least 10 automatic preset to define the desk configuration as per individual operator's requirement.

- To ensure hassle free ergonomic operations/adjustments and durability of the product, the desk shall have UL/Intertek /NABL certified Lab audit certified feature on all mechanisms of desk.

- All bolts shall be of SS material to avoid rust due to environment.

- Workstation Desk: Normal / U-Type

Each workstation shall be provided with a suitable desk as follows:

- Sectional frame suitably clad with hardwood or hard wearing material.

- Desktops of a durable, scratch resistant, non-reflecting finish of suitable thickness.

- Proper Channels for Power, LAN and Telephone cabling with 100% spare capacity i.e. integrated cable management system shall be in place.

- Adequate space shall be provided on the desktop for the writing area, to accommodate the operator workstation, mouse, telephone fand other miscellaneous items.

- Drawers, shelves and miscellaneous fittings.

- Access shall be allowed for maintenance to equipment mounted on or in the desk. Pull out Drawer, Doors or removable panels shall be provided for this purpose.

- Table shall have been provided with sufficient number of power sockets, LAN ports, door-lights, sliding trolley for CPU, soft-door closure etc. Number of sliding trollies, LAN port and power sockets may be provided as per the owner additional requirement.

- All bolts shall be of SS material to avoid rust due to environment.

- Chairs

- Two chairs shall be provided at each workstation.

- The chair shall be of high-backed design with arm rests, covered in durable woven material.

- The chairs shall be of good quality and suitable for continuous use without discomfort.

- Pneumatic Seat height and back angle adjustments shall be provided, capable of easy operation.

- Furniture for Printers

Furniture table for printer shall also be provided which shall have pre-fitted power sockets, LAN ports etc.

Furniture/Fixtures for all other items which are not mounted in the racks shall also be provided by supplier.

The contractor shall provide the workstation desk, its chairs and printer table at same rate to owner whenever required during entire contract period.

Annexure-IV

Vol. II, Part-B

Appendix - F

System Sizing

Appendix F

SYSTEM SIZING

Initial/present power system size and ultimate system size [Future Number/Quantity (Total expansion including present quantity)] are specified in Tables-1 to 6. The specified size shall be applicable for both Main and Backup Control Centre Computer Systems. All the status points defined in this appendix shall be configured as controllable and accordingly the system shall be sized.

Table -1 shows the approximate number of power system components for each Control Centre Computer System sizing. These components need to be modelled for State Estimation and other SCADA/EMS functions, whether or not they have associated telemetry. All the points used for calculations are not telemetered.

Table-2 shows the ICCP data to be exchanged with NLDC, RLDCs, State Load Dispatch Control Centres and other Control Centres.

Table-3 shows the number of RTUs reporting on IEC 60870-5-101 & 104 protocols and Average number of I/O points per RTU.

Table-4 shows the data to be exchanged with other/external computer systems such as off-line applications etc.

Table-5: Sizing of the Data historian.

Table-6: Future Number/Quantity (Total expansion including present quantity). The table shows future expansion requirements for respective control centers (main and backup CC). The system shall be designed in accordance with system design parameter mentioned in Appendix-C, system performance requirement mentioned in Appendix-D and table-6 of Appendix-F for respective control centers.

Note: A more accurate count of the above system sizing parameters will be supplied during detail engineering of the project implementation.

SYSTEM SIZING –initial (Present System)

Table – 1: POWER SYSTEM COMPONENTS SIZING

| POWER SYSTEM COMPONENT | Present Number/Quantity |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | UP | DTL | RRVPNL | HVPNL | PSTCL | HP | NRLDC | J&K | PTCUL | BBMB |
| Substations | 722 | 59 | 597 | 450 | 275 | 85 | 2500 | 85 | 58 | 22 |
| Feeders /Overhead Line | 17830 | 750 | 41823 (Ckt Kms.) | 1000 | 2100 | 800 | 10000 | 800 | 1500 | 90 |
| Transformers | 1589 | 205 | 1584 | 1350 | 650 | 250 | 4000 | 400 | 173 | 146 |
| Generating Units | 23 | 22 | 59 | 17 | 48 | 52 | 2000 | 20 | 17 | 28 |
| HVDC Converter stations | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 10 | 10 | 10 |
| Power Flow Buses | 3029 | 200 | 500 | 400 | 800 | 300 | 6000 | 400 | 400 | 5 |
| Static VAR Compensation | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 10 | 10 | 10 |
| Series capacitor | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |
| Shunt capacitor | 10 | 58 | 10 | 10 | 10 | 10 | 1000 | 20 | 46 | 10 |
| Shunt reactor | 10 | 3 | 54 | 10 | 10 | 3 | 1000 | 10 | 3 | 5 |
| Series reactor | 3 | 3 | 3 | 3 | 3 | 3 | 10 | 3 | 3 | 3 |
| FSC, TCSC, STATCOM & other FACTS devices | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 10 | 10 | 10 |
| Wind Farms | 20 | 3 | 55 | 20 | 20 | 10 | 200 | 10 | 10 | 10 |
| Solar Farms/Parks | 59 | 20 | 124 | 20 | 87 | 20 | 200 | 20 | 20 | 20 |
| CO-GEN PLANTS | 81 | 25 | 10 | 20 | 15 | 10 | 10 | 10 | 5 | 10 |

Table – 2: ICCP Point Count

| Type of Data | Present Number/Quantity |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | UP | DTL | RRVPNL | HVPNL | PSTCL | HP | NRLDC | J&K | PTCUL | BBMB |
| Analog Points | 30000 | 66000 | 23794(client)+16500(server) | 24000 | 6200 | 23164 | 200000 | 12000 | 15143 | 11995 |
| Status Points | 50000 | 30000 | 30757(client)+23500(server) | 31000 | 20000 | 31111 | 200000 | 15000 | 8770 | 27229 |

Table – 3: System sizing (Initial) for RTUs and data received from RTUs

| Elements | Present Number/Quantity |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | UP | DTL | RRVPNL | HVPNL | PSTCL | HP | NRLDC | J&K | PTCUL | BBMB |
| Number of RTUs on IEC 101 | 72 | 4 | 234 | 192 | 175 | 18 | 100 | 10 | 44 | 0 |
| Number of RTUs on IEC 104 | 333 | 51 | 55 | 111 | 160 | 119 | 300 | 85 | 14 | 22 |
| Average Number of analog points per RTU | 102 | 64 | 33 | 44 | 70 | 150 | 100 | 150 | 186 | 56 |
| Average Number of Status points per RTU | 77 | 190 | 68 | 70 | 50 | 100 | 200 | 150 | 118 | 143 |
| Average Number of SOE points per RTU | 27 | 75 | 75 | 70 | 20 | 50 | 100 | 50 | 118 | 134 |
| Average number of control signals per RTU | 10 | 10 | 10 | 20 | 5 | 10 | 20 | 15 | 41 | 10 |

Table- 4: Point Count for exchange with other/external Computer Systems

| POWER SYSTEM COMPONENT | Present Number/Quantity |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | UP | DTL | RRVPNL | HVPNL | PSTCL | HP | NRLDC | J&K | PTCUL | BBMB |
| Analog Points from and into SCADA | 2094 (PWC In: 52, PWC Out: 277, PMC Out: 1765) | 1000 | 13098 | 1000 | 1000 | 1000 | 50000 | 1000 | 1000 | 1000 |
| Status Points from and into SCADA | 1500 | 1500 | 25849 | 1500 | 1500 | 1500 | 50000 | 1500 | 1500 | 1500 |

Table-5: Sizing of the Data historian

| Data Source | No. of Points |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | UP | DTL | RRVPNL | HVPNL | PSTCL | HP | NRLDC | J&K | PTCUL | BBMB |
| Analog Points | 119423 | 3500 | 25180 | 70000 | 20967 | 78000 | 300000 | 78000 | 15168 | 82985 |
| Status points | 90326 | 9700 | 35130 | 80000 | 15785 | 68000 | 300000 | 68000 | 8775 | 71294 |

Table-6: Future Expansion (Main & Backup CC)

| S.no. | Future Expansion |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | UP | DTL | RRVPNL | HVPNL | PSTCL | HP | NRLDC | J&K | PTCUL | BBMB |
| 1 | 300% of present system | 300% of present system | 300% of present system | 300% of present system | 300% of present system | 300% of present system | 200% of present system | 300% of present system | 300% of present system | 200% of present system |

- The expansion requirement is 200% expansion over and above the present system sizing i.e., equal to 300% of present system size except for NRLDC & BBMB where expansion requirement is 100% i.e., equal to 200% of present system size.

Note:

- Under the TS, multiple sources for data points have been envisaged. While defining the sizing of the system it is assumed that all the redundant sources to a data point has been considered as single point and telemetered point itself can be used for redundant data source configuration along with Inter-site (Main-Backup) data transfer. Sizing shall be done accordingly.

- The contractor shall consider hardware sizing considering 7 years of proposed system and 10 years old data, which shall be migrated to new historian. Old data for duration of 10 years needs to be migrated to new system. All this stored data shall be available online for trending and reporting.

- The EMS/SCADA system shall not have any limitations including performance with respect to increase in Database sizing. In case of any resizing or expansion of database is required due to constraint of system parameter in delivered system other than that listed in the table above, it shall be the responsibility of the vendor to re-size the delivered system without any cost of the customer during the entire course of the project including the AMC period.

- System sizing shall include all system calculations like Max/Min/Avg/ROC/pf/MVA calculations and no financial implications to be imposed on the owner.

- The Contractor shall consider the expansion requirement mentioned in Table 6 above of the present system for respective control center.

- The calculated points shall not be counted in the sizing specified herein above.

- ICCP points to be exchanged to & for between multiple control centre simultaneously shall be considered as a single point for sizing point of view.

Annexure-V

| Volume-II,Part D, Appendix-B : Location of RTU sites at J&K |  |  |
| --- | --- | --- |
| S.NO | SUB-STATION NAME | Physical Address |
| 1 | AKHNOOR | 132/33kv grid station near old Akhnoor Steel Bridge Ambran Akhnoor-181201 |
| 2 | Alusteng | 320/100 MVA, 220/132/33 kV GSS Alusteng, Rangil, Near Water Treatment Plant, Ganderbal, Pincode 191201 |
| 3 | Amargarh | 135 MVA GSS Amargarh, Tehsil: Sopore District: Baramulla Pin - 193201 |
| 4 | Awantipora | Grid Station Awantipora Buh, Awantipora Distt.. Pulwama PIN 192122 |
| 5 | B ATOTE | 132/33kv grid station Champa Batote NH 44-182143 |
| 6 | Badampora | 132/33 KV 100MVA Grid Station Badampora Tehsil: Wakura District: Ganderbal PIN code :- 191131 Post Office : Tulmulla |
| 7 | Bandipora | 132/33 KV 100MVA Grid Station Putshaie Bandipora Teh: Bandipora District: Bandipora PIN code :- 193502 |
| 8 | BANIHAL | 132/33 kv grid stattion Banihal.-182146 |
| 9 | Baribrahmana | 181.5,MVA,132/33/11/kv grid station baribrahmana (Industrial Area ) Jammu-181133 |
| 10 | BARIBRAHMANA-2 | 132/33 kv grid station ,kartholi ,morha dasal (bari barhmana )-181133 |
| 11 | BARN | 220/132 grid station Barn tehsil - Bhalwal-181122 |
| 12 | BATTAL MANYAL | 132/33 KV grid station Battal- Manwal, village -Kelay, Manwal ( UDHAMPUR)-182127 |
| 13 | Bemina | 200 MVA, 132/33 kV Grid Sub Station Bemina PDD Complex Bemina District Srinagar PIN 190018 |
| 14 | BHALLESA | 132/33 kv grid station Bhallessa , Location:- CHANGA BHALLESSA-182203 |
| 15 | BISHNAH | 220/132/33 kv station lalyana bishnah -181132 |
| 16 | Budgam | 320/100MVA,220/132/33KV Grid Sub -Station Mawra Budgam,Tesh./Distt. Budgam P.O : Budgam Pin code: 191111 |
| 17 | CANAL | 132/33kv grid station Canal near Chief Engg JPDCL office-180002 |
| 18 | Chadoora | 100MVA 132/33 kV Gridstation Nowbugh Chadoora Tehsil. Chadoora District ,Budgam PIN. 191113 |
| 19 | CHANDAK | 132/33 kv grid station Chandak-185101 |
| 20 | CHATHA | 132/33 kv grid station Chatha, Village Chatha , The.& Distt :- Jammu -180009 |
| 21 | CHENANI | Underr Power Grid |
| 22 | Cheshmashahi | 140MVA, 132/33 kV Grid Station Cheshmashahi Kral Sangri Near Tulip Garden Srinagar PIN 190001 |
| 23 | CHOWAHI | 220/33 kv grid stations chowadi at village Birpur ( SAMBA)-180011 |
| 24 | Delina | Grid Sub-station Delina, near BSF camp, on Delina - Singhpora Kalan road, Delina,Baramulla Pincode - 193103 |
| 25 | DRABA | 132/33 kv grid station Draba-185122 |
| 26 | GANGYAL | 132/33 KV 2x50MVA grid station gangyal-180010 |
| 27 | GHATTI | 220/66 kv grid station -Nanan , block- Barnoti (Kathua )-184143 |
| 28 | GLADNI | 220/132 kv grid station gladni jammu near radission hotel-180006 |
| 29 | Habak | 150 MVA, 132/33 KV Habak,GSS Hazratbal road, Ellahibagh, Srinagar, Kashmir 190020. |
| 30 | Harwan GIS | 160 MVA 220/33 kV GIS Harwan Haripora, Harwan , Pincode - 191123 |
| 31 | HIRANAGAR | 220/132/66 KV grid station hiranagar-184142 |
| 32 | JANIPUR | 132/33kv grid station janipur near high court Janipur-180007 |
| 33 | JHAJJAR KOTLI | 132/33kv grid station Jhajjar Kotli-181221 |
| 34 | JOURIAN | 132/33 kv grid station jourian kaleeth,Akhnoor, jammu -181204 |
| 35 | KALAKOTE | 132/33 kv grid stationkalakote-185202 |
| 36 | Kangan | 132/33 KV Gridstation Kangan , District Ganderbal, Srinagar Leh Highway Near JEE Sahib Power House Kangan PIN 191202. |
| 37 | KATHUA | 150 MVA, 132/66 KV Grid station Halti Morh Kathua-184102 |
| 38 | KATRA | 132/33 grid station village - sarwad-182320 |
| 39 | Khanyar GIS | GIS Khanyar Mill Stop Nalbal Oppsite CRPF Camp Nowshera Srinagar 190011 PO . Nowshera |
| 40 | KHELANI | 132/33 kv grid station opp. FCI godown khelani Doda -182201 |
| 41 | Khrew | 2x50 MVA 132/33 kV KHREW Bathen Khrew Tehsil Pampore District Pulwama Pincode - 191103 |
| 42 | Khunmoh | 100MVA,132/33 KV GSS KHONMOH (Industrial Estate Phase-2nd) District: Srinagar Tehsil: Pantha Chowk Pin code: 191104 |
| 43 | KISHTWAR | 132/33kv grid station Nagini Kistwar -182204 |
| 44 | Kulgam | 100MVA, 132/33KV Grid station Kulgam Dist. Kulgam Tehsil Kulgam Pincode - 192231 |
| 45 | Kupwara | 132/33 kV, 120 MVA Grid Sub Station Arampora Tehsil: Dragmulla Distt:Kupwara Pincode:-193222 |
| 46 | Lassipora AIS | 75 MVA,132KV/33KV AIS LASSIPORA SIDCO LASSIPORA Teh: Litter District:Pulwama Pin code: 192301 |
| 47 | Lassipora GIS | 160 MVA,220KV/33KV GIS LASSIPORA SIDCO LASSIPORA Tehsil: Litter District:Pulwama Pin code: 192301 |
| 48 | Lissar | 132/33 kV, 100 MVA Grid Sub Station Sagam (Lisser) Kokernag Tehsil: Kokernag District: Anantnag Pincode- 192202 |
| 49 | LJHP | LJHP ,Gantamulla , District Baramulla Pincode: 193101 |
| 50 | Magam | 100 MVA, 132/33Kv GSS Ahmedpora – Magam District :- Budgam Pin Code:- 193401 P.O :- Magam |
| 51 | MAHANPUR | 132/33 kv grid station Mahanpur, Basoli (Kathua)-184202 |
| 52 | Mattan | 132/33 KV 100MVA Grid Station Mattan Gopalpora Teh: Anantnag East District: Anantnag PO Martand - 192125 |
| 53 | Mir Bazar | 475 MVA 220/132 KV Grid sub-station Mirbazar Village :-Nipora District:- Kulgam Post office:- Qazigund 192221 |
| 54 | MIRASAHIB | 150 MVA, 132/33 KV Grid station Mirasahib (Talli morh) Jammu-181101 |
| 55 | NHPC KISHTWAR | 132/33kv grid station Semra Kishtwar-182204 |
| 56 | Pampore 132 kV | 132/33 kV Grid Station Pampore Near MEI School Distt:- Pulwama Pin:- 192121 |
| 57 | Pampore 220 kV | 220/132 kV , 450 MVA Grid substation Pampore Tehsil Pampore District. Pulwama Pin code 192121 |
| 58 | Pattan | 120MVA, 132/33KV Grid Sub Station Nehalpora Pattan District: Baramulla J&K Tehsil: Pattan Pincode: 193121. |
| 59 | POUNI CHAK | 132/33kv grid station pouni chak near Gole Gujral -180016 |
| 60 | RAJOURI | 132/33 kv grid station thudi Rajouri-185132 |
| 61 | RAMBAN | 220/132 Govind pura Maitra opp transit camp Ramban-182144 |
| 62 | Rawalpora | Grid Station Rawalpora Sanat Nagar Byepass Distt.. Srinagar PIN 190005 |
| 63 | SAMBA | 220/66 kv grid station near phase -3 near Rakh Amb talli dordashan -184121 |
| 64 | SAMBA (PG) | 132/66 KV 2x50MVA grid station samba -184121 |
| 65 | Sheeri | 100 MVA,132/33 kV Grid Station Sheeri Near Police Training College Sheeri Tehsil, Baramulla Distt Baramulla Pin 193101 |
| 66 | Shopian | 132kv/33kv 100MVA Grid Station Kanipora District Shopian.Pin code - 192303 |
| 67 | SIDHRA | 132/33 kv grid station sidhra( Majeen ) jammu-180019 |
| 68 | SIOT | 132/66 kv 2x50MVA grid station siot (Rajouri)-185152 |
| 69 | Tengpora | 150 MVA , 132/33 kV GIS Tengpora, Near Tengpora Bypass Bridge District Srinagar Pincode - 190009 |
| 70 | Tethar | 50 MVA 132/33 kV Grid Station Tethar Banihal District Ramban Pin 182146 |
| 71 | UDHAMPUR | 220/132 Jakheni opp.TLMD-3 Divison office udhampur-182101 |
| 72 | USHP 1 | USHP Ist , Sumbal Bala, Tehsil: Kangan, District Ganderbal , Pincode: 191202 |
| 73 | USHP 2 | USHP II , Kangan Tehsil: Kangan, District Ganderbal Pincode: 191203 |
| 74 | Villgam | 50 MVA Grid Sub-Station Vilgam, Tehsil Vilgam, District Kupwara, Pin Code - 193224 |
| 75 | Wanganpora | 200 MVA Grid station Wanganpora Eidgah , Srinagar ,JK 190002 Post office : MR Gunj |
| 76 | Wanpoh | 132/33 KV 160 MVA Grid Station Wanpoh Gassipora Wanpoh Tehsil: Anantnag District: Anantnag Pin :192101 |
| 77 | Zainakote | 450 MVA,220/132/33 kV Grid Substation Zainakote Pincode 190018 District Budgam Under Srinagar Municipal Limits Tehsil Budgam |
| Note- Above are tentative locations for RTU Installations, Final locations shall be shared during detail engineering. |  |  |

Annexure-VI

Volume II, Part B, Appendix-B, B 30. Sample Reports & Displays- Added

Network Diagram

Sample SLD

Annexure-VII

Volume-II

Part-E

VIDEO CONFERENCING EQUIPMENT

Table of Contents

1.1	Introduction	19

1.2	LCD Video Wall (LVW)	19

1.3	Controller Features	20

1.4	Multipoint Control Unit (MCU)	21

1.5	Video Endpoints	22

1.6	Camera	24

1.7	Wireless Microphone System	24

1.8	Accessories	25

1.9	FAT methodology for VC equipment	25

1.10	Technical Specifications for Wall Mount Speakers – 2 pairs	25

1.11	Technical Specifications for Amplifier	25

VIDEO CONFERENCING EQUIPMENT

# Introduction

This section describes the functional and technical requirements of Video Conferencing Systems being supplied. The minimum hardware & software requirements are specified here, the Bidder shall assess the adequacy of the same & if any additional hardware, software & interfaces are required to meet all the functional requirements of the technical specifications, the same shall be included in the offer. The BOQ of the equipment’s to be supplied is indicated at Appendix-G, Part-B.

The Contractor shall supply the required furniture and panel with the system. Supplied Video Conferencing (VC) System consists of LCD Video Wall System, Multipoint Control Unit (MCU), Video End Point along with omnidirectional microphones (2), Camera, Wireless Microphone, and any accessory as per the BOQ. VC system shall be used for video conferencing among North Region Constituents.

lt shall be possible for a constituent to do video conferencing between their Main Control Center and Backup Control Center without MCU and if any additional hardware/software is required to meet this functionality, Bidder shall be responsible to supply it. MCU will be required only when more than two CCs are involved in VC.

Wall mountable type LCD Video Wall System (LVWS) consists of LCD Video Walls (LVW) and associated Controller/ drivers shall be supplied by the Contractor. The Contractor shall supply LVWS with all necessary hardware, software, and interfaces, including LCD modules, supporting/mounting/fitting arrangement including cabling etc. to make the entire system operational.

# LCD Video Wall (LVW)

- The LVW shall be able to take Video signals (from CCTV/Dish TV/DVD Player & video conferencing unit) and Laptop Feeds. The LVWS shall enable users to display inputs from multiple sources/applications simultaneously in freely resizable and repositionable windows on entire display area to enable effective collaboration.

- LCD Video wall (LVW) shall be wall-mounted type.

- Other technical specifications required of LVW are given below: -

LCD video wall

| S.No. | Description of the Parameters |  |  |
| --- | --- | --- | --- |
|  | LCD wall features | Parameters | Offered by contractor |
|  | Display Type | LCD screen |  |
|  | Backlit | White LED, Full array |  |
|  | LED Lifetime | Minimum 50000 Hours |  |
|  | Module/Cube size | 55” diagonal |  |
|  | Video screen configuration (No. of modules) | As per BoQ |  |
|  | Display Colours | 16.7 million |  |
|  | Horizontal & Vertical viewing angle | > +1600 (approx.) |  |
|  | Minimum Resolution of each module | 1920x1080 (Full HD) |  |
|  | Driver | OS: Windows XP, Window Vista, Windows 7 and latest |  |
|  | Protection glass Thickness | Approx. 3.4mm |  |
|  | Touch Technology | Optical Imaging Method |  |
|  | Interface ports | 2*DP-in, 2*HDMI, 1*DP-out |  |
|  | Speaker Output | yes |  |
|  | Aspect ratio of each Module/Cube | 16:9 |  |
|  | Minimum Brightness | 170 candelas/sq.m |  |
|  | Brightness & Colour adjustable Manually | Yes |  |
|  | Contrast ratio (minimum) | 1500:1 |  |
|  | Operating temperature range | 160C to 300 C |  |
|  | Operating Relative Humidity | 20-80% non-condensing |  |
|  | Power supply (nominal) | AC 230V±5%, 50±5%, Hz |  |

# Controller Features

- The Controller of LVWS supplied with each set of Video walls shall have the following features as a minimum.

- Support 64 Bit latest Windows Operating System

- Quad Core or higher

- Minimum 16 GB expandable to 32 GB

- DVD-ROM, Keyboard & mouse with 2-buttom + wheel/button

- Internal Auxiliary Memory 480GB minimum

- Common Monitor, Keyboard & Mouse (dual band wireless) for all controllers

- Redundant AC power supply.

- Dual Gigabit Ethernet port

- Interface for CCTV

- Type of Vídeo Signals Supported-

- RGB Analog up to 1920x1200 (up to 165 MHz pixel clock)

- DVI up to 1920x1200. (Up to 165 MHz pixel clock)

- Interface for Video conferencing Equipment

- Interface for Laptop

- Controllers should be capable of mirror images through dual LAN.

- Four videos and three universal input ports.

- A Laptop with the installation kit for Video Conferencing system shall be provided to operate/control all Video Walls.

- VC equipment shall have only one interface point to connect controller. For further connection to remaining controllers, supplier shall include additional switch/distributer etc. as required to display VC output on all LVWs.

- Supplier shall offer OEM application software (with licenses) for wall setup source switching and other controls required for optimization of the display system. The software should be able to configure different layouts. The software shall be able to pre-configure various display layouts (arrangement of different windows) and access them at any time with a simple mouse click. The window can	be of different size and could contain display from different applications/sources. The software shall be able to push the screen content of a Laptop/Windows PC to be shown on the Display wall in scalable and moveable windows in real time environment. The Laptop/Windows PC shall be connected to the Controller. Necessary hardware required to run the application software shall be in the scope of vendor.

# Multipoint Control Unit (MCU)

Under this project, one number of MCU shall be supplied and installed at SLDCs. Technical Specifications of above is given below:

- CAPACITY

- MCU should be a Hardware/appliance solution of either 1U or 2U with all the accessories rack mount into 19-inch rack.

- Should have the ability to connect at least 18 video sites over SIP and H.323 protocols without cascading and MCU license shall be perpetual (no subscription based). At any point of time at least 18 Full HD total participants shall be able to join a meeting on MCU in any combination via VC end point, WebRTc, Application, software-based desktop, Mobile, Laptop/desktop etc.

- Up to 34 sites in continuous presence with auto layout and shall support voice switching.

- All video ports must support 30 fps of 1080p or better resolution.

- Shall support 2 Mbps or more bandwidth per port without any loss of ports at higher bandwidth.

- Minimum 10 layouts which can be accessed during a conference.

- Shall support Far end camera control.

- Should support combination of Full HD, HD & SD in the same conference.

- Shall support connections with remote users over the Internet. MCU shall support software-based desktop and webRTc to join from internet.

- It should support an external appliance-based recording & streaming solution of at least 500GB of video streams from each location and collectively in one grid and shall support 3 concurrent meetings at 1080p from day one.

- Shall support Active Speaker selection using voice switching and shall support automatic face detection and framing to create an optimized view of that single participant or group.

- Dedicated console port (serial/RJ45) or Web based management options for configuration/administration from network or a remote location.

- MCU shall support management tool for monitoring & managing ongoing meetings, creating meeting and directory.

- The MCU should support presentation sharing on H.239 & BFCP through the video endpoint.

- Shall support user end and managed mute control.

- Shall support IVR prompts for auto attendance.

- Dial-in and dial out facility in a conference without disturbing ongoing conference on SIP and H.323

- Shall support external recording and video-on-demand solutions.

- The Soft Client must support dual monitor capability: a first monitor for people and an extended or second monitor for presentations, meaning viewing presentations in a separate window.

- VIDEO STANDARDS

- Shall support H.261, H.263, H.263+ & H.264 video algorithms.

- Shall support H.239 & BFCP {Presenter and Presentation mode)

- AUDIO STANDARDS

- Shall support audio standards like: G.711, G.722, G.7Z2.1, G729A & MPECG4 AAC-LD/LC.

- Shall support individual site audio mute.

- ITU STANDARDS

- H.224/H.281 far end camera control

- H.225, H.245, H.241

- NETWORK FEATURES

- 10/100/1000 NIC (RJ 45 connector) or better

- IPv4 & IPv6 support

- Diffserv and QoS support

- IP address conflict warning

- H.323 and SIP at 6 Mbps or more.

- USER INTERFACE & SECURITY

- Direct control from remote sites

- Web-based control

- Support for SNMP

- Support to operate in integration with existing industry standard MCUs and Video recorders.

- This MCU shall support 128 bit and 256-bit AES encryption on H.323 & SIP using H.235 for every participant without affecting any other feature, functionality, or port count. There should be no port loss when AES encryption is turned on.

- The complete MCU solution (MCU, Software and associated hardware) & Endpoints should be supplied from the same OEM.

# Video Endpoints

Video endpoints shall be installed at various control centres as listed in the BoQ. The technical specifications are as described below:

- CAPACITY

- End point must support 30 fps of 1080p or better resolution.

- Shall support 6 Mbps or more bandwidth.

- Minimum 10 pre-sets which can be accessed during a conference using remote.

- Shall support combination of HD & SD in the same conference.

- Shall support IP & SIP.

- VIDEO RESOLUTION

- Input for PC: 4K@15fps and 1080p

- Output for PC: 4K@15fps and 1080p

- VIDEO STANDARDS

- Shall support H.264AVC, H.264 HP and H.265 or better video algorithms.

- Shall support H.239 & BFCP {Presenter and Presentation mode)

- Picture in picture facility.

- AUDIO STANDARDS

- Shall support audio standards like: G.711, G.722, G.772.1 or better.

- Shall support Automatic Gain control, Noise block & Instant Adaptation Echo cancellation.

- ITU STANDARDS

- H.224/H.281 far end camera control

- H.225, H.245, H.241

- NETWORK FEATURES

- 10/100/100a NIC (RJ 45 connector) or better

- IPv4 & IPv6 support

- Diff serve and QoS support.

- IP address conflict warning

- H.323 and SIP at 6 Mbps or more.

- USER INTERFACE & SECURITY

- Direct control from remote sites

- Web-based control

- Support for SNMP

- Support to operate in integration with existing industry standard MCUs and Video recorders.

- This endpoint shall support 128 bit and 256-bit AES encryption on IP & SIP using H.235 for every participant without affecting any other feature, functionality or port count. There should be no port loss when AES encryption is turned on.

- VIDEO INPUT

- Shall have minimum one Full HD input from the camera.

- Shall have 2x HDMI/DVI/USB/HDCI for an external camera source.

- Shall have a minimum of one HDMI input for PC connectivity.

- VIDEO OUTPUT

- Shall	have minimum two HDMI Output integrating with TV/ Plasma/Projector/Video Walls

- Shall be capable of displaying main video on one Full HD Screen and presentation/dual video on another screen.

- AUDIO INPUTS

- Codec must support 3 microphone ports and bidder shall supply minimum 2 omni directional mics.

- Codec should support third party certified DSP via USB to connect 8 microphones.

- Should have minimum one PC audio in 3.5mm jack.

- AUDIO OUTPUTS

- Should have Minimum 2 Audio Outputs; 3.5mm jack and HDMI.

- USB PASSTHROUGH

- Codec should have inbuilt USB C Port to use VC system as an external camera and microphones when connected to a Laptop/PC over a single USB cable without using any external hardware, software components or converter to connect to any Cloud Based VC platform like Cisco Webex, Zoom, BlueJeans, Microsoft Teams, Google Meet, etc.

- Should support minimum 1080p30fps video transmission in USB Pass-thru mode.

- Other requirements of endpoint

- 10M USB cable to be supplied from same OEM.

- Endpoint should support a minimum 8"inch touch controller from the same OEM.

# Camera

- Camera shall be installed – to be supplied along with end point from the same OEM. The technical specification of the same is defined below:

- Shall support 1080p 30fps or better resolution.

- Shall have both auto or manual options in setting Focus and Brightness.

- Shall support 12 x or above optical zoom, minimum +/- 80-degree pan & +/- 10-degree tilt capability to operate in normal room illumination conditions.

- Shall support far end camera Control.

# Wireless Microphone System

The specification of the Microphone System is detailed below; the number of microphones in each Control Centre shall be as per BoQ. Microphones should be immune to GSM noise caused by mobile phones. Microphones should have a wide band frequency response. Microphones should have buttons for muting and pairing and indications for the same. Shall be equipped power charger with base station for holding and charging microphones. Microphones shall be capable of providing a minimum of 6 hours of talk time on battery on full charge. The base station shall support interface with HD Video Conferencing System compatible to connect at least 8 microphones. The supplied microphones should have at least 02 lapel microphones. The system should support 220V AC, 50Hz input Power.

# Accessories

All necessary cable/accessories must be supplied along with for the interconnectivity with the Video Wall/Laptop to make videos conferencing fully functional. All power cord shall be with Indian Power Connectors. All other accessories must be supplied to ensure proper compatibility, connectivity, and functionality of the supplied video conferencing system.

# FAT methodology for VC equipment

From each batch/total BoQ quantity of VC equipment supplied by the Contractor for Factory acceptance testing (FAT), the Employer shall select 20% of total supplied lot as random sample(s) to be tested for each type of equipment such as microphone, video walls, camera etc. for acceptance. All required FAT tests as per approved FAT procedures, shall be performed. The physical verification and/or random Power ON tests shall be carried out on 100% of the offered quantities as per the approved FAT procedure. The above requirement is tentative, the exact sampling criteria/methodology for FAT shall be finalized during Detail Engineering stage.

# Technical Specifications for Wall Mount Speakers – 2 pairs

- Passive Two-way wall mount speakers with minimum 6.5-inch woofer and 1 inch tweeter.

- Frequency Range: 65 Hz to 19 kHz, 60 W rms continuous pink noise, 120 W RMS continuous program. 87 dB Spl.

- Coverage Angle: Horizontal: 115°, Vertical: 55° or better.

- Tapping: 32, 16 watt selectable @70/100 volt. Provided with 360-degree mounting accessories.

# Technical Specifications for Amplifier

- Dual Channel Class D amplifier with 100 watt per channel.

- Input: 2x balanced/unbalanced,

- Output: 2 channels @ 70/100V.

- THD+Noise: 0.1%,

- Signal to Noise ratio: 100 dB or better.

- Shall have protection from Clip limiting, thermal, short circuit.

- Shall meet Regulatory compliance: CE, ENERGY STAR, FCC RoHS, UL.

---------------------------------------------- End of Section ----------------------------------------------

Annexure-VIII

Vol-II Part-B, Appendix-G, Bill of Quantity:

Table - RTU OF J&K PDD

|  | RTU OF J&K PDD |  |  |
| --- | --- | --- | --- |
| SI. No. | Item Description | Unit | Quantity |
| A | Hardware |  |  |
| 1 | RTU & associated items |  |  |
| (a) | RTU base equipment as per technical specification | Set | 78 |
| (b) | CPU Cards | Nos | 156 |
| (c) | Digital Input Module (16 channel) | Nos | 1371 |
| (d) | Digital Output Module (8 channel) | Nos | 644 |
| (e) | Analog Input Module (8 channel) | Nos | 100 |
| (f) | Multi-Function Transducers | Nos | 2228 |
| (g) | Weather Sensor | Nos | 78 |
| (h) | OLTC Transducer | Nos | 227 |
| (i) | Contact Multiplying Relays (CMRs) | Nos | 21430 |
| (j) | Time Synchronization Equipment | Set | 78 |
| (k) | Heavy Duty Relay | Nos | 4456 |
| (l) | Supervisory Interface Cubicles (SIC) panel for mounting MFTs, CMR etc if required | Set | 78 |
| (m) | LDMS System Along with software | Set | 78 |
| (n) | Furniture for LDMS system (1 Table &1 Chair) | Set | 78 |
| (o) | Inverter for LDMS | Nos | 78 |
| (p) | Cables for RTU | Lot | 78 |
| (q) | Laptop for PCMT | Nos | 8 |
| B | Services |  |  |
| 1 | Integration with Control Centres (SLDC/RLDC) on IEC104 at substation & control centre | Lot | 78 |
| C | Annual Maintenance Contract |  |  |
| 1 | Integration of new bay (Including supply & commissioning of each type Cards, MFT, CMR,Cables etc) at RTU site | Lot | 300 |
| 2 | RTU maintenance (1 Years) | Lot | 1 |
| 3 | RTU maintenance (6 Years) | Lot | 1 |

Vol-II Part-B, Appendix-G, Bill of Quantity

Table - RTU OF DTL

| RTU OF DTL |  |  |  |  |
| --- | --- | --- | --- | --- |
| SI. No. | Item Description | Unit | Quantity |
| A | Hardware |  |  |
| 1 | RTU & associated items |  |  |
| (a) | RTU base equipment as per technical specification | Set | 4 |
| (b) | CPU Cards | Nos | 8 |
| (c) | Digital Input Module (16 channel) | Nos | 113 |
| (d) | Digital Output Module (8 channel) | Nos | 51 |
| (e) | Analog Input Module (8 channel) | Nos | 4 |
| (f) | Multi-Function Transducers | Nos | 185 |
| (g) | Weather Sensor | Nos | 4 |
| (h) | OLTC Transducer | Nos | 17 |
| (i) | Contact Multiplying Relays (CMRs) | Nos | 1769 |
| (j) | Time Synchronization Equipment | Set | 4 |
| (k) | Heavy Duty Relay | Nos | 370 |
| (l) | Supervisory Interface Cubicles (SIC) panel for mounting MFTs, CMR etc if required | Set | 2 |
| (m) | LDMS System Along with software | Set | 4 |
| (n) | Furniture for LDMS system (1 Table &1 Chair) | Set | 4 |
| (o) | Inverter for LDMS | Nos | 4 |
| (p) | Cables for RTU | Lot | 4 |
| (q) | Laptop for PCMT | Nos | 1 |
| B | Services |  |  |
| 1 | Integration with Control Centres (SLDC/RLDC) on IEC104 at substation & control centre | Lot | 4 |
| C | Annual Maintenance Contract |  |  |
| 1 | Integration of new bay (Including supply & commissioning of each type Cards, MFT, CMR,Cables etc) at RTU site | Lot | 40 |
| 2 | RTU maintenance (1 Years) | Lot | 1 |
| 3 | RTU maintenance (6 Years) | Lot | 1 |

Annexure-IX

| Part-D, Appendix A: RTU I/O counts for JK PDD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| S.No. | Name of the Sub-station |  | Nos | LDMS System | GPS System & Interface | AI & Transducers |  |  |  |  | DI (Digital Status input) |  |  |  | DO |
|  |  |  |  |  |  | MFT/MFM (MODBUS/IEC 60870-5-103) |  |  | Weather Sensor | OLTC Transducers (4-20 mA) | Total Double Status Points | Single Status Points | Single Status Points | Total |  |
|  | Station No | Voltage Level |  |  |  | Total No. of Bays | Total No. of MFM/ MFT | No of bus |  |  | CB (NO & NC) | Protection/ Alarms | Isolators |  |  |
| RTUs of JK PDD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 | AKHNOOR | 132 kV/33 kV | 1 | 1 | 1 | 30 | 32 | 2 | 1 | 6 | 36 | 64 | 128 | 264 | 60 |
| 2 | ALUSTENG | 220 kV/132 kV / 33 kV | 1 | 1 | 1 | 41 | 46 | 5 | 1 | 5 | 46 | 92 | 184 | 368 | 82 |
| 3 | AMARGARH | 132 kV / 33 kV | 1 | 1 | 1 | 33 | 35 | 2 | 1 | 4 | 37 | 70 | 140 | 284 | 66 |
| 4 | AWANTIPORA | 132 kV / 33 kV | 1 | 1 | 1 | 30 | 32 | 2 | 1 | 3 | 33 | 64 | 128 | 258 | 60 |
| 5 | BADAMPORA | 132 kV / 33 kV | 1 | 1 | 1 | 21 | 23 | 2 | 1 | 2 | 23 | 46 | 92 | 184 | 42 |
| 6 | BANDIPORA | 132 kV / 33 kV | 1 | 1 | 1 | 19 | 21 | 2 | 1 | 2 | 21 | 42 | 84 | 168 | 38 |
| 7 | BANIHAL | 132 kV/33 kV | 1 | 1 | 1 | 20 | 24 | 4 | 1 | 4 | 24 | 48 | 96 | 192 | 40 |
| 8 | BARN | 220kV/132kV/33kV | 1 | 1 | 1 | 42 | 46 | 4 | 1 | 6 | 48 | 92 | 184 | 372 | 84 |
| 9 | BATOTE | 132 kV/33 kV | 1 | 1 | 1 | 23 | 25 | 2 | 1 | 2 | 25 | 50 | 100 | 200 | 46 |
| 10 | BATTAL MANYAL | 132 kV/33 kV | 1 | 1 | 1 | 21 | 24 | 3 | 1 | 1 | 22 | 48 | 96 | 188 | 42 |
| 11 | BB1 | 132 kV/33 kV | 1 | 1 | 1 | 39 | 41 | 2 | 1 | 3 | 42 | 82 | 164 | 330 | 78 |
| 12 | BB2 | 132 kV/33 kV | 1 | 1 | 1 | 28 | 30 | 2 | 1 | 2 | 30 | 60 | 120 | 240 | 56 |
| 13 | BEMINA | 132 kV / 33 kV | 1 | 1 | 1 | 33 | 35 | 2 | 1 | 4 | 37 | 70 | 140 | 284 | 66 |
| 14 | BHALLESA | 132 kV/33 kV | 1 | 1 | 1 | 19 | 23 | 4 | 1 | 4 | 23 | 46 | 92 | 184 | 38 |
| 15 | BISHNAH | 220kV/132kV/33kV | 1 | 1 | 1 | 47 | 50 | 3 | 1 | 4 | 51 | 100 | 200 | 402 | 94 |
| 16 | BUDGAM | 220 kV/132 kV / 33 kV | 1 | 1 | 1 | 31 | 35 | 4 | 1 | 5 | 36 | 70 | 140 | 282 | 62 |
| 17 | CANAL | 132 kV/33 kV | 1 | 1 | 1 | 36 | 37 | 1 | 1 | 3 | 39 | 74 | 148 | 300 | 72 |
| 18 | CHADOORA | 132 kV / 33 kV | 1 | 1 | 1 | 19 | 21 | 2 | 1 | 2 | 21 | 42 | 84 | 168 | 38 |
| 19 | CHANDAK | 132 kV/33 kV | 1 | 1 | 1 | 15 | 18 | 3 | 1 | 2 | 17 | 36 | 72 | 142 | 30 |
| 20 | CHASHMASHAHI | 132 kV / 33 kV | 1 | 1 | 1 | 30 | 32 | 2 | 1 | 4 | 34 | 64 | 128 | 260 | 60 |
| 21 | CHATHA | 132 kV/33 kV | 1 | 1 | 1 | 20 | 24 | 4 | 1 | 4 | 24 | 48 | 96 | 192 | 40 |
| 22 | CHENANI | 132 kV/33 kV | 1 | 1 | 1 | 24 | 28 | 4 | 1 | 4 | 28 | 56 | 112 | 224 | 48 |
| 23 | CHOWADHI | 220kV/33kV | 1 | 1 | 1 | 17 | 21 | 4 | 1 | 4 | 21 | 42 | 84 | 168 | 34 |
| 24 | DELINA | 220 kV/132 kV / 33 kV | 1 | 1 | 1 | 40 | 45 | 5 | 1 | 2 | 42 | 90 | 180 | 354 | 80 |
| 25 | DRABA | 132 kV/33 kV | 1 | 1 | 1 | 22 | 24 | 2 | 1 | 2 | 24 | 48 | 96 | 192 | 44 |
| 26 | GANGYAL | 132 kV/33 kV | 1 | 1 | 1 | 22 | 24 | 2 | 1 | 2 | 24 | 48 | 96 | 192 | 44 |
| 27 | GLADNI | 220kV/132kV/33kV | 1 | 1 | 1 | 65 | 68 | 3 | 1 | 7 | 72 | 136 | 272 | 552 | 130 |
| 28 | HABAK | 132 kV / 33 kV | 1 | 1 | 1 | 29 | 31 | 2 | 1 | 3 | 32 | 62 | 124 | 250 | 58 |
| 29 | HARWAN GIS | 220 kV / 33 kV | 1 | 1 | 1 | 16 | 18 | 2 | 1 | 2 | 18 | 36 | 72 | 144 | 32 |
| 30 | HIRANAGAR | 220kV/132kV/66kV | 1 | 1 | 1 | 51 | 54 | 3 | 1 | 4 | 55 | 108 | 216 | 434 | 102 |
| 31 | JANIPUR | 132 kV/33 kV | 1 | 1 | 1 | 35 | 38 | 3 | 1 | 3 | 38 | 76 | 152 | 304 | 70 |
| 32 | JHAJJAR KOTLI | 132 kV/33 kV | 1 | 1 | 1 | 25 | 27 | 2 | 1 | 2 | 27 | 54 | 108 | 216 | 50 |
| 33 | JOURIAN | 132 kV/33 kV | 1 | 1 | 1 | 21 | 24 | 3 | 1 | 2 | 23 | 48 | 96 | 190 | 42 |
| 34 | KALAKOT | 132 kV/33 kV | 1 | 1 | 1 | 13 | 15 | 2 | 1 | 2 | 15 | 30 | 60 | 120 | 26 |
| 35 | KANGAN | 132 kV / 33 kV | 1 | 1 | 1 | 17 | 19 | 2 | 1 | 2 | 19 | 38 | 76 | 152 | 34 |
| 36 | KATHUA | 220Kv/66Kv | 1 | 1 | 1 | 17 | 21 | 4 | 1 | 4 | 21 | 42 | 84 | 168 | 34 |
| 37 | KATHUA | 132kV/66kV | 1 | 1 | 1 | 34 | 36 | 2 | 1 | 3 | 37 | 72 | 144 | 290 | 68 |
| 38 | KATRA | 132 kV/33 kV | 1 | 1 | 1 | 18 | 20 | 2 | 1 | 1 | 19 | 40 | 80 | 158 | 36 |
| 39 | KHANYAR GIS | 132 kV / 33 kV | 1 | 1 | 1 | 17 | 20 | 3 | 1 | 2 | 19 | 40 | 80 | 158 | 34 |
| 40 | KHELANI | 132 kV/33 kV | 1 | 1 | 1 | 26 | 28 | 2 | 1 | 2 | 28 | 56 | 112 | 224 | 52 |
| 41 | KHREW | 132 kV / 33 kV | 1 | 1 | 1 | 18 | 20 | 2 | 1 | 2 | 20 | 40 | 80 | 160 | 36 |
| 42 | KHUNMOH | 132 kV / 33 kV | 1 | 1 | 1 | 18 | 20 | 2 | 1 | 2 | 20 | 40 | 80 | 160 | 36 |
| 43 | KISHTWAR | 132 kV/33 kV | 1 | 1 | 1 | 24 | 26 | 2 | 1 | 2 | 26 | 52 | 104 | 208 | 48 |
| 44 | KULGAM | 132 kV / 33 kV | 1 | 1 | 1 | 19 | 21 | 2 | 1 | 2 | 21 | 42 | 84 | 168 | 38 |
| 45 | KUPWARA | 132 kV / 33 kV | 1 | 1 | 1 | 26 | 28 | 2 | 1 | 3 | 29 | 56 | 112 | 226 | 52 |
| 46 | LASSIPORA | 132 kV / 33 kV | 1 | 1 | 1 | 17 | 19 | 2 | 1 | 1 | 18 | 38 | 76 | 150 | 34 |
| 47 | LASSIPORA GIS | 220 kV / 33 kV | 1 | 1 | 1 | 17 | 20 | 3 | 1 | 1 | 18 | 40 | 80 | 156 | 34 |
| 48 | LISSAR | 132 kV / 33 kV | 1 | 1 | 1 | 17 | 20 | 3 | 1 | 2 | 19 | 40 | 80 | 158 | 34 |
| 49 | LJHP | 132 kV / 33 kV | 1 | 1 | 1 | 22 | 26 | 4 | 1 | 4 | 26 | 52 | 104 | 208 | 44 |
| 50 | MAGAM | 132 kV / 33 kV | 1 | 1 | 1 | 18 | 20 | 2 | 1 | 2 | 20 | 40 | 80 | 160 | 36 |
| 51 | MAHANPUR | 132 kV/33 kV | 1 | 1 | 1 | 26 | 28 | 2 | 1 | 1 | 27 | 56 | 112 | 222 | 52 |
| 52 | MATAN | 132 kV / 33 kV | 1 | 1 | 1 | 19 | 21 | 2 | 1 | 2 | 21 | 42 | 84 | 168 | 38 |
| 53 | MIR BAZAR | 220 kV / 132 kV | 1 | 1 | 1 | 30 | 32 | 2 | 1 | 2 | 32 | 64 | 128 | 256 | 60 |
| 54 | MIRANSAHIB | 132 kV/33 kV | 1 | 1 | 1 | 37 | 39 | 2 | 1 | 3 | 40 | 78 | 156 | 314 | 74 |
| 55 | NAGROTA | 220kV/33kV | 1 | 1 | 1 | 20 | 24 | 4 | 1 | 4 | 24 | 48 | 96 | 192 | 40 |
| 56 | NHPC KISHTWAR | 132 kV/33 kV | 1 | 1 | 1 | 20 | 24 | 4 | 1 | 4 | 24 | 48 | 96 | 192 | 40 |
| 57 | PAMPORE 132 kV | 132 kV / 33 kV | 1 | 1 | 1 | 38 | 40 | 2 | 1 | 4 | 42 | 80 | 160 | 324 | 76 |
| 58 | PAMPORE 220 kV | 220 kV / 132 kV | 1 | 1 | 1 | 24 | 26 | 2 | 1 | 3 | 27 | 52 | 104 | 210 | 48 |
| 59 | PATTAN | 132 kV / 33 kV | 1 | 1 | 1 | 27 | 29 | 2 | 1 | 3 | 30 | 58 | 116 | 234 | 54 |
| 60 | PAUNICHAK | 132 kV/33 kV | 1 | 1 | 1 | 23 | 25 | 2 | 1 | 2 | 25 | 50 | 100 | 200 | 46 |
| 61 | RAJOURI | 132 kV/33 kV | 1 | 1 | 1 | 33 | 35 | 2 | 1 | 3 | 36 | 70 | 140 | 282 | 66 |
| 62 | RAMBAN | 220kV/132kV/33kV | 1 | 1 | 1 | 40 | 44 | 4 | 1 | 2 | 42 | 88 | 176 | 348 | 80 |
| 63 | RAWALPORA | 132 kV / 33 kV | 1 | 1 | 1 | 31 | 32 | 1 | 1 | 4 | 35 | 64 | 128 | 262 | 62 |
| 64 | SAMBA | 220Kv/66Kv | 1 | 1 | 1 | 17 | 21 | 4 | 1 | 2 | 19 | 42 | 84 | 164 | 34 |
| 65 | SAMBA | 132kV/66kV | 1 | 1 | 1 | 28 | 30 | 2 | 1 | 2 | 30 | 60 | 120 | 240 | 56 |
| 66 | SHEERI | 132 kV / 33 kV | 1 | 1 | 1 | 18 | 20 | 2 | 1 | 2 | 20 | 40 | 80 | 160 | 36 |
| 67 | SHOPIAN | 132 kV / 33 kV | 1 | 1 | 1 | 17 | 22 | 3 | 1 | 2 | 19 | 44 | 88 | 170 | 38 |
| 68 | SIDHRA | 132 kV/33 kV | 1 | 1 | 1 | 24 | 26 | 2 | 1 | 2 | 26 | 52 | 104 | 208 | 48 |
| 69 | SIOT | 132 kV/33 kV | 1 | 1 | 1 | 20 | 24 | 4 | 1 | 4 | 24 | 48 | 96 | 192 | 40 |
| 70 | TENGPORA GIS | 132 kV / 33 kV | 1 | 1 | 1 | 24 | 28 | 4 | 1 | 3 | 27 | 56 | 112 | 222 | 48 |
| 71 | TETHAR | 132kv/33kV | 1 | 1 | 1 | 15 | 17 | 2 | 1 | 1 | 16 | 34 | 68 | 134 | 30 |
| 72 | UDHAMPUR | 220kV/132kV/33kV | 1 | 1 | 1 | 48 | 51 | 3 | 1 | 5 | 53 | 102 | 204 | 412 | 96 |
| 73 | UPERSINDH-I | 11 kV / 132 kV | 1 | 1 | 1 | 4 | 8 | 4 | 1 | 4 | 8 | 16 | 32 | 64 | 8 |
| 74 | UPERSINDH-II | 11 kV / 132 kV | 1 | 1 | 1 | 9 | 13 | 4 | 1 | 4 | 13 | 26 | 52 | 104 | 18 |
| 75 | VILGAM | 132 kV / 33 kV | 1 | 1 | 1 | 17 | 19 | 2 | 1 | 1 | 18 | 38 | 76 | 150 | 34 |
| 76 | WAGANPORA | 132 kV / 33 kV | 1 | 1 | 1 | 29 | 31 | 2 | 1 | 3 | 32 | 62 | 124 | 250 | 58 |
| 77 | WANPOH | 132 kV / 33 kV | 1 | 1 | 1 | 36 | 39 | 3 | 1 | 5 | 41 | 78 | 156 | 316 | 72 |
| 78 | ZAINKOTE | 220 kV/132 kV / 33 kV | 1 | 1 | 1 | 42 | 45 | 3 | 1 | 4 | 46 | 90 | 180 | 362 | 84 |
|  | Sub-Total |  | 78 | 78 | 78 | 2018 | 2228 | 208 | 78 | 227 | 2245 | 4456 | 8912 | 17858 | 4040 |
|  | Note:- The Station wise quantity given above table is tentative and may vary after site survey of RTU locations |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| List of RTU Spare of RLDC/SLDCs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | NRLDC |  | HP |  |  | UPPTCL |  |  | BBMB |  | PSTCL |  | DTL |  |  | HVPNL |  |  | J&K |  |  | RRVPNL |  |  | RRVPNL Sub-SLDC-Kota |  | RRVPNL Sub-SLDC-Ratangarh |  | RRVPNL Sub-SLDC-Jodhpur |  | PTCUL |  | PTCUL Sub-SLDC Rishikesh |
| Sl.no | Item description | Unit | Quantity |  | Quantity |  |  | Quantity |  |  | Quantity |  | Quantity |  | Quantity |  |  | Quantity |  |  | Quantity |  |  | Quantity |  |  | Quantity |  | Quantity |  | Quantity |  | Quantity |  | Quantity |
|  |  |  | Main CC | Backup-CC | Main CC | Backup-CC | Main CC |  | Backup-CC | Main CC |  | Main CC |  | Main CC |  | Backup-CC | Main CC |  | Backup-CC | Main CC |  | Backup-CC | Main CC |  | Backup-CC | Main CC |  | Main CC |  | Main CC |  | Main CC |  | Backup-CC | Main CC |
| F | RTU Spares |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 | CPU Cards | No. | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | 0 | 0 |  | 0 | 16 |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |
| 2 | Digital Input Module (16 channel) | No. | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 12 |  | 0 | 0 |  | 0 | 138 |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |
| 3 | Digital Output Module (8 channel) | No. | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 6 |  | 0 | 0 |  | 0 | 65 |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |
| 4 | Analog Input Module (8 channel) | No. | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | 0 | 0 |  | 0 | 10 |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |
| 5 | Multi Function Transducers | No. | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 19 |  | 0 | 0 |  | 0 | 223 |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |
| 6 | OLTC Transducer | No. | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | 0 | 0 |  | 0 | 23 |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |
| 7 | Contact Multiplying Relays (CMRs) | No. | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 177 |  | 0 | 0 |  | 0 | 2143 |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |
| 8 | Heavy Duty Relay | No. | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 37 |  | 0 | 0 |  | 0 | 446 |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |

Annexure-X