| Sl. No | Clause No | Existing clause | Amended clause |
| --- | --- | --- | --- |
|  | Vol. II Part-A, Section – 1, Clause no. –1.7 | Existing SCADA/EMS systems at Load Dispatch Centers (LDCs) of various regions ……. | Inserted Existing SCADA/EMS systems at Load Dispatch Centers (LDCs) of various regions ……. - The existing SCADA system in northern region is Spectrum Power 7 Version 1.0 and the historian system is EDNA version: 2.0.14. |
|  | Vol. II Part-A, Section – 1, Clause no. – 1.8, Intent of the Project | Intent of the Project ……. The delivered system should be robust enough to run all the critical functions without any interruption when one machine fails e.g., failure of one SCADA server or failure of a power supply in the server should not interrupt the availability of the functions catered by the server. ……. The Diagnostic software’s shall be provided with the system to perform health monitoring of different components so that timely action can be taken e. g. VPS module health (e.g., CPU) monitoring. Server CPU utilization can be monitored so that, before it goes beyond a percentage and system performance deteriorate, action can be taken. System should be secure against the cyber threats.The measures should be taken to harden the system and make multiple level of defense e.g., firewalls supplied should be from different OEM in a Control Centre. ……. | Replace with Intent of the Project ……. The delivered system should be robust enough to run all the critical functions without any interruption when one machine fails e.g., failure of one SCADA server or failure of power supply in the redundant server should not interrupt the availability of the functions catered by the server. ……. The Diagnostic software’s shall be provided with the system to perform health monitoring of different components so that timely action can be taken e.g. VPS module health (e.g. CPU, RAM utilization etc.) monitoring. Server CPU & RAM utilization can be monitored so that, before it goes beyond a percentage and system performance deteriorate, action can be taken. System should be secure against the cyber threats.The measures should be taken to harden the system and make multiple level of defense e.g., firewalls supplied should be from different OEM in a Control Centre as specified in Part-B section-5. ……. |
|  | Vol. II Part-A Section-1, Clause 1.10, Scope of Work | Scope of Work ……. c )Integration of Main and Back up Control Centers with existing Control Centers on Mix mode ICCP protocol (i.e., new control centers are exchanging data on secure ICCP and existing on plain ICCP and/or Secure ICCP protocol). ……. (y) …….This shall include all the services including cabling and interface modification required for intervening period before final shifting to main Control Center. | Replace with Scope of Work ……. (c )Integration of Main and Back up Control Centers with other Control Centers on Mix mode ICCP protocol (i.e., new control centers are exchanging data on secure ICCP and existing on plain ICCP and/or Secure ICCP protocol). ……. (y) …….This shall include all the services including cabling and interface modification required for intervening period before final shifting to main Control Center. The provision for clean data wiping shall be in the scope of contractor during dismantling as per owner’s policy. ……. (ss) Annual OT security audit of supplied RTU under this project during entire AMC period as per cyber security guidelines issued by statutory authority and amended time to time shall be in the scope of the contractor. The above audit shall be carried out by following ISO 27019 along with other provision. |
|  | Vol. II Part-A, Section – 1, Clause no. – 1.11, General Requirements | General Requirements …….. Adequate measures shall be taken to provide protection against rodents, contaminants, pollutants, water & moisture, lightning & short circuit, vibration and electromagnetic interference etc. The delivered system should be robust enough to run all the critical functions without any interruption when one machine fails e.g., failure of one SCADA server or failure of a power supply in the server should not interrupt the availability of the functions catered by the server. System Network should be resilient enough to withstand single fault on network devices. It should be able to monitor multivendor network elements (Server, workstation, Router, switch, VPS cubes etc.). The Diagnostic software’s shall be provided with the system to perform health monitoring of different components so that timely action can be taken e.g., VPS module health (e.g., CPU) monitoring. Server CPU utilization can be monitored so that, before it goes beyond a percentage and system performance deteriorate, action can be taken. System should be secure against the cyber threats. The measures should be taken to harden the system and make multiple level of defense e.g., firewalls supplied should be from different OEM in a Control Centre. System should be flexible enough and it should be possible to do user interface related adjustment on-line without limiting operator options e.g., on-lining of new displays, adjustment of Colour and brightness of VPS etc. shall not require downtime or image loss at any time to the operator. The entire performance requirements shall be demonstrated for the worst case, if requirements are not explicitly mentioned. All the requirements of the specification are to be met by the delivered system. If there is any conflicting requirement, the applicable requirement shall be decided by the owner and that shall be binding on the contractor. Backup Control Centre should be considered as independent CC (i.e., users are sitting at Backup CC and operating all the functions delivered even when Main CC is available) for licenses i.e., licenses for Backup CC should not be dependent on Main CC in anyway. The Contractor shall demonstrate a specified level of performance of the offered items during well-structured factory and field tests. It shall be the employer’s/Owner’s choice to keep Furniture colour and design different for each Control Centre or same for all. …….. If any development, customizations, testing etc. needs to be done for the solution provided, then the same shall be borne by the contractor at its own cost throughout the period of contract including AMC. …….. | Replace with General Requirements …….. Adequate measures shall be taken to provide protection against rodents, contaminants, pollutants, water & moisture, lightning & short circuit, vibration and electromagnetic interference etc. It shall be the employer’s/Owner’s choice to keep Furniture colour and design different for each Control Centre or same for all. …….. If any development, customizations, testing etc. needs to be done for the solution provided, then the same shall be borne by the contractor at its own cost during entire contract period including extension of contract, if any. …….. |
|  | Vol. II Part-A Section-1, Clause 1.12.2, Contractor’s Responsibilities and Obligations | Provision to be complied as per latest guidelines of GOI/MOP/DPIIT/DOT with subsequent amendments in the entire period of contract. | Replace with All provisions and orders of DPIIT, MoP, DoT, Meity or any other Nodal Ministry have to be mandatorily complied by the contractor with subsequent amendments in the entire period of contract. |
|  | Vol. II Part-A, Section – 1, Clause no. – 1.12.4, Owner’s Responsibilities and Obligations | Owner’s Responsibilities and Obligations | Inserted - Communication system and link for data communication (RTUs to control centers and between control centers) |
|  | Vol. II Part-A, Section – 1, Clause no. – 1.12.5, Employer’s Responsibilities and Obligations | Employer’s Responsibilities and Obligations …….. viii. Coordination of the Contractor's activities with the Employer's concerned departments and Owner. | Replace with Employer’s Responsibilities and Obligations …….. viii. Coordination of the Contractor's activities with the Employer's concerned departments and Owner. POWERGRID as the consultant shall also be responsible for all the above items and services on behalf of HP SLDC and NRLDC except for the site activities. |
|  | Vol. lI Part-A, Section – 1, Clause – 1.13, Relocation and Commissioning at New Location (as per BOQ) | Relocation and Commissioning at New Location (as per BOQ) …….. • Project management. • Technical management. Following are the Owner scope of work at control centre which is being shifted during Relocation and Commissioning at New Location: …… | Replace with Relocation and Commissioning at New Location (as per BOQ) …….. • Project management. • Technical management. • Integration, testing and validation at new location for RTUs, Control centers, other applications etc. The contractor shall not be including any RTU integration activities separately during relocation of items. The scope of work for relocation and commissioning at new location mentioned in Part-B, Appendix-G, Bill of Quantity is for once in the entire life cycle of the project. Following are the Owner scope of work at control centre which is being shifted during Relocation and Commissioning at New Location: …….. |
|  | Vol. II Part-A Section-1, Clause 1.17, Applicable Standards | Applicable Standards …… The available equivalent Indian Standard shall be complied. All latest guidelines issued by regulatory authorities such as MoP and CEA etc. Bidder shall offer established and tested products (hardware and software) under the project considering the criticality of the system. …… | Replace with Applicable Standards …… The available equivalent Indian Standard shall be complied. All latest guidelines issued by regulatory authorities such as MoP CEA, NCIIPC, MEITY etc. shall be complied by the bidders for the offered products (hardware and software) under the project. These should be established and tested product (hardware and software) considering criticality of the system. In this regard, bidder has to comply with order issued by MoP No. 25-11/6/2018-PG dated 2.7.2020 (with all amendments) and CEA Cyber Security in Power System Guidelines, 2021 (with all amendments) throughout the period of contract. …… |
|  | Vol. II Part-A Section-1, Clause 1.18, Table of Compliance |  | Inserted Table of Compliance Bidder shall use one copy of Volume I, "Conditions of Contract" and Volume II, "Technical Specifications" to indicate compliance status and Technical Status with those volumes. Within the right-hand margin, Bidder shall indicate compliance status and, technical Status to each paragraph and an index key for any explanation or comment. In addition, the Bidder shall annotate the Table of Contents of each of the above stated volumes to provide a high-level summary of compliance status and Technical Status. In both cases, the following symbols, and no others, shall be used Compliance Status: - C Bid complies with all requirements A Bid is not compliant with the requirements, but a functional alternative is proposed. X Bid takes exception to the requirements and no functional alternative is proposed. Technical Status: - S Bidder’s Standard product will be used to meet the Requirements D Bidder will take development work to meet the Requirements Only one symbol of Compliance Status and one symbol of Technical Status shall be assigned for a paragraph and shall indicate the worst-case level of compliance for that paragraph. This annotation may be handwritten. Bidder shall also underline, on the compliance copy, all requirements to which exceptions have been taken (X) or to which alternatives have been proposed (A). Each alternative shall be clearly and explicitly described. Such descriptions shall use the same paragraph numbering as the bid document sections addressed by the alternatives. All alternative descriptions shall be in one contiguous section of the Bidder's proposal, preferably in the same volume, and titled "Alternatives." A separate section titled "Exceptions" should be provided containing any discussion or explanation Bidder chooses to provide concerning exceptions taken. Alternatives which do not substantially comply with the intent of the bid documents will be considered exceptions. The Employer/Owner will assess the merits of each alternative and exception and will be the sole judge as to their acceptance. |
|  | Vol. II Part-A, Section – 2, Clause no. – 2.2.1.2 | (o) System hardening and Cyber security: | Replace with (o) System hardening and Cyber security: All modules of Cyber security shall be covered in details which as a minimum include GUI, log filtering & searching, reporting, configuration changes, addition/deletion of new rules/policies/devices etc. |
|  | Vol. II Part-A, Section – 2, Clause no. – 2.2.1.7 | Cyber security course …… - Vulnerability Assessment and Penetration Testing (VAPT) procedure | Cyber security course …… - Vulnerability Assessment and Penetration Testing (VAPT) procedure - Tools such as application whitelisting, VAPT etc. |
|  | Vol. II Part-A, Section – 2, Table 2.1 | Table:2.1 – Training Requirements | Replace with Revised Table:2.1 – Training Requirements is attached at Annexure – I. |
|  | Vol. II Part-A, Section – 3, Clause no. – 3.7.1, Quality Assurance & Testing | All materials and parts of the system/sub-system to be supplied under the project shall be of current manufacturer from a supplier regularly engaged in the production of such equipment and producing such components since last five years at-least. | Replace with All materials (hardware, software etc.) and parts of the system/sub-system to be supplied under the project shall be of reputed manufacturer from a supplier regularly engaged in the production of such equipment as per the OEM requirement specified under the technical specification. Also, supplier shall be producing such components since last five years at-least. |
|  | Vol. II Part-A, Section – 3, Clause no. – 3.7.7, Type Testing | (b) Type Tests shall be performed for all equipment types for which certification is not provided as required in (a) above, or if it is determined by the Employer that the certification provided is not acceptable. If any of the type tests are required to be carried out, the same shall be carried out by the Contractor. | Replace with (b) Type Tests shall be performed for all equipment types for which certification is not provided as required in (a) above, or if it is determined by the Employer that the certification provided is not acceptable. If any of the type tests are required to be carried out, the same shall be carried out by the Contractor at its own cost. |
|  | Vol. II Part-A, Section – 3, Clause – 3.7.7, Type Testing |  | Add new para (h)Type test (if it fail), the expenses for repeating the test and the expenditure of the Employer personnel for witnessing the Type Test shall be borne by the contractor. |
|  | Vol. II Part-A, Section – 3, Clause no. –3.8, Documentation | Documentation …… For this a web based “Document Management System” (DMS) software shall be supplied and installed at the owner’s facility by the contractor along with minimum 100 number of client access licenses. …… | Replace with Documentation …… For this a web based “Document Management System” (DMS) software shall be supplied and installed at the owner’s facility by the contractor along with minimum 50 number of client access licenses. …… |
|  | Vol. II Part-A, Section – 4, Maintenance & Support Services | The word “Employer/owner “wherever referred in Section-4 | Replaced by “owner” in Section -4 |
|  | Vol. II Part-A, Section-4 ,Clause 4.2, Maintenance support | For any addition (e.g. integration of new RTUs or new control center) during the maintenance period, bidder shall provide services for maintenance of those systems also without any additional cost. | Replace with For any addition (e.g. integration of new RTUs or new control center) during maintenance period, contractor shall provide all the services at control center end without any additional cost during entire period of the contract including extension (if any). |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.2 (f - ii) | …… OEM can be changed only after the receipt of letter from OEM regarding non-availability of non-supported item(s). …… | Replace with …… OEM can be changed only after the receipt of letter from OEM regarding non-availability of similar or higher configuration of non-supported item(s). …… |
|  | Vol. II Part-A, Section – 4, Clause no. –4.3.1, Hours of Cover | …… (The Software Engineer to be deployed during AMC shall have experience in Cyber Security also along with the SCADA/EMS system) Sl. No.; Control Centre; Number of manpower at control centre; Remarks. Main; Back up; Sub-LDC. 1; For NRLDC; 3; 2; -; Hardware, Software, Network (wherever applicable). 2; For each SLDC except BBMB and PSTCL; 2; 1; -. 3; BBMB; 2; -; -; Since BBMB and PSTCL are backup to each other, the 2 Engineers to be deployed at each control center shall be responsible for maintenance of Main and backup of both SLDCs, i.e., at BBMB, the proposed 2 Maintenance engineers shall look after Main SLDC of BBMB as well as backup of PSTCL and vice versa.. 4; PSTCL; 2; -; -. Man power requirement for RTUs AMC:. S.No; Name of SLDC; No of Manpower required during AMC; Remarks. 5; J&K SLDC; 2 (Two); 1 RTU Engineer for Main SLDC at Jammu& 1 Engineer for backup SLDC at Kashmir. 6; DTL; Nil. | Replace with …… Any of the engineer which is being deployed during AMC shall have experience in cyber security along with SCADA/EMS system Sl. No.; Control Centre; Number of manpower at control centre; Remarks. Main; Back up; Sub-LDC. 1; For NRLDC; 3 (1 H, 1 S, 1 N); 2 (1 H, 1 S); -; Hardware (H), Software (S), Network (N) (wherever applicable). 2; For each SLDC except BBMB and PSTCL; 2 (1 H, 1 S); 1 (1 S); -. 3; BBMB; 2 (1 H, 1 S); -; -; Since BBMB and PSTCL are backup to each other, the 2 Engineers to be deployed at each control center shall be responsible for maintenance of Main and backup of both SLDCs, i.e., at BBMB, the proposed 2 Maintenance engineers shall look after Main SLDC of BBMB as well as backup of PSTCL and vice versa.. 4; PSTCL; 2 (1 H, 1 S); -; -. Man power requirement for RTUs AMC:. S.No; Name of SLDC; No of Manpower required during AMC; Remarks. 5; J&K SLDC; 2 (Two); 1 RTU Engineer for Main SLDC at Jammu& 1 Engineer for backup SLDC at Kashmir. 6; DTL; Nil. |
|  | Vol. II Part-A Section-4, Clause 4.3.3 | Cyber security System monitoring and Monitoring and compliance manager for Critical Infrastructure Protection …… Biannually Cyber security Audit shall be conducted from two different CERT-In certified auditing firms. …… The Contractor shall submit signed reports for phase-1 and phase-2 audits (signed by Certified Audit agency) to the Owner. The auditors along with auditing firms need to be changed every 4 years so that different auditors audit the system throughout the maintenance phase. In case VAPT/cyber audit during AMC period suggest deployment of any new hardware/software solution to further improve cyber security posture, which was not envisaged under this supply/services contract then the same shall not be considered under contractor’s scope. …… | Replace with Each auditor along with auditing firm need to be mandatorily changed after 3 consecutive audits so that different auditors audit the system throughout the maintenance phase including extension if any. Experience of cyber security auditing firm– The cyber security auditing firm must have carried out audit of at least one number of critical infrastructure site identified by NCIIPC during last one year. SOP issued by NCIIPC for auditing of CIIs/Protected systems by Private/Government Organisation shall be followed by the contractor during cyber security audit along with its amendment/revision. The contractor shall ensure confidentiality and submit the NDA from cyber security auditor firms before auditing to the owner/employer. The format shall be provided by owner/employer. …… The Contractor shall submit signed reports for phase-1 and phase-2 audits (signed by Certified Audit agency) to the Owner. In case VAPT/cyber audit during AMC period suggest deployment of any new hardware/software solution to further improve cyber security posture, which was not envisaged under this supply/services contract then the same shall not be considered under contractor’s scope. …… |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.3.3.3 | All advisories given by CERT-In /CERT-GO/NCIIPC etc. shall be complied in the timely manner. | Replace with All advisories given by CERT-In/CERT-GO/NCIIPC/CEA etc. shall be complied in the timely manner during entire contract period including extension of contract, if any. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.3.4, Patch Management | ………. All the patches shall be downloaded through this single point of connection. …………….. The contractor shall upgrade the various applications delivered under the project through patch management and version upgrade to make it compliant with IEC standards as envisaged under the specification throughout the AMC period. …… | Replace with …….. All the patches shall be downloaded through this single point of connection. The patch management of SUBSLDC and remote consoles supplied under the project shall be done by the contractor through respective SLDCs/RLDC. ………. The contractor shall upgrade the various applications delivered under the project through patch management and upgrade to make it compliant with IEC standards as envisaged under the specification during entire contract period including extension of contract, if any. ………. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.3.9 | Any spares required for maintaining the Furniture in fully operational condition shall be provided by the contractor. | Replace with Any spares required for maintaining the Furniture in fully operational condition shall be provided by the contractor without any additional cost to owner. |
|  | Vol. II Part-A Section-4, Clause 4.4, Spares inventory | Spares inventory …… The spares shall be used as and when required and no separate charges are payable other than the maintenance charges. …… This shall be periodically verified by the Employer/Owner and unavailability of spares shall be treated as non-availability as per severity 2. …… | Replace with Spares inventory …… The spares shall be used as and when required andare to be replenished. No separate charges are payable other than the AMC charges. …… This shall be periodically verified by the Employer/Owner and unavailability of spares shall be treated as non-availability as per severity 2 if not replenished after a specified period. …… |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.6.1.1 | b. Outages of CFE system | Replace with b. Outages of both CFE system |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.6.1.2 (b) | Severity-2 …… b. Failure of one output ACDB, one input ACDB, failure of one UPS system, Failure of Battery System and failure of any other system of Auxiliary Power supply not covered under Severity-1 are included in this category. …… m. Non-compliance of Monitoring functions as specified in 4.2.3.3. …… | Replace with Severity-2 …… b. Failure of one output ACDB, one input ACDB, failure of one UPS system, Failure of Battery System and failure of any other system of Auxiliary Power supply not covered under Severity-1 are included in this category. The Failure of DG set when one of the UPS/battery bank is also failed simultaneously, shall be considered under Severity-1. …… m. Non-compliance of Monitoring functions as specified in 4.3.3.3. …… |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.9, Detailed Scope of work during Warranty and AMC Period | Detailed Scope of work during Warranty and AMC Period The detailed scope of services to be provided by Contractor during contract period. …… | Replace with Detailed Scope of work during Warranty and AMC Period The detailed scope of services to be provided by Contractor during contract period including extension of contract, if any. …… |
|  | Vol. II Part-A, Section – 4, Clause-4.12.1, Introduction | This project scope includes the maintenance of the RTU & associated items (RTU & Associated Cards, LDMS, MFT, CMR, HDR, OLTC, Weather Sensor etc. and other associated cabling) supplied under this project at different locations across the Northern Region. These RTUs shall provide data to the respective NRLDC/SLDC/Sub SLDC. | Replace with This project scope includes the maintenance of the RTU & associated items (RTU & Associated Cards, LDMS, MFT, CMR, HDR, OLTC, Weather Sensor etc. and other associated cabling) supplied under this project at different locations across the Northern Region. The above scope also covers maintenance of integrated new bay extension (MFT, CMR, HDR, OLTC etc. and other associated cabling) in the supplied RTU under this project during entire project life cycle. These RTUs shall provide data to the respective NRLDC/SLDC/Sub SLDC. |
|  | Vol. II Part-A, Appendix-A, Existing RTU Details | List of RTU details | New Table Inserted - UPSLDC List of RTU details of UP SLDC is attached at Annexure-II |
|  | Vol. II Part-A, Appendix-H, Details of Control Centers–Location | Details of New Control Centres under this Project S.No.; SLDC; Main; Backup. 5; HVPNL; Panipat; Shimla. | Replace with Details of New Control Centres under this Project S.No.; SLDC; Main; Backup. 5; HVPNL; Panipat; HQ, Shakti Bhawan, Panchkula. |
|  | Vol. II Part-A, Appendix-J, List of equipment for buy-back | List of equipment for buy-back | New Table Inserted List of equipment for buy-back (HVPNL) List of equipment for buy-back (PSTCL) List of equipment for buy-back (HVPNL and PSTCL) is attached at Annexure-III. |
|  | Vol. II Part-B, Section – 1, Clause – 1.1.1.7 | ……… The SCADA system shall also maintain the RTU communication statistics for a period of one month on hourly basis for all RTUs. The details to be maintained in statistics are ‘Number of poll requests sent by the SCADA system’, ‘Number of responses received from the RTU’, ‘Number of no reply errors (Communication channel failure, RTU device failure)’ and ‘Number of faulty packets’ received. The RTU communication statistics shall also be transferred to Historian System. The SCADA system shall also maintain the latency of data received from RTU to control center. Real time RTU status and RTU’s availability report must be in text or CSV or Excel file in SCADA system. | Replace with …….. The SCADA system shall also maintain the RTU communication statistics for a period of one month, on daily basis, on hourly basis and any user defined periodicity for all RTUs. The details to be maintained in statistics are ‘Number of poll requests sent by the SCADA system’, ‘Number of responses received from the RTU’, ‘Number of no reply errors (Communication channel failure, RTU device failure)’ and ‘Number of faulty packets’ received. The RTU communication statistics shall also be transferred to Historian System. The status of primary and secondary channel availability and data operation on it must also be stored in the historian. The SCADA system shall also maintain the latency of data received from RTU to control center. Real time RTU status and RTU’s availability report shall also be available/exportable in text or CSV or Excel file from system as and when required/periodically. |
|  | Vol. II Part-B, Section – 1, Clause – 1.2.1 | Data Exchange with Control Centres …… System shall support Integration of Main and Back up Control Centers with RLDC Control Centers on secure mode ICCP protocol. The communications links for data exchange among control centres shall allow configuration of each channel transmission rate up to 2 Mbps or more. Communication links shall be configured as Main (or Primary) & Backup (or Secondary) links. …… | Replace with Data Exchange with Control Centres …… System shall support Integration of Main and Back up Control Centers with other Control Centers on secure mode ICCP protocol as well as ICCP protocol. The required communications links shall be provided by the Owner for data exchange among Control Centers. The communications links for data exchange among control centres shall allow configuration of each channel. Communication links shall be configured as Main (or Primary) & Backup (or Secondary) links. …… |
|  | Vol. II Part-B, Section – 1, Clause – 1.2.4 | Data Exchange with Market Applications and Open Access …… All data mentioned in the above bulleted points would be available in one or more of the following formats shall be finalized during detail engineering– Dedicated API, CSV format, TXT format, XML format, SOAP/REST and OPC etc. …… | Replace with Data Exchange with Market Applications and Open Access …… All data mentioned in the above bulleted points would be available in one or more of the following formats shall be finalized during detail engineering – Dedicated API, SOAP/REST and OPC etc. …… |
|  | Vol. II Part-B, Section – 1, Clause no. –1.1.1, Data Acquisition | ……. Typical architecture of RTU data reporting to Main and Back up Control Centre is given in Appendix-N. | Replace with ……. Typical architecture of RTU data reporting to Main and Back up Control Centre is given in Part-A, Appendix-F. |
|  | Vol. II Part-B, Section – 1, Clause – 1.3.1 (a) | a) Reasonability Limit Check …… An alarm shall be generated the first time a reasonability limit violation is detected. The last valid value of the variable shall be maintained in the database and marked with a quality code indicating the ‘reasonability limit violation’. …… | Replace with a) Reasonability Limit Check …… An alarm shall be generated the first time a reasonability limit violation is detected and list of all such points shall be available to the user in real time. The last valid value of the variable shall be maintained in the database and marked with a quality code indicating the ‘reasonability limit violation’. …… |
|  | Vol. II Part-B, Section – 1, Clause no. –1.3.1, (d) Sign conventions | Equipment; Flow Convention. Loads; Real power into load: Positive Reactive power into equipment: Positive. | Equipment; Flow Convention. Loads; Real power into load: Positive Reactive power into load: Positive. Replace with |
|  | Vol. II Part-B, Section – 1, Clause no. –1.3.1, Analog Data Processing (f) | Freeze data/Stale Data Check …… In case of freeze/stale data, SCADA quality (telemetry failure) should be assigned on the point/field and accordingly data should be switched between multiple sources as per the alternate data configuration methodology. Alternate Data Source should be activated. Separate display should be provided for summary of Stale Data. | Replace with Freeze data/Stale Data Check ……..In case of freeze/stale data, freeze/stale data quality flag should be assigned on the point/field and accordingly data should be switched between multiple sources as per the alternate data configuration methodology. Alternate Data Source should be activated. Separate display should be provided for summary of Stale Data. |
|  | Vol. II Part-B, Section – 1, Clause – 1.3.3.5 | Max. and Min. Value Calculations …… These calculations shall use the real-time clock and initially shall be performed for 15-minute intervals and it should be available to operator for last 244 hours. The ability to calculate and display the Maxima and Minima values of user selected telemetered and calculated analog points shall be provided. …… | Replace with Max. and Min. Value Calculations …… These calculations shall use the real- time clock and initially shall be performed for 15-minute intervals and it should be available to operators for last 24 hours. The ability to calculate and display the Maxima and Minima values of user selected telemetered and calculated analog points shall be provided. …… |
|  | Vol. II Part-B, Section – 1, Clause – 1.3.3.5 | Average Value Calculations …… Average of value over duration of interest = Sum of values/No. of samples The duration of interest shall be configurable on a system wide basis from 5 minutes to 24 hrs in steps of 5 minutes (total 12 options to be provided for user’s duration of interest). The results shall bear the time-tag of the time at the start of the interval. These calculations shall use the real-time clock. Initial setting for capacity and performance shall be 15 minute and it should be available to operator for last 24 hours. …… | Replace with …… Average of value over duration of interest = Sum of values of samples/No. of samples The duration of interest shall be configurable on a system wide basis from 5 to 60 minutes in steps of 5 minutes (total 12 options to be provided for user’s duration of interest). The results shall bear the time-tag of the time at the start of the interval. These calculations shall use the real-time clock. Initial setting for capacity and performance shall be 15 minutes and it should be available to operator for last 24 hours. …… |
|  | Vol. II Part-B, Section – 1, Clause – 1.6 | Supervisory Control …… Control command can also be given from other control center through ICCP. The devices that can be controlled from any particular console shall be determined by the partitions assigned to that console. It shall be possible to assign a number of controllable devices in one group and then control all the devices by executing a single control command on the group. …… | Replace with Supervisory Control …… Control command can also be given from other control center through ICCP. The devices that can be controlled from any console shall be determined by the controlled authority assigned to that console and user. It shall be possible to assign a number of controllable devices in one group and then control all the devices by executing a single control command on the group. …… |
|  | Vol. II Part-B, Section – 1, Clause – 1.8 | Historian …… The historian shall also store data as mentioned in different clauses of the specification in secure manner. All the functions described in the technical specification for historian (including visualization) shall be fulfilled by Historian COTS (Commercial of the self) product only. Historian shall be able to provide dedicated dashboard and different types of graphs as PART-B, Appendix-N apart mentioned herein under. …… | Replace with …… The historian shall also store data as mentioned in different clauses of the specification in secure manner. Functionalities mentioned under this section (including visualization) shall be meet by the Historian itself and from SCADA wherever specifically mentioned. Proposed solution shall be COTS product and as per COTS definition specified under the technical specification and BoQ. Historian shall be able to provide dedicated dashboard and different types of graphs as PART-B, Appendix-N apart mentioned herein under. …… |
|  | Vol. II Part-B, Section – 1, Clause – 1.8.2 | Configuration of the Historian System at Main and Backup Control Centres ….. Similarly, Historian at back up control centre will receive data from SCADA at back up control centre as primary source and data from main control centre can be synced as per user selectable date and time range on requirement. Typical architecture of historian data reporting to Main and Backup control center is given in Part-A Appendix-J. ……… Software utilities shall be provided in the Historian System to back-up the Historian data to an auxiliary memory (e.g. SAN System) available on network. …….. | Replace with Configuration of the Historian System at Main and Backup Control Centres ….. Similarly, Historian at back up control centre will receive data from SCADA at back up control centre as primary source and data from main control centre can be synced as per user selectable date and time range on requirement. Typical architecture of historian data reporting to Main and Backup control center is given in Part-A Appendix-F. ……. Software utilities shall be provided in the Historian System to back-up the Historian data in a redundant SAN and backup appliance available on network. …… |
|  | Vol. II Part-B, Section – 1, Clause – 1.8.3 | Features required with the Historian System …… c) Real-time data interfaces The Historian System shall provide real-time, fault-tolerant, high-speed links from any industrial automated real-time data sources through an industry standard interfaces such as multiple OPC industry standards, OPC DA, OPC UA and OPC HDA, connector. Also, it shall have interfaces compatible with DAS (1.0a and 2.0) compliant servers, SQL, ODBC, OLEDB, Modbus, ASCII, and text. …… | Replace with Features required with the Historian System …… c) Real-time data interfaces …… The Historian System shall provide real-time, fault-tolerant, high-speed links from any industrial automated real-time data sources through an industry standard interfaces such as multiple OPC industry standards, OPC DA, OPC UA and OPC HDA, connector. Also, it shall have interfaces compatible with DAS (1.0a and 2.0) compliant servers, SOAP, REST, SQL, ODBC, OLEDB, Modbus, ASCII, and text. …… |
|  | Vol. II Part-B, Section – 1, Clause – 1.8.3 | Features required with the Historian System …… d) Calculated values …… The Historian System shall also have data summary function for defining calculations such as totals, averages, and other aggregates from real-time data inputs. …… The Historian System must be able to save calculated values as separate data points. …… | Replace with Features required with the Historian System …… d) Calculated values …… The Historian System shall also have data summary function for defining calculations such as totals, averages, and other aggregates from real-time data and historical data input points available in historian on the fly. Summarized functions/calculation created can evaluate the output on the existing historical data points also. …… The Historian System must be able to save calculated values as separate data fields/points within historian directly (independent with SCADA database). …… |
|  | Vol. II Part-B, Section – 1, Clause no. –1.10(b), Scope of work | The devices required for integration of RTUs shall be in the scope of the contractor. | The communication interfacing devices required for integration of RTUs at control centre end for RTUs mentioned in BoQ of AMC period shall be in the scope of the contractor. |
|  | Vol. II Part-B, Section – 2, Clause – 2.2.5.4 | High Voltage Direct Current Model …… e) Ensure that the maximum connectable shunts are not exceeded. …… | Replace with High Voltage Direct Current Model …… e) Ensure that the maximum connectable shunts are not exceeded. f) Ensure that the minimum numbers of AC filters are connected …… |
|  | Vol. II Part-B, Section – 2, Clause – 2.2.6.2 | Control Centre Power System Model ……. The Control Centre Model shall include the entire network for the Control Centre operating area as agreed during engineering. ….. | Replace with Control Centre Power System Model ……. The Control Centre Model shall include the entire network (generally 110kV and above, HVDC, etc.) for the Control Centre operating area as agreed during engineering. ……. |
|  | Vol. II Part-B, Section – 2, Clause – 2.2.13.1 | General Characteristics …… l) The user shall be able to disable generator reactive power limiting on user-selectable sets of units, e.g., on a Control Centre basis. …… | Replace with General Characteristics …… l) The user shall be able to disable generator reactive power limiting on user-selectable sets of units, e.g., on a Control Centre basis. m) Phase Shifters control shall be available, and user can enable/disable the control as per requirement. ….. |
|  | Vol. II Part-B Section-2 Clause 2.2.13.6, Optimization Features | 2.2.13.6 Optimization Features | Replace with 2.2.13.6 Optimization Features – Security Enhancement |
|  | Vol. II Part-B, Section – 2, Clause – 2.2.15 | Transmission Line/ Corridor Capability Monitor (TCM) …… • TCM shall be limited to minimum of the following constraints: ……. (c) Angular pair limits ……….. | Replace with Transmission Line/ Corridor Capability Monitor (TCM) …… • TCM shall be limited to minimum of the following constraints: ……. (c) Angular pair limits (d) Peak-time Scenario (Defined by system operator) ……... |
|  | Vol. II Part-B, Section – 2, Clause – 2.2.16 | Creation of a Dashboard for performance monitoring of EMS applications as per the sample attached at figure B21 of Appendix - B. | Creation of a Dashboard for performance monitoring of EMS applications as per the sample attached at figure Appendix - B. |
|  | Vol. II Part-B, Section – 2, Clause – 2.3 | Dispatcher Training Simulator …… g) Instructor control features that include the ability to set up, control, participate in, and review the results of a training session. …………. | Replace with Dispatcher Training Simulator …… g) Trainee or instructor consoles. The DTS shall support single or multiple instructors. It shall include Instructor control features that include the ability to set up, control, participate in, and review the results of a training session. ………... |
|  | Vol. II Part-B, Section – 2, Clause – 2.4.3 | Real-Time Dispatch The RLDC/SLDCs shall calculate the generation requirements for the participating ISGS based on ACE/PACE. AGC for real-time dispatch shall be performed at an adjustable periodicity. ………..….. | Replace with Real-Time Dispatch The RLDC/SLDCs shall calculate the generation requirements for the participating ISGS based on ACE/PACE. AGC for real-time dispatch shall be performed at an adjustable periodicity. The AGC system hardware and inputs from SCADA (viz., frequency and tie-line flows) shall be designed with redundancy in such a way that database development of SCADA and EMS Network models (transmission lines, buses, generators, etc.,) shall not hamper the real-time dispatch activity of AGC for reboots/restarts/builds etc. ………… |
|  | Vol. II Part-B, Section – 2, Clause – 2.5 | Dynamic Security Assessment (DSA) ….. The above-mentioned tools i.e., VSA, TSA and SSA shall be deployed as an on-line dynamic security assessment (DSA) tool with the SCADA/EMS System. ……… | Replace with Dynamic Security Assessment (DSA) ….. The above-mentioned tools i.e., VSA, TSA and SSA shall be deployed as an on-line dynamic security assessment (DSA) tool with the SCADA/EMS System and offline dynamic security assessment (DSA) with standard static and dynamic network models (as indicated in Table 2.1) ……… |
|  | Vol. II Part-B, Section – 2, Clause – 2.5.1 | Special protection scheme (SPS) models (refer Appendix – B(B18)) | Replace with Special protection scheme (SPS) models (refer Appendix – B(B17)) |
|  | Vol. II Part-B, Section – 3, Clause no. –3.2.1, Identity Manager | A dedicated Identity and access management application shall be deployed (as per BoQ) to manage and to help achieve seamless access to all applications for authenticated users. ……….. | Replace with A dedicated Identity and access management application shall be deployed (as per BoQ) to manage and to help achieve seamless access to all applications for authenticated users. The system and users of SUBSLDC and remote consoles supplied under this project shall also be authenticated/authorised through identity management application of respective SLDCs/RLDC. The identity management application shall integrate the cyber security applications, cyber security devices, networking devices and other third party application supplied under this project. ……… |
|  | Vol. II Part-B, Section – 3, Clause no. – 3.7 Display Interactions |  | Add new para - The content of user display can be seen any other user but can be deleted by only that particular user having access rights. |
|  | Vol. II Part-B, Section – 3, Clause no. – 3.8.3, Trending (SCADA Application) | Points to be trended: All SCADA points, System parameters such as communication and application parameters shall be made available for trending, by default. | Replace with Points to be trended: All SCADA points shall be made available for trending by default. However, any system parameters such as communication or application statistics whose trend is required by user, need to be integrated as SCADA data and shall also be available for trending. |
|  | Vol. II Part-B, Section – 3, Clause no. – 3.9, Alarms | - Minimum 7 days ALARMS shall be available in real-time. | Deleted |
|  | Vol. II Part-B, Section – 3, Clause no. – 3.10, Hardcopy Printout | The printout of the display, reports, etc. shall also be made available in PDF-format along with corresponding licensed software. | Replace with The printout of the display, reports, etc. shall also be made available in PDF-format along with corresponding licensed software. In case of printing of large geographical / map / SLDs display into a pdf format, the complete ( not limited to the visible portion) display (Map) shall be converted into pdf file format with high resolution so that the values/texts plotted in Maps in pdf format shall be clearly visible and readable after zooming the pdf file. If any additional software is required, the same shall be provided by contractor. |
|  | Vol. II Part-B, Section – 3, Clause no. – 3.11 | Sample Display building approved guidelines are attached at Annexure-B, the same shall be followed. | Replace with Sample Display building approved guidelines are attached at Annexure-K, the same shall be followed. |
|  | Vol. II Part-B, Section – 3, Clause no. – 3.14, SCADA/EMS System Display | SCADA/EMS System Display ….This tool shall have advanced features such as 3D visualizations, geo-spatial maps, contouring, and other objects to enhance operations and significantly enhance situational awareness in the control room. There shall not be any limitation in number of user-based desktops. A search facility for finding desired display from the display index/directory shall be provided…… | Replace with SCADA/EMS System Display ….This tool shall have advanced features such as 3D visualizations, geo-spatial maps, contouring, and other objects to enhance operations and significantly enhance situational awareness in the control room. All workstations shall be provided with the SCADA/EMS graphical user interface including the visualisation tools for 3D displays, geo-spatial maps, contouring etc. There shall not be any limitation in opening, editing of database and display from any of the workstations supplied under the contract. User shall be able to edit from any workstation after login with proper credential. A search facility for finding desired display from the display index/directory shall be provided…… |
|  | Vol. II Part-B, Section – 3, Clause no. – 3.14.9 (j) | (j) In the Operations Monitor Display, the following quantities as a minimum need to be displayed with EMS database and SCADA measurements. For SCADA measurements displayed with EMS database and SCADA measurements. For SCADA measurements calculations shall be user-definable for Actuals MW/Net interchange/Tie-Line Exchanges etc. | Replace with (j) In the Operations Monitor Display, the following quantities as a minimum need to be displayed with EMS database and SCADA measurements. SCADA measurements calculations shall be user-definable for Actuals MW/Net interchange/Tie-Line Exchanges etc. |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.1 | Audit by Operating System OEM for system configuration after Installation & Commissioning shall be tied by the Contractor for the proposed system. | Deleted |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.1, General requirements | General requirements ….. Bidder has to provide latest version of all SCADA/EMS Application software supplied under the project before the start of Site Acceptance Test (SAT) without any cost implication. | Replace with General requirements ….. Bidder has to provide latest version of all SCADA/EMS Application software supplied under the project before the start of Site Acceptance Test (SAT) without any cost implication. Bidder has to provide the latest version of all third party application software supplied under the project before the start of Factory Acceptance Test (FAT) without any cost implication. The contractor shall provide details of all the API’s including its source code supplied/used under the contract to the owner without any additional cost. |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.1.2, Operating System | The system security shall also be maintained in line with cyber security guidelines/ recommendations issued by statutory authorities from time-to-time throughout the life cycle of the project. | Replace with The system security shall also be maintained in line with cyber security guidelines/recommendations issued by various statutory authorities like CEA, CERT-In, NCIIPC, MeITY etc. from time-to-time throughout the life cycle of the project including extension if any. The operating system and data files shall be placed in different disk partition. |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.2.3, Commercial Off-The-Shelf (COTS) product | Commercial Off-The-Shelf (COTS) product means bidder has to quote product which is independently commercially available in the market. For all such products bidder has to provide at least three references in Govt/Public Listed companies at the time of bid submission and same shall have been sold as an independent product and solution shall be in successful operation for at least three years. For that Bidder has to submit copy of PO/LOA and installation/completion certificate for the relevant reference. | Commercial Off-The-Shelf (COTS) product means bidder has to quote product which is independently commercially available in the market. For all such products bidder has to provide at least three references in Govt/Public Listed companies at the time of bid submission and same shall have been sold as an independent product and solution shall be in successful operation for at least three years at the time of bid submission. For that Bidder has to submit copy of PO/LOA and installation/completion/operational certificate issued by Customer for the relevant reference. |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.5, Network Management System (NMS) | c. Data Links | Replace with c. Data Links (bandwidth utilisation of current and last 24 hours) |
|  | Vol. II Part-B, Section – 4, Clause no. –4.5, Network Management System (NMS) | ……. a. Utilization (CPU and/or channel time being used as applicable) for a. Servers, Workstations, Storage Devices (SAN, NAS, HDD etc.) b. Router, Switches c. Data Links b) Memory utilization, Auxiliary memory I/O utilization, of a. Servers and Other Machines b. Mass Storage Devices c) Temperature monitoring of servers, network and storage devices etc. | Replace with ……. a. Utilization (CPU and/or channel time being used as applicable) for a. All Active devices (Servers, Workstations, etc), Storage Devices (SAN, NAS, HDD etc.) b. Router, Switches, Firewall c. Data Links b) Memory utilization, Auxiliary memory I/O utilization, of a. All Active Devices (Servers, Workstations, etc) b. Mass Storage Devices c) Temperature monitoring of all active devices (servers, network and storage devices etc.) |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.6.3.2, Database Integration (on lining) | …. Inconsistencies shall be annunciated to the user. The database changes made in Main Control Center shall be reflected immediately in Backup Control Center with minimal user intervention and without requiring any downtime. The database of Main and Backup Control Centers should be checked at regular intervals for any mismatch and necessary up-dation shall be done for the same. Databases for all Application like Web, Replica server/Historian should be updated automatically. | Replace with …Inconsistencies shall be annunciated to the user. Further, appropriate message/alarm shall be generated after the on-lining of each relevant applications/database. The database changes made in Main Control Center shall be reflected immediately in Backup Control Center with minimal user intervention and without requiring any downtime. At regular intervals (Daily) the database of Main and Backup Control Centers be checked for any differences in entries, linkages, calculations and database elements and necessary updation shall be done for the same. It shall be possible to do Database Integration by following method: • Real Time - No Failover of Online Server required. • Off Line- Failover of Online Server required. Databases for all Application like Web, Replica server/Historian should be updated automatically. |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.6.4, Tracking Database Changes | …..User shall be able to compare two cases of database at any point of time. | Replace with ……User shall be able to compare two cases of database at any point of time to generate any reports from audit trail database based on different parameters (such as date and time of a database change, identity of the user who modified a database and a text string contained in the database etc.) using SQL query. |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.7, Display Generation and Management | ….. Segments shall be defined at an arbitrary scale factor selected by the user. For Display Generation, the contractor shall following display building guidelines, as mentioned in Appendix K. | Replace with ……Segments shall be defined at an arbitrary scale factor selected by the user. The display editor/generator shall have option to compile all displays corresponding to a change in a symbol or element in the library. For Display Generation, the contractor shall following display building guidelines, as mentioned in Appendix K. |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.8.6, Other Utility Services | The MS office software and Adobe-PDF (With Valid License Version) software shall be provided in each of the workstations, laptops and remote consoles etc. by the contractor. Contractor has to supply MS Office and PDF software (With Valid License Version) for all the supplied endpoints (workstations, laptops, CPU, remote consoles etc). | Replace with The MS office software and Adobe PDF reader (With Valid License Version) software shall be provided in each of the workstations, laptops and remote consoles etc. by the contractor. Contractor has to supply MS Office and Adobe PDF reader software (With Valid License Version) for all the supplied endpoints (workstations, laptops, CPU, remote consoles etc). |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.12 | 4.12 Scope of Maintenance of RTUs and Associated Items ………… | Replace with 4.12 Scope of Maintenance of new RTUs and Associated Items……….. |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.12.4, (c ) | Further, integration new Bays shall not be treated as new RTU integration during AMC period, and any such bay extension during AMC shall be in the scope of the contractor without any commercial implication to the Owner. | Replace with Further, integration of new Bays shall not be treated as new RTU integration during AMC period, and any such bay integration at Control Centre end during AMC shall be in the scope of the contractor. The cost of new bay integration shall be inclusive in the Annual Maintenance charges. |
|  | Vol. II Part-B, Section – 5, Clause no. – 5.3, Hardware Configuration | Peripheral device includes Workstation consoles, WAN router, LAN, printer, Time & Frequency system, storage device, External Cartridge, Magnetic tape drive, VPS, Firewalls etc. | Replace with Peripheral device includes Workstation consoles, WAN router, LAN, printer, Time & Frequency system, storage device, VPS, Firewalls etc. and other devices/solution supplied under the project. |
|  | Vol. II Part-B, Section – 5, Clause no. – 5.4, Servers (Rack mountable servers/ Blade servers) | Servers (Rack mountable servers/ Blade servers) The Servers shall have provision for expansion of the processor, auxiliary memory and Main memory (RAM) as mentioned in technical specification. ….. Servers supplied shall be compatible to connect with the external storage and other network components identified in the BOQ, necessary additional hardware (if any) required for connectivity shall be part of servers. Blade Servers: Servers shall be accommodated in (8/16) slot chassis capable of mounting in a rack and a rack mountable TFT monitor, keyboard and mouse using an IP based KVM switch to access all servers and peripherals in the panel. All servers shall be hot swappable, have backplane redundancy, dual redundant power supplies and be capable to operate on single power supply module. And there shall not be any interruptions in the operation of servers when there is a failover between the two AC Power Supply of the server. Servers supplied shall be compatible to connect with the external storage and other network components identified in the BOQ, necessary additional hardware (if any) required for connectivity shall be part of servers. Some of the application shall be installed on physical server whereas many shall be on virtual servers as per the proposed architecture and bill of quantity.…. | Replace with Servers (Rack mountable servers) The Servers shall have provision for Upgrade of the processor, auxiliary memory and Main memory (RAM) as mentioned in technical specification. ….. Servers supplied shall be compatible to connect with the external storage and other network components identified in the BOQ, necessary additional hardware (if any) required for connectivity shall be part of servers. Some of the application shall be installed on physical server whereas many shall be on virtual servers as per the proposed architecture and bill of quantity.…. |
|  | Vol. II Part-B, Section-5, Clause No. – 5.8.6 | Integrated Remote Consoles: The integrated remote console shall be provided wherein the workstation is part of monitor structure/frame. Note: For 55” wall mounter video wall, CPU shall be accommodated between wall and screen. All the supplied system shall have supplied with stands (Wall/Floor) as per the Employer/Owner requirements during DRS approval. | Replace with 5.8.6.1 Remote console – The remote consoles are workstations of different type which are to installed outside the control room. These will be connected either on LAN /extended LAN or through a wide band communication link through a router. The remote console shall primarily be used as interface for the SCADA user application and Data historian application. The remote console shall have access to all the displays, trends and reports available in the local Operator workstations for SCADA and Data historian. The remote consoles are of different types as mentioned in Appendix-H. - Remote Console with Dual monitor - All-in-One workstations with CPU - Remote Consoles with 55" Monitor with CPU Integrated Remote Consoles (All in one): The integrated remote console shall be provided wherein the workstation is part of monitor structure/frame. 5.8.6.2 Video Wall – In addition to remote console, there will be video wall consoles as per Appendix-G with Wall/Floor mounted monitors. For 55” wall mount video wall, CPU shall be accommodated between wall and screen. All the supplied system shall be supplied with stands (Wall/Floor) as per the Employer/Owner requirements during DRS approval. The video walls are of different types as mentioned in Appendix-H. - 55” video wall with controller - 55” video wall (Wall/Floor) The video wall shall primarily be used as interface for the SCADA user application and Data historian application. The video wall shall have access to all the displays, trends and reports available to the local operator workstations for SCADA and Data historian, and shall also be available for the video wall users. |
|  | Vol. II Part-B Section-5 Clause 5.13, Video Projection System (VPS) | The contractor shall provide a video projection system based on modular DLP (Digital Light Processing) based high resolution LED/Laser based rear projection technology as per BoQ. | Replace with The contractor shall provide a video projection system based on modular DLP (Digital Light Processing) based high resolution Laser based rear projection technology as per BoQ. |
|  | Vol. II Part-B Section-5 Clause 5.13, Video Projection System (VPS) | The Visual Display Unit / Rear Projection Modules shall have in-built redundancy in LEDs/Laser and ensures redundancy at the light source colour. | Replace with The Video Projection Modules shall have in-built redundancy in Laser and ensures redundancy at the light source. |
|  | Vol. II Part-B Section-5 Clause 5.13.1, Testing methodology for VPS | From each batch/total BoQ quantity of VPS modules for each control center offered by the Contractor for Factory acceptance testing (FAT), the Employer shall select random configuration as sample(s) to be tested for each type (LED/LASER) & Model of equipment for acceptance. | Replace with From each batch/total BoQ quantity of VPS modules for each control center offered by the Contractor for Factory acceptance testing (FAT), the Employer shall select random configuration as sample(s) to be tested for each Model of equipment for acceptance. |
|  | Vol. II Part-B Section-5 Clause 5.13.4, VPS diagnostics and maintenance (b) | LED age | Replace with Light source age |
|  | Vol. II Part-B, Section – 6, Clause no. –6.2, Network Attached Storage (NAS) | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 10; Heat Load. | Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 10; Heat Load. 11.; Interface Ports; 4*10G Base T ports. |
|  | Vol. II Part-B, Section – 6, Clause no. – 6.6.2, Restart | Restart … Restart as described above shall be completed within 30 seconds except for EMS server which can be 120 seconds. | Replace with Restart … Restart as described above shall be completed within 30 seconds except for EMS server which can be 120 seconds. Also, the cold restart of the devices (Firewall, Router, Switch etc.) shall be completed within 5 minutes. |
|  | Vol. II Part-B, Section – 7, Clause no. – 7.2, Test Plan and Test Procedures | ……The test plans and test procedures shall be modular to allow individual test segments to be repeated as necessary. They shall be subject to Employer/Owner approval (see Part-A Section-3). | Replace with …….The test plans and test procedures shall be modular to allow individual test segments to be repeated as necessary. They shall be subject to Employer/Owner approval (see Part-A Section-3). For SCADA/EMS system guidance from Indian standard IS 15953:2011 “SCADA System for Power System Applications” should be included for FAT & SAT procedure.“ |
|  | Vol. II Part-B, Section – 7, Clause no. – 7.7.1, Functional FAT | Verification of all SCADA, EMS, CFE, Historian, NMS, Cyber Security functions and features as specified in technical specifications and as per approved FAT procedure. | Replace with Verification of all SCADA/EMS applications, Historian, NMS, Cyber Security functions etc and all features as specified in BoQ and technical specifications and as per approved FAT procedure. |
|  | Vol. II Part-B, Section – 7, Clause no.– 7.7.2, Integrated FAT | …..(c )At least 2 RTUs for each control center mentioned above At least two RTUs for each protocol shall be connected with control centre and the remaining RTU shall be simulated in the factory test environment. ….. | Replace with …… (c )At least 2 RTUs for each control center mentioned above (d) ICCP integration with these control centres and data exchange as per design and approval. At least two RTUs for each protocol shall be connected with control centre and the remaining RTU shall be simulated in the factory test environment. ….. |
|  | Vol. II Part-B, Section – 8, Clause no. – 8.2.2 | All user requests and application data requirement for Web server/application/ services hall be served from Data Replica server. | Replace with All user requests and application data requirement for Web server/application/ services shall be served from Data Replica server. |
|  | Vol. II Part-B, Section – 9, Clause no. –9.1, Cyber Security System | - All the Hardware, Operating Systems (OS) and application software shall be hardened based on industry standards such as CIS benchmarks. …………… - Whitelisting policy shall be deployed for all port configuration, network routing, data flow, access etc. and all these details shall be documented. ………………. (m) Centralized log collection shall be implemented using SIEM, which consolidates all system, ssh, network, and go-logs into one central repository. This log collection system will be implemented with SIEM. ………… | Replace with - All the Hardware, Operating Systems (OS) and application software shall be hardened. List of ports and services enabled in each hardware device must be shared after SAVT. This list must be updated periodically if any new ports/services are allowed or blocked after prior approval of Owner. ………. (i) Whitelisting policy shall be deployed for all port configuration, network routing, data flow, access etc. and all these details shall be documented and any changes shall be recorded and informed to owner during entire period of contract. ………. m) Centralized log collection shall be implemented using SIEM, which consolidates the logs from all the devices. …………….. (t) For assessment of policies implementation in firewall/routers/switches necessary audit shall be conducted after site acceptance test (SAT) only. (u) Policy implementation audit must be conducted periodically (quarterly) by the contractor and report to be submitted to owner. (v) All the external traffic (RTU, ICCP, IT, OT etc.) destined to control centre shall be routed through firewall only. (w) Automatic report/log generation for every device shall be provided. (x) All the proposed cyber security products OEMs shall have their own threat intelligence platform. |
|  | Vol. II Part-B, Section – 9, Clause no. – 9.1.1, Cyber Security Policy | - Auditing by CERT-In certified third-party during FAT,SAT and bi-annually during AMC period. Minimum three no. of auditing agency need to be engaged for performing six-monthly cyber security auditing. Biannually consecutive cyber security audit shall be conducted from two different CERT-In certified auditing firms. Contractor shall implement the recommendation/remedial actions suggested by the auditor after audit for any upgrade (Patches) in existing system. | Replaced with - Auditing by CERT-In certified third-party during FAT,SAT and bi-annually during AMC period. Each auditor along with auditing firm need to be mandatorily changed after 3 consecutive audits so that different auditors audit the system throughout the maintenance phase including extension if any. Contractor shall implement the recommendation/remedial actions suggested by the auditor after audit for any upgrade (Patches) in existing system. |
|  | Vol. II Part-B, Section – 9, Clause no. –9.1.1, Cyber Security Policy | ……. - Mechanism to detect unauthorized/unusual activity and attempts to compromise system security based on logs of SIEM, NMS and Application logs. - Unused ports (physical and logical) pf all devices such as on switches, routers, firewalls, consoles, servers, NIPS shall be disabled. …….. | Replace with ……….. - Mechanism to detect unauthorized/unusual activity and attempts to compromise system security based on logs of SIEM, NMS and Application logs. The contractor to propose and document what constitutes normal activity/traffic periodically. - Unused ports (physical and logical) of all devices such as on switches, routers, firewalls, consoles, servers, HIPS etc. shall be disabled. ………… |
|  | Volume II, Part B, Section-9, Clause No. -9.1.3.1, Firewall | # The proposed Firewall / Firewall Operating System shall be tested and certified for EAL3+/ NDPP (Network Device Protection Profile)/NDcPP (Network Device Collaborative Protection Profile) or above under Common Criteria Program for security related functions or under Indian Common Criteria Certification Scheme (IC3S) by STQC, DEIT, Govt. of India. | Replace with The proposed Firewall / Firewall Operating System shall be tested and certified for EAL4+/ NDPP (Network Device Protection Profile)/NDcPP (Network Device Collaborative Protection Profile) or above under Common Criteria Program for security related functions or under Indian Common Criteria Certification Scheme (IC3S) by STQC, DEIT, Govt. of India. |
|  | Vol. II Part-B, Section – 9, Clause no. – 9.1.6, Application Whitelisting Tool | A tool shall be provided by the contractor for ensuring that only required software are running on the system being procured. | Replace with A tool (separate or part of NAC or End Point Security Solution) shall be provided by the contractor for ensuring that only required software are running on the system being procured. |
|  | Vol. II Part-B, Section – 9, Clause no. –9.1.6, Application Whitelisting Tool | ……. Generic architecture of Application Whitelisting tool is given in Appendix -B (B- 36) | Replace with …….. Generic architecture of Application Whitelisting tool is given in Appendix -B. |
|  | Vol. II Part-B, Section – 9, Clause no. –9.1.7, End Point Security | End Point Security | Replace with End Point Security Solution (Antivirus) |
|  | Vol. II Part-B, Section – 9, Clause no. –9.1.7, End Point Security | ….. It shall log all USB port access events. | Replace with …….. It shall log all USB port access events. (capturing details of connected USB). It shall allow only identified USB devices to connect to a computer system. |
|  | Vol. II Part-B, Section – 9, Clause no. –9.1.8, Software Update and Patch Management tool | The Contractor shall be responsible for the maintenance & update of the patches, firmware and signatures of Operating system, entire SCADA/EMS system, Firewalls, Networking Equipment during entire contract period. Automated patch management tools shall be provided to facilitate the distributions of relevant patches to the entire system. Patches should be applied to all the devices & software delivered in the project. The contractor shall also be responsible for providing updates/patches for all the software products supplied under the project for entire period of contract. | Replace with The Contractor shall be responsible for the maintenance & update of the patches, firmware and signatures of Operating system, entire SCADA/EMS system, Firewalls, Networking Equipment during entire contract period including extension of contract, if any. Patches shall be downloaded from authentic sources in patch management server that is available in DMZ zone. After successful downloading it shall be transferred to patch management server in PDS Lan, where all the patches will be tested. After successful testing of the patches, it shall be distributed to the entire system. Automated patch management tools shall be provided to facilitate the distributions of relevant patches to the entire system. Patches should be applied to all the devices & software delivered in the project. The contractor shall also be responsible for providing updates/patches for all the software products supplied under the project for entire period of contract. |
|  | Vol. II Part-D, RTU | Appendix A: RTU I/O counts for JK PDD | Replace with Appendix A: RTU I/O counts for JK PDD & DTL The revised Appendix A: RTU I/O counts for JK PDD & DTL is attached at Annexure-IV |
|  | Vol. II Part-D, Section-1, Clause 1.2, RTU Functions | (j) Acting as a data concentrator for acquiring data from Slave RTUs, MFTs and exercising supervisory control on slave RTUs, MFTs using IEC 60870-5-101, IEC 60870-5-104 and MODBUS protocol. | Replace with (j) Acting as a data concentrator for acquiring data from Slave RTUs, exercising supervisory control on slave RTUs, using IEC 60870-5-101, IEC 60870-5-104 protocol and acquiring data from MFTs on MODBUS protocol. Add para ### (n) The supplied RTU shall have data communication on secure IEC 60870-5-104. The security features shall be per IEC 60870-5-7. |
|  | Vol. II Part-D. Section-1, Clause 1.3, Communication ports | (f) Required number (minimum two) of RS485 ports for polling Multi-function Transducers using MODBUS, IEC 60870-5-101 protocol in multi-drop (party line) mode or IEC 60870-5-104 protocol. However Maximum 8 Numbers of MFTs shall be connected to a single port in multi-drop mode…………………………. | Replace with (f) Required number (minimum two) of RS485 ports for polling Multi-function Transducers using MODBUS, IEC 60870-5-103 protocol in multi-drop (party line) mode. However Maximum 8 Numbers of MFTs shall be connected to a single port in multi-drop mode…………………………. |
|  | Vol. II Part-D, Section-1, Clause 1.12, Analog Points | Mean accuracy shall drift no more than 0.002% per degree C with in the temperature range of –5 to +55 degree C. | Replace with Mean accuracy shall drift no more than 0.002% per degree C with in the temperature range of –5 to +55 degreeCfor all RTU Locations except J&K and of –20 to +55 degree C for J&K RTU Locations. |
|  | Vol. II Part-D Section-1, Clause 1.16, | # Control Outputs The RTU shall provide the capability for a master station to select and change the stateof digital output points either directly or through MFT. In case the Control Output is provided through MFT, the communication between RTU & MFT shall also support select before operate functionality. Device control will be used by owner to control power system devices including: (a) Two-state Devices: Circuit breakers, motor-operated switches, auto/manual switches, relay disable/enable, and other two-state devices (b) Variable Output Devices: Raise/lower control of generators, transformer load-tap-changers (LTC), and other variable output devices. The RTUs shall have the capability for control outputs as described in the following sections. | Replace with # Control Outputs The RTU shall provide the capability for a master station to select and change the stateof digital output points. Device control will be used by owner to control power system devices including: (a) Two-state Devices: Circuit breakers, motor-operated switches, auto/manual switches, relay disable/enable, and other two-state devices (b) Variable Output Devices: Raise/lower control of generators, transformer load-tap-changers (LTC), and other variable output devices. The RTUs shall have the capability for control outputs as described in the following sections. |
|  | Vol. II Part-D Section-1, Clause 1.20 | # Environmental Requirements The RTUwill be installed in control room buildings with no temperature or humidity control. The RTUs shall be capable of operating in ambient temperature from -5 to +55 degree C with rate of temperature change of 20 degree C/hour and relative humidity less than 95%, non-condensing. At some locations, environmental temperature may go below –5 degree C for which the contractor shall take suitable measures for successful operation of RTU. | Replace with # Environmental Requirements - For all RTU Locations except J&K The RTUwill be installed in control room buildings with no temperature or humidity control. The RTUs shall be capable of operating in ambient temperature from -5 to +55 degree C with rate of temperature change of 20 degree C/hour and relative humidity less than 95%, non-condensing. At some locations, environmental temperature may go below –5 degree C for which the contractor shall take suitable measures for successful operation of RTU. - For J&K RTU Locations The RTU will be installed in control room buildings with no temperature or humidity control. The RTUs & associated items shall be capable of operating in ambient temperature from -20 to +55 degree C and relative humidity less than 95%, non-condensing. At some locations, environmental temperature may go below –20 degree C for which the contractor shall take suitable measures for successful operation of RTU & associated items. |
|  | Vol. II Part-D, Section-1, Clause 1.28.4.2, Relative Humidity Sensor | Accuracy:3 % or better Operating Temperature: -5 oC to + 60 o C | Replace with Accuracy :± 3 % or better Operating Temperature Range: -5oC to + 60 o Cfor all RTU Locations except J&K Operating Temperature Range : -20 oC to + 60 o C for J&K RTU Locations |
|  | Vol. II Part-D, Section-1, Clause 1.28.4.2, Air Temperature Sensor | Temperature Range: -5 oC to + 60 o C | Replace with Temperature Range: -5oC to + 60 o C for all RTU Locations except J&K Temperature Range : -20 oC to + 60 o C for J&K RTU Locations |
|  | Vol. II Part-D, Section-1, Clause 1.28.4.3, Rainfall Sensor | Accuracy :4 % Operating Temperature Range : -5 oC to + 60 o C | Replace with Accuracy :± 4 % Operating Temperature Range:-5oC to + 60 o C for all RTU Locations except J&K Operating Temperature Range: -20 oC to + 60 o C for J&K RTU Locations |
|  | Vol. II Part-D Section-1, Clause 1.29 | # Portable Configuration and Maintenance Terminal (PCMT) Contractor shall supply a Portable Configuration and maintenance Terminal (Laptop PC) which shall provide followings capabilities:……… | Replace with # Portable Configuration and Maintenance Terminal (PCMT) Contractor shall supply Portable Configuration and maintenance Terminal (Laptop PC) as mentioned in BPS which shall provide followings capabilities. ……… |
|  | Vol. II Part-D Section-1, Clause 1.29 (b) Local Operator interface and RTU diagnostics | ### (b) Local Operator interface and RTU diagnostics The Local Operator interface software shall support operator inquiries to demand current status and data values of various RTU points, or an overall substation snapshot, or of the status change buffer………… | Replace with ### (b) Local Operator interface and RTU diagnostics The Local Operator interface software being supplied with the PCMT shall support operator inquiries to demand current status and data values of various RTU points, or an overall substation snapshot, or of the status change buffer…………………… |
|  | Vol. II Part-D Section-1, Clause 1.29 (c) Master station-cum-RTU simulator & protocol analyser software tool | ### (c) Master station-cum-RTU simulator & protocol analyzer software tool The Master station and RTU simulator cum Protocol Analyser software shall be used to monitor and test the RTU's operation using the master station communication protocol. It shall have the following features………………. | Replace with ### (c) Master station-cum-RTU simulator & protocol analyzer software tool The Master station and RTU simulator cum Protocol Analyser software being supplied with the PCMT shall be used to monitor and test the RTU's operation using the master station communication protocol. It shall have the following features………………….. |
|  | Vol. II Part-D Section-1 | # New Table added. | # New table addition DRS of LDMS IPC, Monitor for LDMS IPC, Time Synchronization Equipment, PCMT (Laptop PC) & Furniture for LDMS is attached at Annexure-V. |
|  | Vol. II Part-D Section-1, Table 3, | 14; Cold Test; ON; -; Continuous operation at 00 C for 96 hrs; 0. | 14; ON; Cold Test; -; Continuous operation at 00 C for 96 hrs1. (For all RTU Locations except J&K); 0. Continuous operation at -200 C for 96 hrs (For J&K RTU Locations). Replace with |
|  | Vol. II Part-B Appendix-G, Bill of Quantity, NRLDC | B; Hardware. 2.21; Video Projection System. S.No.; Item Description; Unit; Quantity. Main CC; Backup CC. (i); Laser VPS; No.; 0; 0. (ii); LED VPS; No.; 21; 6. | Replace with B; Hardware. 2.21; Video Projection System. S.No.; Item Description; Unit; Quantity. Main CC; Backup CC. (i); Laser VPS; No.; 21; 6. (ii); LED VPS; No.; 0; 0. |
|  | Vol. II Part-B Appendix-G, Bill of Quantity | Note: - Above mentioned requirements are minimum, however, if bidder feels that some additional hardware/software is also required to meet the technical specification requirements. Same may be considered by the bidder without any additional cost to the Owner. …… | Replace with Note: The above mentioned requirements are applicable to BoQ of all constituents specified under Appendix-G. - Above mentioned requirements are minimum, however, if bidder feels that some additional hardware/software is also required to meet the technical specification requirements. Same may be considered by the bidder without any additional cost to the Owner. …….. |
|  | Vol. II Part-B Appendix-G, Bill of Quantity, Spares | SPARES OF NRLDC, HVPNL, PTCUL, J&K, DTL, UP, PSTCL, BBMB, RRVPNL, HP SLDC | Replace with SPARES OF NRLDC, HVPNL, PTCUL, J&K, DTL, UP, PSTCL, BBMB, RRVPNL, HP SLDC The List of Spare of RLDC/SLDCs is attached at Annexure-VI. |
|  | Vol. II Part-B Appendix-G, Bill of Quantity |  | Add new line VPS configuration of RLDC/SLDCs/SUBSLDCs Annexure – VII. |
|  | Vol. II Part-B Appendix-G, Bill of Quantity, PSTCL | Bill of Quantity for SCADA/EMS System of PSTCL. SI. No.; Item Description; Unit; Quantity Main CC. 1.15 (b)+A50 :DA50: D205; NAS Software; Lot; 1. | Replaced with Bill of Quantity for SCADA/EMS System of PSTCL. SI. No.; Item Description; Unit; Quantity Main CC. 1.15 (b); NAS Software; Lot; 1. |
|  | Vol. II Part-B Appendix-G, Bill of Quantity, Ballabhgarh | Bill of Quantity for SCADA/EMS System. SI. No.; Item Description; Unit; Quantity Main CC; Quantity Backup CC. 2.18; Data Concentrator PC (DCPC) with following compoments at each site as per technical specification; Set; 0; 0. | Bill of Quantity for SCADA/EMS System. SI. No.; Item Description; Unit; Quantity Main CC; Quantity Backup CC. 2.18; Data Concentrator PC (DCPC) with following components at each site as per technical specification. Replaced with |
|  | Vol. II Part-B Appendix-G, Bill of Quantity, NRLDC | Bill of Quantity for SCADA/EMS System of NRLDC. SI. No.; Item Description; Unit; Quantity. Main CC; Backup CC. 3.2; 80 KVA UPS system. (a); 80 kVA (64 kW at 0.8 pf) UPS running in parallel; No.; 0; 2. | Bill of Quantity for SCADA/EMS System of NRLDC. SI. No.; Item Description; Unit; Quantity. Main CC; Backup CC. 3.2; 80 KVA UPS system - Modular. (a); 80 kVA (64 kW at 0.8 pf) Modular UPS running in parallel; No.; 0; 2. Replace with |
|  | Vol. II Part-B Appendix-G, Bill of Quantity, NRLDC | Bill of Quantity for SCADA/EMS System of NRLDC. SI. No.; Item Description; Unit; Quantity. Main CC; Backup CC. 3.3; 60 KVA UPS system. (a); 60 kVA (48 kW at 0.8 pf) UPS running in parallel; No.; 2; 0. | Bill of Quantity for SCADA/EMS System of NRLDC. SI. No.; Item Description; Unit; Quantity. Main CC; Backup CC. 3.3; 60 KVA UPS system - Modular. (a); 60 kVA (48 kW at 0.8 pf) Modular UPS running in parallel; No.; 2; 0. Replace with |
|  | Vol. II Part-B Appendix-G, Bill of Quantity, HP SLDC | Bill of Quantity for SCADA/EMS System of HP SLDC. Quantity. SI. No.; Item Description; Unit; Main CC; Backup CC. 3.2; 80 KVA UPS system. (a); 80 kVA (64 kW at 0.8 pf) UPS running in parallel; No.; 2; 0. (b); VRLA type Battery banks for UPS (each bank of atleast 153.6 kVAH); No.; 2; 0. (c ); Input ACDB (350KVA rating); No.; 1; 0. (d); Output ACDB (300 kVA rating); No.; 1; 0. | Replace with Bill of Quantity for SCADA/EMS System of HP SLDC. Quantity. SI. No.; Item Description; Unit; Main CC; Backup CC. 3.2; 120 KVA UPS system. (a); 120 kVA (96 kW at 0.8 pf) UPS running in parallel; No.; 2; 0. (b); VRLA type Battery banks for UPS (each bank of atleast 230.4 kVAH); No.; 2; 0. (c ); Input ACDB (600 KVA rating); No.; 1; 0. (d); Output ACDB (400 kVA rating); No.; 1; 0. |
|  | Vol. II Part-B Appendix-G, Bill of Quantity, HP SLDC | Bill of Quantity for SCADA/EMS System of HP SLDC. Quantity. SI. No.; Item Description; Unit; Main CC; Backup CC. D; DG system. (d); 160 KVA DG set; No.; 0; 0. (e); 200 KVA DG Set; No.; 1; 0. | Replace with Bill of Quantity for SCADA/EMS System of HP SLDC. Quantity. SI. No.; Item Description; Unit; Main CC; Backup CC. D; DG system. (d); 160 KVA DG set; No.; 1; 0. (e); 200 KVA DG Set; No.; 0; 0. |
|  | Vol. II Part-B, Appendix-G, RRVPNL | Bill of Quantity for SCADA/EMS System of RRVPNL S.No.; Item Description; Unit; Quantity. Main CC; Backup CC. 2.20; Remote Consoles. (c ); Remote consoles with 55"monitor with CPU. (i); Remote consoles with CPU (55"monitor); No; 3; 0. (ii); 55" monitor for remote console; No; 3; 0. 2.23; Printers. (c ); A4 size Multi Functional Printer; No; 0; 0. | Replace with Bill of Quantity for SCADA/EMS System of RRVPNL S.No.; Item Description; Unit; Quantity. Main CC; Backup CC. 2.20; Remote Consoles. (c ); Remote consoles with 55"monitor with CPU. (i); Remote consoles with CPU (55"monitor); No; 0; 0. (ii); 55" monitor for remote console; No; 0; 0. 2.23; Printers. (c ); A4 size Multi Functional Printer; No; 5; 0. |
|  | Vol. II Part-B, Appendix-G, RRVPNL Sub SLDC, JODHPUR | S.No.; Item Description; Unit; Quantity. Main CC. 2.20; Remote Consoles. (c ); Remote consoles with 55"monitor with CPU. (i); Remote consoles with CPU (55"monitor); No; 0. (ii); 55" monitor for remote console; No; 0. Bill of Quantity for SCADA/EMS System of RRVPNL SUBSLDC JODHPUR | Replace with Bill of Quantity for SCADA/EMS System of RRVPNL SUBSLDC JODHPUR S.No.; Item Description; Unit; Quantity. Main CC. 2.20; Remote Consoles. (c ); Remote consoles with 55"monitor with CPU. (i); Remote consoles with CPU (55"monitor); No; 1. (ii); 55" monitor for remote console; No; 1. |
|  | Vol. II Part-B, Appendix-G, RRVPNL Sub SLDC, KOTA | S.No.; Item Description; Unit; Quantity. Main CC. 2.20; Remote Consoles. (c ); Remote consoles with 55"monitor with CPU. (i); Remote consoles with CPU (55"monitor); No; 0. (ii); 55" monitor for remote console; No; 0. Bill of Quantity for SCADA/EMS System of RRVPNL SUBSLDC KOTA | Replace with Bill of Quantity for SCADA/EMS System of RRVPNL SUBSLDC KOTA S.No.; Item Description; Unit; Quantity. Main CC. 2.20; Remote Consoles. (c ); Remote consoles with 55"monitor with CPU. (i); Remote consoles with CPU (55"monitor); No; 1. (ii); 55" monitor for remote console; No; 1. |
|  | Vol. II Part-B, Appendix-G, RRVPNL Sub SLDC, Ratangarh | S.No.; Item Description; Unit; Quantity. Main CC. 2.20; Remote Consoles. (c ); Remote consoles with 55"monitor with CPU. (i); Remote consoles with CPU (55"monitor); No; 0. (ii); 55" monitor for remote console; No; 0. Bill of Quantity for SCADA/EMS System of RRVPNL SUBSLDC Ratangarh | Replace with Bill of Quantity for SCADA/EMS System of RRVPNL SUBSLDC Ratangarh S.No.; Item Description; Unit; Quantity. Main CC. 2.20; Remote Consoles. (c ); Remote consoles with 55"monitor with CPU. (i); Remote consoles with CPU (55"monitor); No; 1. (ii); 55" monitor for remote console; No; 1. |
|  | Vol. II Part-B, Appendix-G | Table - RTU OF J&K PDD Table - RTU OF DTL | Replaced with Table - RTU OF J&K PDD Table - RTU OF DTL The BoQ of RTU of J&K and DTL is attached at Annexure-VIII. |
|  | Vol. II Part-B Appendix-H, DRS- HARDWARE & SOFTWARE SPECIFICATION, DRS of LED VPS | Table 21. Video Projection System - LED (VPS) | Deleted |
|  | Vol. II Part-B Appendix-H, Hardware Specifications, 19. Laptops: a.For Maintenance b. For DTS c.For RTU Testing d. VAPT | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 10; Wi-Fi wireless LAN adapter; Dual Band Wireless-AC 7265 2x2 + Bluetooth 4.0. | Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 10; Wi-Fi wireless LAN adapter; Dual Band Wireless + Bluetooth 4.0. |
|  | Vol. II Part-B, Appendix-H-1, SIEM, S.No. 27 | Sr. No.; Minimum Technical Specifications; Bidder’s Compliance. 27; SIEM shall be integrated with SOAR or another SOC in future and provision of bidirectional message exchange in SYSLOG, CEF and LEEF format shall be provided along with the supplied SIEM system. | Replace with Sr.No.; Minimum Technical Specifications; Bidder’s Compliance. 27; SIEM shall be integrated with SOAR or another SOC in future and provision of bidirectional message exchange in SYSLOG, CEF or LEEF format shall be provided along with the supplied SIEM system.. |
|  | Vol. II Part-B, Appendix-H-1, Software Specification, Table no. 16, ANTI-APT | Sr. No.; Minimum Required Specifications; Offered by the Contractor. 17.; There should be Separate purpose-built Appliance for Zero Day/Sandbox/ATP with minimum 4x 1GE/10G Ethernet/FO interface (depends on proposed architecture), 950 GB or more Storage on appliance.. | Replace with Sr. No.; Minimum Required Specifications; Offered by the Contractor. 17.; There should be separate purpose-built Appliance for Zero Day/Sandbox/ATP with minimum 4x1GE/FO interface (depends upon proposed architecture), 950 GB or more storage on appliance.. |
|  | Volume II, Part B, Appendix-H , Table 15, Centralized Management of Firewalls | Centralized Management of Firewalls (Common for main and backup Control Centre) Sr. No.; Minimum Required Specifications; Bidder’s proposed specifications. 1; In case of software-based application, required VM for the installation of software has already considered under the project, however, if specific OS is required to make it operational, same shall be provided by the vendor. All other necessary licenses shall be provided by the bidder.. 8; The management platform must provide multiple report output types or formats, such as PDF, HTML, and CSV.. | Replace with Centralized Management of Firewalls Sr. No.; Minimum Required Specifications; Bidder’s proposed specifications. 1; In case of software-based application, required VM for the installation of software to be considered by the contractor Also, if specific OS is required to make it operational, same shall be provided by the vendor.. 8; The management platform must provide multiple report output types or formats, such as PDF and CSV.. |
|  | Volume II, Part B, Appendix-H, Table-13, External Network Firewall with NIPS (For DMZ and RTU-ICCP Connectivity) | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 4 (a); Should have 6 Gbps or more of NGFW (FW and AVC) throughput in real-world / production environment/Application Mix and Minimum NG Threat prevention throughput in real world/production environment (by enabling and measured with Application-ID/AVC, NGIPS, Anti-Virus, Anti-Spyware, Anti Malware, Anti-Bot, Zeroday attacks and logging security threat prevention features enabled – 3 Gbps real world/production environment/Application Mix.. 4 (b ); Firewall should have at least 1.5 Gbps of VPN throughput. 11; IPv6 features; Syn Cookie, Syn-proxy DoS attack detection, SIP, RSTP, ALG’s, BGP4, DHCPv6 Relay, IPv4 to IPv6 translations & Encapsulations.. | Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 4. (a); Should have Minimum NG Threat prevention throughput in real world/production environment (by enabling and measured with Application-ID/AVC, NGIPS, Anti-Virus, Anti-Spyware, Anti Malware, Anti-Bot, Zero-day attacks and logging security threat prevention features enabled – 6 Gbps real world/production environment/Application Mix.. 4 (b ); Delete. 11; IPv6 features; Syn Cookie, Syn-proxy DoS attack detection, SIP, ALG’s, BGP4, DHCPv6 Relay, IPv4 to IPv6 translations & Encapsulations.. 29.; All features in the firewall should be functional/operational within 5 minutes of Power ON... 30.; Any new policy/ policies should be applied in the firewall in not more than 5 minutes. The time shall be measured from the pushing of the policy from management console to the policy becoming effective.. 31.; Shall support inbuilt IPS inspection for all traffic including IEC60870-5- 104, ICCP and other SCADA protocols. |
|  | Volume II, Part B, Appendix-H Table-14, Internal Network Firewall with NIPS | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 4 (a); Should have 6 Gbps or more of NGFW (FW and AVC) throughput in real-world / production environment/Application Mix and Minimum NG Threat prevention throughput in real world/production environment (by enabling and measured with Application-ID/AVC, NGIPS, Anti-Virus, Anti-Spyware, Anti Malware, Anti-Bot, Zeroday attacks and logging security threat prevention features enabled – 3 Gbps real world/production environment/Application Mix.. 4 (b ); Firewall should have at least 1.5 Gbps of VPN throughput. 10; IPv6 features; Syn Cookie, Syn-proxy DoS attack detection, SIP, RSTP, ALG’s, BGP4, DHCPv6 Relay, IPv4 to IPv6 translations & Encapsulations.. | Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 4. (a); Should have Minimum NG Threat prevention throughput in real world/production environment (by enabling and measured with Application-ID/AVC, NGIPS, Anti-Virus, Anti-Spyware, Anti Malware, Anti-Bot, Zero-day attacks and logging security threat prevention features enabled – 6 Gbps real world/production environment/Application Mix.. 4 (b); Delete. 10; IPv6 features; Syn Cookie, Syn-proxy DoS attack detection, SIP, ALG’s, BGP4, DHCPv6 Relay, IPv4 to IPv6 translations & Encapsulations.. 29.; All features in the firewall should be functional/operational within 5 minutes of Power ON.. 30.; The policy application should be applied in the firewall in not more than 5 minutes. The time shall be measured from the pushing of the policy from management console and it coming into effect.. 31.; Shall support inbuilt IPS inspection for all traffic including IEC60870-5- 104, ICCP and other SCADA protocols. |
|  | # Volume II, Part B, Appendix-H Table 12, Link Load Balancer (LLB) | Sr. No.; Minimum Required Specifications; Bidder’s proposed specifications. 9; The proposed appliance shall have capability to run in standalone as well as virtualized mode. 17; LLB shall be designed to run both IPv4 & IPv6 simultaneously (Dual Stack) from day one.. | Sr. No.; Minimum Required Specifications; Bidder’s proposed specifications. 9; The proposed appliance shall have capability to run in standalone as well as in HA mode. 17; LLB shall be designed to run both IPv4 & IPv6 simultaneously (Dual Stack) from day one and appliance should be IPV6 Ready logo certified from day one.. Replace with |
|  | Volume II, Part B, Appendix-H Table 1, Servers: | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 5.; Processor; Min 2x16 core, x86 64-bit latest processor (with latest chipset) with 3.0 GHz or more base frequency. 10; Optical Drive; DVD RW. 12; Configuration & management; • Real-time out-of-band hardware performance monitoring & alerting • Agent-free monitoring, driver updates & configuration, power monitoring & capping, RAID management, monitoring of I/O card & system health. • Out-of-band hardware & firmware inventory • Auto configuration to auto deploy a baseline server configuration profile. • Automated hardware configuration and deployment to multiple servers •Virtual IO management / stateless computing. | Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 5.; Processor; Min 2x16 core, x86 64-bit third generation or latest processor (with compatible chipset) with 3.0 GHz or more base frequency The OEM software should be tested on the offered processor & chipset. 10; Deleted. 12; Configuration & management; • Real-time out-of-band hardware performance monitoring & alerting •Agent-free monitoring, driver updates & configuration, power monitoring & capping, RAID management, monitoring of I/O card & system health. • Out-of-band hardware & firmware inventory • Auto configuration to auto deploy a baseline server configuration profile. • Automated hardware configuration and deployment to multiple servers. |
|  | Volume II, Part B, Appendix-H, Table 2, Servers: DSA application | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 5.; Processor; Min 2x18 core, x86 64-bit latest processor (with latest chipset) with 3.0 GHz or more base frequency. 7; Internal Auxiliary memory; 4 TB SSD delivered after RAID 1 disk configuration, expandable up to 8 TB, Hot-pluggable. 10.; Optical Drive; DVD RW. 12; Configuration & management; • Real-time out-of-band hardware performance monitoring & alerting • Agent-free monitoring, driver updates & configuration, power monitoring & capping, RAID management, monitoring of I/O card & system health. • Out-of-band hardware & firmware inventory • Auto configuration to auto deploy a baseline server configuration profile. • Automated hardware configuration and deployment to multiple servers •Virtual IO management / stateless computing. | Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 5.; Processor; Min 2x18 core, x86 64-bit third generation or latest processor (with compatible chipset) with 3.0 GHz or more base frequency The OEM software should be tested on the offered processor & chipset. 7; Internal Auxiliary memory; 3.84 TB SSD delivered after RAID 1 disk configuration, expandable up to 8 TB, Hot-pluggable. 10; Deleted. 12; Configuration & management; • Real-time out-of-band hardware performance monitoring & alerting • Agent-free monitoring, driver updates & configuration, power monitoring & capping, RAID management, monitoring of I/O card & system health. • Out-of-band hardware & firmware inventory • Auto configuration to auto deploy a baseline server configuration profile. • Automated hardware configuration and deployment to multiple servers. |
|  | Volume II, Part B, Appendix-H, Table 3, Servers: a.DTS Applications b.PDS Applications | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 5.; Processor; Min 2x16 core, x86 64-bit latest processor (with latest chipset) with 3.0 GHz or more base frequency. 10; Optical Drive; DVD RW. 12; Configuration & management; • Real-time out-of-band hardware performance monitoring & alerting • Agent-free monitoring, driver updates & configuration, power monitoring & capping, RAID management, monitoring of I/O card & system health. • Out-of-band hardware & firmware inventory • Auto configuration to auto deploy a baseline server configuration profile. • Automated hardware configuration and deployment to multiple servers •Virtual IO management / stateless computing. | Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 5.; Processor; Min 2x16 core, x86 64-bit third generation or latest processor (with compatible chipset) with 3.0 GHz or more base frequency The OEM software should be tested on the offered processor & chipset. 10; Deleted. 12; Configuration & management; • Real-time out-of-band hardware performance monitoring & alerting • Agent-free monitoring, driver updates & configuration, power monitoring & capping, RAID management, monitoring of I/O card & system health. • Out-of-band hardware & firmware inventory • Auto configuration to auto deploy a baseline server configuration profile. • Automated hardware configuration and deployment to multiple servers. |
|  | Volume II, Part B, Appendix-H, Table-4, Servers: # a. Server for Third Party Applications # b.Servers for Management Applications # c.Servers for Applications in Internal DMZ # d.Servers for Applications in External DMZ | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 5.; Processor; Min 2x16 core, x86 64-bit latest processor (with latest chipset) with 3.0 GHz or more base frequency. 6; RAM; 156 GB delivered, expandable up to 256 GB or Above DDR4RDIMMs/LRDIMMs. The operating system delivered should support expansion up to 256 GB of RAM.. 7; Internal Auxiliary memory; 2 TB SSD delivered after RAID 1 disk configuration, expandable up to 4 TB, Hot-pluggable. 12; Configuration & management; • Real-time out-of-band hardware performance monitoring & alerting • Agent-free monitoring, driver updates & configuration, power monitoring & capping, RAID management, monitoring of I/O card & system health. • Out-of-band hardware & firmware inventory • Auto configuration to auto deploy a baseline server configuration profile. • Automated hardware configuration and deployment to multiple servers •Virtual IO management / stateless computing. | Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 5.; Processor; Min 2x16 core, x86 64-bit third generation or latest processor (with compatible chipset) with 3.0 GHz or more base frequency The OEM software should be tested on the offered processor & chipset. 6; RAM; 256 GB delivered, expandable up to 512 GB or Above DDR4RDIMMs/LRDIMMs. The operating system delivered should support expansion up to 512 GB of RAM.. 7; Internal Auxiliary memory; 1.92 TB SSD delivered after RAID 1 disk configuration, expandable up to 4 TB, Hot-pluggable. 12; Configuration & management; • Real-time out-of-band hardware performance monitoring & alerting • Agent-free monitoring, driver updates & configuration, power monitoring & capping, RAID management, monitoring of I/O card & system health. • Out-of-band hardware & firmware inventory • Auto configuration to auto deploy a baseline server configuration profile. • Automated hardware configuration and deployment to multiple servers. Note : 5 nos. of DVD RW to be supplied per each control center for servers(Main and Backup CC) |
|  | Volume II, Part B, Appendix-H, Table-4, Storage System 6.1 Storage Area Network (SAN) | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 6; The Storage array should be able to support Block protocols since current use case is also for storing Databases via FC & iSCSI.. | Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 6; The Storage array should be able to support Block protocols since current use case is also for storing Databases via FC.. |
|  | Volume II, Part B, Appendix-H, Table 5, Back-up Solution | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 3; The proposed appliance must be a converged, integrated appliance for long term data retention and disaster recovery.. 14; Should have min 02 TB/hr. backup throughput.. 15; The Proposed backup solutions should support online backup of IBM DB2, IBM Lotus Domino, Microsoft Exchange, Microsoft Office Share Point Server, Microsoft SQL Server, MySQL, Oracle Databases and NoSQL, without any additional licenses requirement. 18; Should have optimized de- duplication Algorithm. The de- duplication Solution must provide an optimized de-duplication pool for multiple logical devices i.e. multiple devices created over disk through NAS, CIFS, OST etc. in order to significantly improve backup appliance storage utilization n and help retain data longer.. 28; Interface ports; The appliance should be offered with Min.4 x10 Gbps SFP+. If Fiber Ethernet ports are provided then SFPs to be supplied for all ports.. | Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 3; The proposed appliance must be a purpose built backup appliance for long term data retention and disaster recovery.. 14; Should have min 10 TB/hr. backup throughput.. 15; The Proposed backup solutions should support online backup of IBM DB2, IBM Lotus Domino, Microsoft Exchange, Microsoft Office Share Point Server, Microsoft SQL Server, MySQL, Oracle Databases and NoSQL. Contractor has to supply all or any licences without any additional cost, which may be required in Back-up Solution to meet functionalities envisaged of supplied systems and software components under the project.. 18; Should have optimized de-duplication Algorithm. The deduplication Solution should significantly improve backup appliance storage utilization and help retain data longer.. 28; Interface ports; The appliance should be offered with Min.4 x10 Gbps SFP+. If Fiber Ethernet ports are provided then SFPs to be supplied for all ports. The appliance should have minimum 2 x 16 Gbps FC.. |
|  | Volume II, Part B, Appendix-H, Table-7, Router cum Firewall: ICCP and RTU Communication | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 6; Features to support; QoS, MPLS, Security, Broadband, Multiservice, Voice, IP to IP Gateway. | Replace with Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 6; Features to support; QoS, MPLS, Security, Multiservice, IP to IP Gateway. |
|  | Volume II, Part B, Appendix-H Table-8, Router cum Firewall for PDS, Remote Console, External World Connectivity and others | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 6; Features to support; QoS, MPLS, Security, Broadband, Multiservice, Voice, IP to IP Gateway. | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 6; Features to support; QoS, MPLS, Security, Multiservice, IP to IP Gateway. Replace with |
|  | Volume II, Part B, Appendix H, Table-9 LAN switch | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 7; L3 feature; c. IS-IS for IPv4 and IPv6 (IS-ISv6). | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 7; L3 feature; c. {IS-IS for IPv4 and IPv6} or {OSPF for IPv4 and IPv6}. Replace with |
|  | Volume II, Part B, Appendix-H, Table 10, LAN switch | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 7; L3 feature; c. IS-IS for IPv4 and IPv6 (IS-ISv6). | Sr. No.; Description of the Features; Minimum Quantity of the features; Offered by the Contractor. 7; L3 feature; c. {IS-IS for IPv4 and IPv6} or {OSPF for IPv4 and IPv6}. Replace with |
|  | Volume II, Part B, Appendix-H, Table-26, Terminal Server | Table 26, Terminal Server | Replace with Revised Table- 26, Terminal Server is attached at Annexure-IX |
|  | Volume II, Part B, Appendix-H, Table -27, PC for DCPC | Table 27, PC for DCPC | Replace with Revised Table- 27, PC for DCPC is attached at Annexure-X |
|  | Volume II, Part B, Appendix-H, Table- 33, Video Wall - Tower type /Wall Mounted (55”) | Table 33, Video Wall - Tower type /Wall Mounted (55”) | Replace with Revised Table- 33, 55” Video Wall with controller is attached at Annexure-XI |
|  | Volume II, Part B, Appendix-H, |  | Inserted Table- 38, Splitter attached at Annexure-XII |