| Sl. No | Reference/ Clause no | Description |  | Bidder's Queries | Clarification |
| --- | --- | --- | --- | --- | --- |
|  | GIS-REV 5A2.3 | The equipment offered shall be protected against all types of voltage surges and any equipment necessary to satisfy this requirement shall deemed to be included. |  | We understand that surge arrestors are required to cater the requirement and are of AIS type. | Bidder to Quote as per requirement of Bidding Documents. |
|  | GIS-REV 5A7.2.13 | The disconnectors and safety grounding switches shall have a mechanical and electrical inter-locks to prevent closing of the grounding switches when isolator switches are in the closed position and to prevent closing of the disconnectors when the grounding switch is in the closed position. Integrally mounted lock when provided shall be equipped with a unique key for such three phase group. Master key is not permitted. |  | The disconnectors and the safety grounding switches are separate modules in GIS design and shall have only electrical inter-locks between them. However the required padlocking facility shall be provided for the manual interlocking for additional protection. Offer shall be as per past supplies to PGCIL. | Bidder to Quote as per requirement of Bidding Documents. |
|  | Section ProjectB | The details of existing GIS Building and GIS bus extension module shall be provided to successful bidder for necessary interfacing during detailed engineering. |  | Existing GIS room dimension and availability of space for the extension of GIS diameter under present scope is very important hence we request you to provide GA drawings of existing GIS. | The relevant drawings shall be shared with successful bidder during detailed engineering. |
|  | Section ProjectB | The details of existing GIS Building and GIS bus extension module shall be provided to successful bidder for necessary interfacing during detailed engineering. |  | Section view, busbar height from ground as well as another busbar is not available hence request you to provide below minimum details to design interface module, 1. Section drawings as well as end module drawing which will be extended. 2. Pressure in the end module gas compartments of the GIS. | The relevant drawings shall be shared with successful bidder during detailed engineering. |
|  | General |  | - | Please confirm the location of GIS, LCC and trench route in between? | Location of GIS hall at 400 kV Malerkotla S/s is indicated in Tender GA. The other details shall be shared with successful bidder during detailed engineering. |
|  | General |  | - | Please confirm any plan for further bay extension after present scope? | The offered GIS should be suitable for future bay extension. |
|  | General |  | - | Power cable housing in GIS equipment shall be provided as per OEM standard. | Bidder to Quote as per requirement of Bidding Documents. |
|  | General |  | - | Outdoor GIB length shall be calculated from inner edge of GIS hall wall | - Please refer Annexure-S11, ANNEXURE- 13 Of GIS Rev5A of Section- Specific Requirement |
|  | General |  | - | GIB length inside GIS hall shall be considered in respective bay | Please refer Annexure-S11, ANNEXURE- 13 Of GIS Rev5A of Section- Specific Requirement |
|  | General |  | - | AC DC power shall be made available by main contractor at HE supplied equipment. | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A5.36 |  | Indicators shall be provided on all circuit breakers, isolators and earth-switches, which shall clearly show whether the switches are open or closed. | Indicators shall be provided on Drive Box/Equipment . Request for your acceptance. | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A5.44 |  | xxv. Additional CB data to be furnished during detailed engineering : a) Design ata on capabilities of circuit breakers in terms of time and number of operations at duties ranging from 100 fault currents to load currents of the lowest possible value without requiring any maintenance or checks. b) Curves supported by test data indicating the opening time under close open operation with combined variation of trip coil voltage and hydraulic pressure. c) Contact Travel: Operating mechanism operating shaft travel and contact overlap of Circuit Breaker to be provided | These Documents being Intellectual property of Hitachi Energy under IPR we shall not be able to submit the same during detail Engg & same never has been requested and submitted to PGCIL in previously executed project. Request to remove the same from requirment list. | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A6.4.6 |  | Withstanding all dielectric stresses imposed on it in open condition at lock out pressure continuously (i.e. shall be designed for 2 p.u. across the breaker continuously, for validation of which a power frequency withstand test conducted for a duration of at least 15 minutes is acceptable). | We wish to clarify that subject clause requirement is not in line to IEC 62271-203 standards requirement. We confirm to offer GIS type tested as per IEC 62271-203. We do not envisage any test to be conducted against clause 6.4.6. | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A6.7.1 e |  | An operation counter shall also be provided . | The operation counter shall be in LCC where it is easier to monitor / note along with other indications. | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A6.7.3 k |  | Separate MCBs shall be provided for each spring charging motor and the rating of MCBs shall be suitably selected to match the starting, running and stalling time. | Offered HMB drive is Spring-hydralic type, and is already accepted in PGCIL. For MCB requirement, If needed MCB will be provided in LCC, same is not feasible to be provided in Drives due to compactness and design constraints. | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A6.7.3 I |  | An overload relay shall be provided for protection of the spring charging motor. | If needed relay will be provided in LCC, same is not feasible to be provided in Drives due to compactness and design constraints. | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A7.2 |  | 7.2.13. The disconnectors and safety grounding switches shall have mechanical/electrical inter-locks to prevent closing of the grounding switches when isolator switches are in the losedposition and to prevent closing of the disconnectors when the grounding switch is in the closed position. | In our offered designed in 420KV GIS , there is a mechanical interlock between Disconnector & Earthing Switch i.e Single drive for the disconnector and earthing switch. Hope the same is acceptable. | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A8.8 |  | All portions of the grounding switch and operating mechanism required for grounding shall be connected together utilizing flexible copper conductors having a minimum cross-sectional area of 100 sq. mm. | In our offered GIS design, Earthing switches and its mechanism are connected via the enclosure i.e they make a continuous earthing path via enclosure itself and so is the case for all the componets. Further, the complete GIS is earthed / grounded at multiple points utilizing flat CU / GI bars. Hope the same is acceptable | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A8.8 |  | All portion of the grounding switches and operating mechanism required for connection to ground shall be connected together utilizing copper conductor having minimum cross-sectional area of 100 sq. mm. | In our offered GIS design, Earthing switches and its mechanism are connected via the enclosure i.e they make a continuous earthing path via enclosure itself and so is the case for all the componets. Further, the complete GIS is earthed / grounded at multiple points utilizing flat CU / GI bars. Hope the same is acceptable | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A15.3.6 |  | All instrument transformer connections shall be hard wired to terminal block via ring type connection. | We understand this requirement is at LCC side only considering the reliability of latest design of Pin Type terminals, request to please accept the Pin type terminations as well. | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A19.7 |  | Further, the manufacturer shall furnish the following information during detailed engineering: b) Calculation for adequacy of UHF sensors to be provided in GIS Installation as per clause no 5.41. c) The calculations and documents in support of the average intensity of electromagnetic field on the surface of the enclosure. d) Calculations to show that there is no Ferro resonance due to capacitance of GIS for the voltage transformers. e) Calculations in support of touch & step voltages in all enclosures and earthing of complete GIS installation. f) Measures to mitigate transient enclosure voltage by high frequency currents. g) The acceptance criteria and limits of impact (of impact recorder) in all three directions which can be withstood by the equipment during transportation and handling. | Please confirm/clarify the following - b. As the design calculations are done via software tool, field experience, therefore request to exempt us from submission of design calculation report. c. , d. , e., f., g. We confirm to submit our standard General Technical Information for your review. Please confirm for the acceptance of the same | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A20.14 |  | Reactor current switching test For Reactive Current switching capability as per Clause 6.4.1 | Shall be in line with Annexure III (14). | Noted |
|  | Technical specification GIS Rev 05 A6.4.7 |  | Circuit breakers shall be able to switch in and out the shunt reactor as detailed below: 400 kV - 50 to 150 MVAr Reactor Ratings | We wish to clarify that the standard test values in IEC 62271-110 are given in order to demonstrate the ability of the switching device to interrupt reactor currents and to determine chopping characteristics (suppression peak over voltages) and re-ignition behavior. The lower the reactor current value, the higher are the stress levels during breaker switching. Hence the offered GIS with test reports with breaking current of 116A are more stringent than the breaking current associated with the project specfic requirement that is 125 MVAr reactor. If any other value of reactor switching current which is lower than IEC requirement, same shall be proven by calculations, if required. Hope the same shall be acceptable | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A8.13 |  | Mechanical position indication shall be provided locally at each switch and Electrical indication at each Local Control Cabinet (LCC) / SAS. | Shall be provided on drives. | Bidder to Quote as per requirement of Bidding Documents. |
|  | Technical specification GIS Rev 05 A6.8 |  | CSD | We understand CSD is to be provided for 1 no. ICT Bay and respective tie bay. Please confirm. If yes request you to add line item of CSD in BoQ | Please refer Clause B.8 of Section- Specific Requirement |
|  | Technical specification GIS Rev 05 A6.8 |  | CSD | Request to clarify if CSD is acceptable in place of PIR in Line & respective Tie bay. Please confirm. If yes then please add line item of CSD in BoQ. | Bidder to Quote as per requirement of Bidding Documents. |
|  | Section-ProjectB (Page 14) |  | 400kV Main Buses for 400kV bays under present scope are to be extended from the existing 400kV GIS buses (one and a half breaker bus bar arrangement) (as per tentative GA and SLD uploaded with tender drawings). | Request to share the tender drawings | The relevant drawings shall be shared with successful bidder during detailed engineering. |
|  | Section-Project9.5 |  | Gopalpur (New) & Gopalpur (OPTCL) substations are situated in coastal area. Hence, all the specifications defined for coastal area in various sections of Technical Specifications shall be applicable for Gopalpur (OPTCL) substations | We shall offer Indoor GIS suitable for corrosion class C4 as per ISO 9223:2012. | Not pertaining to Scope of Tender. |
|  |  |  | Controlled switching device - 7 nos | The qty in BOQ is not matching with the specification of PGCIL. Request to confirm which Bays shall be equipped with CSD. | Not pertaining to Scope of Tender. |
|  | Exclusion |  | General | Any type earthing below or above ground. | Bidder to Quote as per requirement of Bidding Documents. |
|  |  |  |  | Outdoor AIS termination kit for power cable |  |
|  |  |  |  | Indoor GIS side cable termination kit |  |
|  |  |  |  | Any type of system study |  |
|  |  |  |  | Any type of statutory / government utility approval |  |
|  |  |  |  | Any type of cable carrier system /tray/ trench/pipe etc for 1.1kV power control cabling in between GIS to LCC. |  |
|  |  |  |  | Any type of modification/strengthening work in existing system except above mentioned GIS equipment scope. |  |
|  |  |  |  | CRP/BCU/Ethernet/LIU/Metering/SCADA/Integration , HV/EHV cable work |  |
|  |  |  |  | Illumination/ Lightening protection |  |
|  |  |  |  | Any civil work |  |
|  |  |  |  | Transformer & its accessories and any type of cable supply or work from CCM to other equipment's. |  |