## NEW (hidden)
S. No. | VOLT. LEVEL | BAY NAME | BAY NUM. | FEEDER TYPE | DEVICE IDENTIFICATION | POINT DESCRIPTION | DATA TYPE | IEC 104 ADDRESS | REMARK
1 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB OPEN/CLOSE STATUS | DPS
3 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR-RPh | BPCB R PHASE OPEN/CLOSE STATUS | DPS
5 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR-YPh | BPCB Y PHASE OPEN/CLOSE STATUS | DPS
7 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR-Bph | BPCB B PHASE OPEN/CLOSE STATUS | DPS
9 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS ISOLATOR OPEN/CLOSE STATUS | DPS
10 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | ISOLATOR 1 OPEN/CLOSE STATUS | DPS
11 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | ISOLATOR 2 OPEN/CLOSE STATUS | DPS
12 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES1 | EARTH SWITCH 1 OPERATION INTERLOCK | SPS
13 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES2 | EARTH SWITCH 2 OPERATION INTERLOCK | SPS
14 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES1 | EARTH SWITCH 1 OPEN/CLOSE STATUS | DPS
15 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES2 | EARTH SWITCH 2 OPEN/CLOSE STATUS | DPS
16 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE DE-ENRGIZED | SPS
17 | …KV | XXXXXX | BAY NO | FSC | BAY NO | FAULT TO PLATFORM TRIP-1/2 | SPS
18 | …KV | XXXXXX | BAY NO | FSC | BAY NO | PERMANENT BYPASS | SPS
19 | …KV | XXXXXX | BAY NO | FSC | BAY NO | MOV TEMPERATURE R PHASE | AI
20 | …KV | XXXXXX | BAY NO | FSC | BAY NO | MOV TEMPERATURE Y PHASE | AI
21 | …KV | XXXXXX | BAY NO | FSC | BAY NO | MOV TEMPERATURE B PHASE | AI
22 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR R PHASE CURRENT | AI
23 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR Y PHASE CURRENT | AI
24 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR B PHASE CURRENT | AI
25 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR R PHASE UNBALANCED CURRENT | AI
26 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR Y PHASE UNBALANCED CURRENT | AI
27 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR B PHASE UNBALANCED CURRENT | AI
28 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE CT CURRENT R-PH | AI
29 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE CT CURRENT Y-PH | AI
30 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE CT CURRENT B-PH | AI
31 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB STATUS DISCREPANCY | SPS
32 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB AUX CONTACT DISCORDANCE | SPS
33 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | GENRAL LOCKOUT/MIN OIL PRESSURE LOCKOUT | SPS
34 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB POLE DISCREPANCY | SPS
35 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB DC 1/2 FAIL | SPS
36 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB LOSS OF SF6 | SPS
37 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | 1POLE REINSERTION DURING AR | SPS
38 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER FAIL TO OPEN | SPS |  | COMMON- R-PH,Y-PH,B-PH FAIL TO OPEN
39 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER SWITCHWED WITHOUT COMMAND | SPS
40 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER FAIL TO CLOSE | SPS |  | COMMON- R-PH,Y-PH,B-PH FAIL TO CLOSE
41 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS CB SPRING DISCHARGE/FAILURE | SPS
42 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB OPEN CMD | DPC
43 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB CLOSE CMD | DPC
44 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB OPERATION INTERLOCK | SPS
45 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS OPEN CMD | DPC
46 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS CLOSE CMD | DPC
47 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS OPERATION INTERLOCK | SPS
48 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | BYPASS CAP ISO 1 OPEN CMD | DPC
49 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | BYPASS CAP ISO 1 CLOSE CMD | DPC
50 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | BYPASS CAP ISO 1 OPERATION INTERLOCK | SPS
51 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | BYPASS CAP ISO 2 OPEN CMD | DPC
52 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | BYPASS CAP ISO 2 CLOSE CMD | DPC
53 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | DISCONNECTOR 1 PHASE DISAGREEMENT | SPS
54 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | GENERAL ALARM | SPS
55 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS DISCONNECTOR ALARM | SPS
56 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | DISCONNECTOR 2 PHASE DISAGREEMENT | SPS
57 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | GENERAL ALARM | SPS
58 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR UNBALANCE ALARM | SPS
59 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR UNBALANCED TRIP | SPS |  | FOR BOTH HIGH SET AND LOW SET (IF AVAILABLE)
60 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR OVERLOAD ALARM | SPS
61 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR OVERLOAD TRIP | SPS
62 | …KV | XXXXXX | BAY NO | FSC | BAY NO-MOV | MOV TRIP | SPS
63 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM FAIL-1 | SPS
64 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM FAIL-2 | SPS
65 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | SIGNAL TRANSMISSION POWER FAIL | SPS
66 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MASTER TRIP | SPS
67 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | GPS TIME SYNC FAIL | SPS
68 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | DIRECT TRIP RECEIVE | SPS
69 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | COMMUNICATION CHANNEL FAIL | SPS
70 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | BYPASS CAP ISO 2 OPERATION INTERLOCK | SPS
71 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MASTER TRIP RST | SPC
72 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MOV FAIL | SPS |  | COMMON- R-PH,Y-PH,B-PH
73 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | KIOSK TEMP | AI
74 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL SYSTEM 1 HARDWARE ALARM | SPS |  | Group Alarm
75 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 1 HARDWARE ALARM | SPS |  | Group Alarm
76 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM 1 COMMUNICATION FAULT | SPS |  | Group Alarm
77 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 1 MEASURING SYSTEM WARNING | SPS |  | Group Alarm
78 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL SYSTEM 2 HARDWARE ALARM | SPS |  | Group Alarm
79 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 2 HARDWARE ALARM | SPS |  | Group Alarm
80 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM 2 COMMUNICATION FAULT | SPS |  | Group Alarm
81 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 2 MEASURING SYSTEM WARNING | SPS |  | Group Alarm
82 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM POWER SUPPLY ALARM | SPS |  | Group Alarm
83 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM REDUNDANCY DISTURBED | SPS |  | Group Alarm
84 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | EARTH SWITCH 1 ALARM | SPS |  | Group Alarm
85 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | EARTH SWITCH 2 ALARM | SPS |  | Group Alarm
86 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | DISCONNECTOR SWITCH 1 ALARM | SPS |  | Group Alarm
87 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | DISCONNECTOR SWITCH 2 ALARM | SPS |  | Group Alarm
88 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | LINE EARTH SWITCH ALARM | SPS |  | Group Alarm
89 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | BYPASS BREAKER ALARM | SPS |  | Group Alarm
90 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MAIN BYPASS SWITCH ALARM | SPS |  | Group Alarm
91 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | LINE SIDE 1: DE-ENERGIZED | SPS
92 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | LINE SIDE 2: DE-ENERGIZED | SPS
93 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER LOCAL/REMOTE CONTROL | SPS
94 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER MAIN CLOSING COIL UNHEALTHY | SPS
95 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER BACKUP CLOSING COIL UNHEALTHY | SPS
96 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | FIRE FIGHTING SYSTEM: ALARM | SPS
97 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV OVERLOAD | SPS
98 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV TEMPERATURE TRIP | SPS
99 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV TEMPERATURE GRADIENT LOW SET | SPS
100 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV TEMPERATURE GRADIENT HIGH SET | SPS
101 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV UNBALANCE | SPS
102 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV HIGH CURRENT | SPS
103 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP FAILED TO TRIGGER | SPS
104 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP DELAYED TRIGGER | SPS
105 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP PROLONGED CONDUCTION | SPS
106 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP SELF TRIGGER | SPS
107 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP TRIGGER (R,Y,B) | SPS |  | R,Y,B Phase to be combined
108 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: BYPASS BREAKER FAIL | SPS
109 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: PREVENT REINSERTION ACTIVE | SPS
110 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: PERMANENT BYPASS | SPS
111 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: TEMPORARY BYPASS PHASE(R,Y,B) | SPS |  | R,Y,B Phase to be combined
112 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: REINSERTION | SPS
113 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: LINE TRIP | SPS
114 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV OVERLOAD | SPS
115 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV TEMPERATURE TRIP | SPS
116 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV TEMPERATURE GRADIENT LOW SET | SPS
117 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV TEMPERATURE GRADIENT HIGH SET | SPS
118 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV UNBALANCE | SPS
119 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV HIGH CURRENT | SPS
120 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP FAILED TO TRIGGER | SPS
121 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP DELAYED TRIGGER | SPS
122 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP PROLONGED CONDUCTION | SPS
123 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP SELF TRIGGER | SPS
124 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP TRIGGER (R,Y,B) | SPS |  | R,Y,B Phase to be combined
125 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: BYPASS BREAKER FAIL | SPS
126 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: PREVENT REINSERTION ACTIVE | SPS
127 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: PERMANENT BYPASS | SPS
128 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: TEMPORARY BYPASS PHASE(R,Y,B) | SPS |  | R,Y,B Phase to be combined
129 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: REINSERTION | SPS
130 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: LINE TRIP | SPS

## FSC SIGNALS-SIEMENS (hidden)
S. No. | VOLT. LEVEL | BAY NAME | BAY NUM. | FEEDER TYPE | DEVICE IDENTIFICATION | POINT DESCRIPTION | DATA TYPE | IEC 104 ADDRESS | REMARK
1 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB OPEN/CLOSE STATUS | DPS
3 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR-RPh | BPCB R PHASE OPEN/CLOSE STATUS | DPS
5 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR-YPh | BPCB Y PHASE OPEN/CLOSE STATUS | DPS
7 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR-Bph | BPCB B PHASE OPEN/CLOSE STATUS | DPS
9 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS ISOLATOR OPEN/CLOSE STATUS | DPS
10 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | ISOLATOR 1 OPEN/CLOSE STATUS | DPS
11 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | ISOLATOR 2 OPEN/CLOSE STATUS | DPS
12 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES1 | EARTH SWITCH 1 OPERATION INTERLOCK | SPS
13 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES2 | EARTH SWITCH 2 OPERATION INTERLOCK | SPS
14 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES1 | EARTH SWITCH 1 OPEN/CLOSE STATUS | DPS
15 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES2 | EARTH SWITCH 2 OPEN/CLOSE STATUS | DPS
16 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE DE-ENRGIZED | SPS
17 | …KV | XXXXXX | BAY NO | FSC | BAY NO | FAULT TO PLATFORM TRIP-1/2 | SPS
18 | …KV | XXXXXX | BAY NO | FSC | BAY NO | PERMANENT BYPASS | SPS
19 | …KV | XXXXXX | BAY NO | FSC | BAY NO | MOV TEMPERATURE R PHASE | AI
20 | …KV | XXXXXX | BAY NO | FSC | BAY NO | MOV TEMPERATURE Y PHASE | AI
21 | …KV | XXXXXX | BAY NO | FSC | BAY NO | MOV TEMPERATURE B PHASE | AI
22 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR R PHASE CURRENT | AI
23 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR Y PHASE CURRENT | AI
24 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR B PHASE CURRENT | AI
25 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR R PHASE UNBALANCED CURRENT | AI
26 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR Y PHASE UNBALANCED CURRENT | AI
27 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR B PHASE UNBALANCED CURRENT | AI
28 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE CT CURRENT R-PH | AI
29 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE CT CURRENT Y-PH | AI
30 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE CT CURRENT B-PH | AI
31 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB STATUS DISCREPANCY | SPS
32 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB AUX CONTACT DISCORDANCE | SPS
33 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | GENRAL LOCKOUT/MIN OIL PRESSURE LOCKOUT | SPS
34 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB POLE DISCREPANCY | SPS
35 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB DC 1/2 FAIL | SPS
36 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB LOSS OF SF6 | SPS
37 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | 1POLE REINSERTION DURING AR | SPS
38 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER FAIL TO OPEN | SPS |  | COMMON- R-PH,Y-PH,B-PH FAIL TO OPEN
39 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER SWITCHWED WITHOUT COMMAND | SPS
40 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER FAIL TO CLOSE | SPS |  | COMMON- R-PH,Y-PH,B-PH FAIL TO CLOSE
41 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS CB SPRING DISCHARGE/FAILURE | SPS
42 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB OPEN CMD | DPC
43 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB CLOSE CMD | DPC
44 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB OPERATION INTERLOCK | SPS
45 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS OPEN CMD | DPC
46 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS CLOSE CMD | DPC
47 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS OPERATION INTERLOCK | SPS
48 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | BYPASS CAP ISO 1 OPEN CMD | DPC
49 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | BYPASS CAP ISO 1 CLOSE CMD | DPC
50 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | BYPASS CAP ISO 1 OPERATION INTERLOCK | SPS
51 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | BYPASS CAP ISO 2 OPEN CMD | DPC
52 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | BYPASS CAP ISO 2 CLOSE CMD | DPC
53 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | DISCONNECTOR 1 PHASE DISAGREEMENT | SPS
54 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | GENERAL ALARM | SPS
55 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS DISCONNECTOR ALARM | SPS
56 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | DISCONNECTOR 2 PHASE DISAGREEMENT | SPS
57 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | GENERAL ALARM | SPS
58 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR UNBALANCE ALARM | SPS
59 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR UNBALANCED TRIP | SPS |  | FOR BOTH HIGH SET AND LOW SET (IF AVAILABLE)
60 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR OVERLOAD ALARM | SPS
61 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR OVERLOAD TRIP | SPS
62 | …KV | XXXXXX | BAY NO | FSC | BAY NO-MOV | MOV TRIP | SPS
63 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM FAIL-1 | SPS
64 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM FAIL-2 | SPS
65 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | SIGNAL TRANSMISSION POWER FAIL | SPS
66 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MASTER TRIP | SPS
67 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | GPS TIME SYNC FAIL | SPS
68 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | DIRECT TRIP RECEIVE | SPS
69 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | COMMUNICATION CHANNEL FAIL | SPS
70 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | BYPASS CAP ISO 2 OPERATION INTERLOCK | SPS
71 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MASTER TRIP RST | SPC
72 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MOV FAIL | SPS |  | COMMON- R-PH,Y-PH,B-PH
73 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | KIOSK TEMP | AI
74 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL SYSTEM 1 HARDWARE ALARM | SPS |  | Group Alarm
75 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 1 HARDWARE ALARM | SPS |  | Group Alarm
76 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM 1 COMMUNICATION FAULT | SPS |  | Group Alarm
77 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 1 MEASURING SYSTEM WARNING | SPS |  | Group Alarm
78 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL SYSTEM 2 HARDWARE ALARM | SPS |  | Group Alarm
79 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 2 HARDWARE ALARM | SPS |  | Group Alarm
80 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM 2 COMMUNICATION FAULT | SPS |  | Group Alarm
81 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 2 MEASURING SYSTEM WARNING | SPS |  | Group Alarm
82 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM POWER SUPPLY ALARM | SPS |  | Group Alarm
83 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM REDUNDANCY DISTURBED | SPS |  | Group Alarm
84 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | EARTH SWITCH 1 ALARM | SPS |  | Group Alarm
85 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | EARTH SWITCH 2 ALARM | SPS |  | Group Alarm
86 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | DISCONNECTOR SWITCH 1 ALARM | SPS |  | Group Alarm
87 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | DISCONNECTOR SWITCH 2 ALARM | SPS |  | Group Alarm
88 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | LINE EARTH SWITCH ALARM | SPS |  | Group Alarm
89 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | BYPASS BREAKER ALARM | SPS |  | Group Alarm
90 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MAIN BYPASS SWITCH ALARM | SPS |  | Group Alarm
91 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | LINE SIDE 1: DE-ENERGIZED | SPS
92 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | LINE SIDE 2: DE-ENERGIZED | SPS
93 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER LOCAL/REMOTE CONTROL | SPS
94 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER MAIN CLOSING COIL UNHEALTHY | SPS
95 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER BACKUP CLOSING COIL UNHEALTHY | SPS
96 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | FIRE FIGHTING SYSTEM: ALARM | SPS
97 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV OVERLOAD | SPS
98 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV TEMPERATURE TRIP | SPS
99 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV TEMPERATURE GRADIENT LOW SET | SPS
100 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV TEMPERATURE GRADIENT HIGH SET | SPS
101 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV UNBALANCE | SPS
102 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV HIGH CURRENT | SPS
103 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP FAILED TO TRIGGER | SPS
104 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP DELAYED TRIGGER | SPS
105 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP PROLONGED CONDUCTION | SPS
106 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP SELF TRIGGER | SPS
107 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP TRIGGER (R,Y,B) | SPS |  | R,Y,B Phase to be combined
108 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: BYPASS BREAKER FAIL | SPS
109 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: PREVENT REINSERTION ACTIVE | SPS
110 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: PERMANENT BYPASS | SPS
111 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: TEMPORARY BYPASS PHASE(R,Y,B) | SPS |  | R,Y,B Phase to be combined
112 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: REINSERTION | SPS
113 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: LINE TRIP | SPS
114 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV OVERLOAD | SPS
115 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV TEMPERATURE TRIP | SPS
116 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV TEMPERATURE GRADIENT LOW SET | SPS
117 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV TEMPERATURE GRADIENT HIGH SET | SPS
118 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV UNBALANCE | SPS
119 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV HIGH CURRENT | SPS
120 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP FAILED TO TRIGGER | SPS
121 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP DELAYED TRIGGER | SPS
122 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP PROLONGED CONDUCTION | SPS
123 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP SELF TRIGGER | SPS
124 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP TRIGGER (R,Y,B) | SPS |  | R,Y,B Phase to be combined
125 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: BYPASS BREAKER FAIL | SPS
126 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: PREVENT REINSERTION ACTIVE | SPS
127 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: PERMANENT BYPASS | SPS
128 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: TEMPORARY BYPASS PHASE(R,Y,B) | SPS |  | R,Y,B Phase to be combined
129 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: REINSERTION | SPS
130 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: LINE TRIP | SPS

## FSC
NTAMC TYPICAL SIGNALS FOR FSC
FSC PROTECTION SIGNALS |  |  | BYPASS CB SIGNALS
S.No | SIGNAL NAME | TYPE | S.No | SIGNAL NAME | TYPE
1 | SYSTEM 1: MOV OVERLOAD | SPS | 1 | BPCB STATUS DISCREPANCY | SPS
2 | SYSTEM 1: MOV TEMPERATURE TRIP | SPS | 2 | BPCB AUX CONTACT DISCORDANCE | SPS
3 | SYSTEM 1: MOV TEMPERATURE GRADIENT LOW SET | SPS | 3 | GENRAL LOCKOUT/MIN OIL PRESSURE LOCKOUT | SPS
4 | SYSTEM 1: MOV TEMPERATURE GRADIENT HIGH SET | SPS | 4 | BPCB POLE DISCREPANCY | SPS
5 | SYSTEM 1: MOV UNBALANCE | SPS | 5 | BPCB DC 1/2 FAIL | SPS
6 | SYSTEM 1: MOV HIGH CURRENT | SPS | 6 | BPCB LOSS OF SF6 | SPS
7 | SYSTEM 1: SPARK GAP FAILED TO TRIGGER | SPS | 7 | 1 POLE REINSERTION DURING AR | SPS
8 | SYSTEM 1: SPARK GAP DELAYED TRIGGER | SPS | 8 | BYPASS BREAKER FAIL TO OPEN | SPS
9 | SYSTEM 1: SPARK GAP PROLONGED CONDUCTION | SPS | 9 | BYPASS BREAKER SWITCHWED WITHOUT COMMAND | SPS
10 | SYSTEM 1: SPARK GAP SELF TRIGGER | SPS | 10 | BYPASS BREAKER FAIL TO CLOSE | SPS
11 | SYSTEM 1: SPARK GAP TRIGGER (R,Y,B) | SPS | 11 | BYPASS CB SPRING DISCHARGE/FAILURE | SPS
12 | SYSTEM 1: BYPASS BREAKER FAIL | SPS | 12 | BYPASS BREAKER LOCAL/REMOTE CONTROL | SPS
13 | SYSTEM 1: PREVENT REINSERTION ACTIVE | SPS | 13 | BYPASS BREAKER MAIN CLOSING COIL UNHEALTHY | SPS
14 | SYSTEM 1: PERMANENT BYPASS | SPS | 14 | BYPASS BREAKER BACKUP CLOSING COIL UNHEALTHY | SPS
15 | SYSTEM 1: TEMPORARY BYPASS PHASE(R,Y,B) | SPS | NOTE- 1)CB Status, Command and Interlock are also required
16 | SYSTEM 1: REINSERTION | SPS
17 | SYSTEM 1: LINE TRIP | SPS
18 | SYSTEM 1: BYPASS PLATFORM PROTECTION | SPS | ISOLATOR SIGNALS
19 | SYSTEM 1: BYPASS GAP PROTECTION | SPS | S.No | SIGNAL NAME | TYPE
20 | SYSTEM 1: CAPACITOR UNBALANCE ALARM | SPS | 1 | DS-DISCONNECTOR 1 PHASE DISAGREEMENT | SPS
21 | SYSTEM 1: CAPACITOR UNBALANCED TRIP | SPS | 2 | DS-GENERAL ALARM | SPS
22 | SYSTEM 1: CAPACITOR OVERLOAD ALARM | SPS | 3 | MBS-BYPASS DISCONNECTOR ALARM | SPS
23 | SYSTEM 1: CAPACITOR OVERLOAD TRIP | SPS | NOTE- 1)Isolator Status, Command and Interlock are also required
24 | SYSTEM 1: MOV TRIP | SPS
25 | SYSTEM 1: FAULT TO PLATFORM TRIP-1/2 | SPS
26 | SYSTEM 1: DC SUPPLY FAIL | SPS
27 | SYSTEM1: EXTERNAL BYPASS | SPS | EARTH SWITCH SIGNALS
28 | LINE DE-ENRGIZED | SPS | S.No | SIGNAL NAME | TYPE
29 | PROTECTION SYSTEM FAIL/BLOCKED-1 | SPS | 1 | EARTH SWITCH 1 ALARM | SPS
30 | PROTECTION SYSTEM FAIL/BLOCKED-2 | SPS | NOTE- 1)Earth Switch Status and Interlock are also required
31 | SIGNAL TRANSMISSION POWER FAIL | SPS
32 | MASTER TRIP | SPS
33 | DIRECT TRIP RECEIVE | SPS | ANALOG SIGNALS
34 | COMMUNICATION CHANNEL FAIL | SPS | S.No | SIGNAL NAME | TYPE
35 | MOV FAIL | SPS | 1 | MOV TEMPERATURE R PHASE | AI
36 | GPS TIME SYNC FAIL | SPS | 2 | MOV TEMPERATURE Y PHASE | AI
37 | CONTROL SYSTEM 1 HARDWARE ALARM | SPS | 3 | MOV TEMPERATURE B PHASE | AI
38 | PROTECTION SYSTEM 1 HARDWARE ALARM | SPS | 4 | CAPACITOR R PHASE CURRENT | AI
39 | CONTROL & PROTECTION SYSTEM 1 COMMUNICATION FAULT | SPS | 5 | CAPACITOR Y PHASE CURRENT | AI
40 | PROTECTION SYSTEM 1 MEASURING SYSTEM WARNING | SPS | 6 | CAPACITOR B PHASE CURRENT | AI
41 | CONTROL & PROTECTION SYSTEM POWER SUPPLY ALARM | SPS | 7 | CAPACITOR R PHASE UNBALANCED CURRENT | AI
42 | CONTROL & PROTECTION SYSTEM REDUNDANCY DISTURBED | SPS | 8 | CAPACITOR Y PHASE UNBALANCED CURRENT | AI
43 | LINE SIDE 1: DE-ENERGIZED | SPS | 9 | CAPACITOR B PHASE UNBALANCED CURRENT | AI
44 | LINE SIDE 2: DE-ENERGIZED | SPS | 10 | LINE CT CURRENT R-PH | AI
45 | FIRE FIGHTING SYSTEM: ALARM | SPS | 11 | LINE CT CURRENT Y-PH | AI
46 | PROTECTION SYSTEM 1 MEASURING SYSTEM WARNING | SPS | 12 | LINE CT CURRENT B-PH | AI
47 | LOCAL CONTROL ROOM TEMPERATURE ALARM | SPS | 13 | KIOSK TEMP | AI
48 | TFR FAULT | SPS | 14 | MOV CURRENT R PHASE | AI
49 | PERMANENT /MONITORING LOCKOUT DUE TO C&P SYSTEM | SPS | 15 | MOV CURRENT Y PHASE | AI
NOTE- 1)S.No. 1-27 to be taken for SYSTEM-2 also 2) S.No. 37-40 to be taken for Control and Protection System-2 also |  |  | 16 | MOV CURRENT B PHASE | AI
|  |  | 17 | MOV BRANCH CURRENT R PHASE | AI
|  |  | 18 | MOV BRANCH CURRENT Y PHASE | AI
|  |  | 19 | MOV BRANCH CURRENT B PHASE | AI
|  |  | 20 | SPARK GAP CURRENT R PHASE | AI
|  |  | 21 | SPARK GAP CURRENT Y PHASE | AI
|  |  | 22 | SPARK GAP CURRENT B PHASE | AI
|  |  | 23 | PLATFORM CURRENT R PHASE | AI
|  |  | 24 | PLATFORM CURRENT Y PHASE | AI
|  |  | 25 | PLATFORM CURRENT B PHASE | AI
NOTE- If any other signal is required for remote operation as per site condition, it needs to be incorporated in final signal list.