## HVDC
NTAMC SIGNALS FOR HVDC SUBSTATION
BIPOLE |  |  | BACK TO BACK |  |  | VSC
S.No | SIGNAL NAME | TYPE | S.No | SIGNAL NAME | TYPE | SL. No. | SIGNAL NAME | TYPE
1 | POLE-1 DC POWER | AI | 1 | POLE-1 DC POWER | AI | 1 | SM-1 DC POWER | AI
2 | POLE-1 DC VOLTAGE | AI | 2 | POLE-1 DC VOLTAGE | AI | 2 | SM-1 DC LINE VOLTAGE | AI
3 | POLE-1 DC CURRENT | AI | 3 | POLE-1 DC CURRENT | AI | 3 | SM-1 DC CURRENT | AI
4 | POLE-1 FIRING/EXTINCTION ANGLE | AI | 4 | POLE-1 FIRING/EXTINCTION ANGLE | AI | 4 | SM 1 ACTIVE POWER | AI
5 | POLE-1 GROUND/METALLIC RETURN | SPS | 5 | POLE-1 BLOCKED/DEBLOCKED | SPS | 5 | SM-1 REACTIVE POWER | AI
6 | POLE-1 POWER DIRECTION POWER FLOW DIRECTION NORMAL/REVERSE | SPS | 6 | POLE 1 VBE/VCU SUMMARY FAULT | SPS | 6 | SM-1 ACTIVE POWER CAPABILITY | AI
7 | POLE-1 BLOCKED/DEBLOCKED | SPS | 7 | POLE 1 VALVE HALL SUMMARY TRIP | SPS | 7 | SM-1 RECATIVE POWER CAPABILITY | AI
8 | POLE-1 OVERLOAD IN USE | SPS | 8 | POLE-1 CONVERTER TRANSFORMER SUMMARY FAULT | SPS | 8 | SM-1 POWER FLOW DIRECTION FORWARD/REVERSE | SPS
9 | POLE-1 POWER RAMP IN PROGRESS | SPS | 9 | POLE-1 VALVE COOLING SYSTEM FAULT | SPS | 9 | SM-1 COUPLED | SPS
10 | POLE-1 DC VOLTAGE FULL/REDUCED | SPS | 10 | POLE-1 VALVE COOLING TRIP | SPS | 10 | SM-1 DECOUPLED | SPS
11 | POLE-1 RUNBACK ACTIVATED INDICATION | SPS | 11 | POLE-1 VESDA TRIP | SPS | 11 | SM-1 DC LINE FAULT RECOVERY SEQUENCE IN PROGRESS | SPS
12 | POLE-1 POWER SWING MODULATION ON/OFF | SPS | 12 | POLE-1 EMERGENCY SWITCH OFF | SPS | 12 | SM-1 AC BYPASS AREA SUMMARY FAULT | SPS
13 | POLE-1 FREQUENCY CONTROL ON/OFF | SPS | 13 | POLE-1 POWER DIRECTION | SPS | 13 | SM-1 COUPLING TRANSFORMER SUMMARY FAULT | SPS
14 | POLE-1 FREQUENCY CONTROL ACTIVATED | SPS | 14 | POLE-1 POWER SWING MODULATION ON/OFF | SPS | 14 | SM-1 STAR POINT AREA SUMMARY FAULT | SPS
15 | POLE-1 DC LINE TRANSIENT FAULT | SPS | 15 | POLE-1 FREQUENCY CONTROL ON/OFF | SPS | 15 | SM-1 VALVE HALL SUMMARY FAULT | SPS
16 | POLE-1 IN P/I MODE | SPS | 16 | POLE-1 FREQUENCY CONTROL ACTIVATED | SPS | 16 | SM-1 VALVE COOLING SYSTEM SUMMARY FAULT | SPS
17 | POLE 1 VBE/VCU SUMMARY FAULT | SPS | 17 | POLE-1 OPERATION AT POWER/CURRENT LIMIT | SPS | 17 | SM-1 VALVE COOLING TRIP | SPS
18 | POLE 1 VALVE HALL SUMMARY TRIP | SPS | 18 | BIPOLE DC POWER | AI | 18 | SM-1 DC YARD SUMMARY FAULT | SPS
19 | POLE-1 CONVERTER TRANSFORMER SUMMARY FAULT | SPS | 19 | STABILITY FUNCTION ENABLED | SPS | 19 | SM-1 VESDA/ARC PROTECTION TRIP | SPS
20 | POLE-1 VALVE COOLING SYSTEM FAULT | SPS | 20 | ABSOLUTE MINIMUM FILTER CRITERIA NOT FULFILLED | SPS | 20 | SM-1 LINE FAULT PROTECTION OPERATED | SPS
21 | POLE-1 VALVE COOLING TRIP | SPS | 21 | AUTOMATIC BIPOLE POWER CONTROL | SPS | 21 | SM-1 RECONFIGURATION TO DECOUPLED SEQUENCE IN PROGRESS | SPS
22 | POLE-1 DC YARD SUMMARY FAULT | SPS | 22 | RPC ON/OFF | SPS | 22 | SM-1 RECONFIGURATION TO ISLANDED SEQUENCE IN PROGRESS | SPS
23 | POLE-1 VESDA TRIP | SPS | 23 | RPC AUTO/MANUAL | SPS | 23 | SM-1 EMERGENCY SWITCH OFF | SPS
24 | POLE-1 EMERGENCY SWITCH OFF | SPS | NOTE- Signals from 1-17 are to be repeated for all Pole |  |  | 24 | SM-1 POD ENABLED | SPS
25 | POLE-1 DC FILTER CONNECTED/DISCONNECTED | SPS |  |  |  | 25 | SM-1 RUN BACK | SPS
26 | POLE-1 DC LINE FAULT | SPS |  |  |  | 26 | SM-1 FREQUENCY CONTROL | SPS
27 | POLE-1 OPERATION AT POWER/CURRENT LIMIT | SPS |  |  |  | 27 | MULTI LINK POWER ORDER | AI
28 | BIPOLE DC POWER | AI |  |  |  | 28 | SPS ACTIVATED | SPS
29 | NEUTRAL AREA SUMMARY TRIP | SPS |  |  |  | 29 | ACTIVE POWER MULTI LINK OPERATION SELECTED | SPS
30 | ABSOLUTE MINIMUM FILTER CRITERIA NOT FULFILLED | SPS |  |  |  | 30 | ACTIVE POWER SINGLE LINK OPERATION SELECTED | SPS
31 | DMR 1/2 CONNECTED | SPS |  |  |  | 31 | REACTIVE POWER MULTI LINK OPERATION SELECTED | SPS
32 | AUTOMATIC BIPOLE POWER CONTROL | SPS |  |  |  | 32 | REACTIVE POWER SINGLE LINK OPERATION SELECTED | SPS
33 | MASTER STATION STATION A/ STATION B | SPS |  |  |  | NOTE- Signals from 1-26 are to be repeated for Symmetric Monopole
34 | RPC ON/OFF | SPS
35 | RPC AUTO/MANUAL | SPS
36 | STABILITY FUNCTION ENABLED | SPS
NOTE- Signals from 1-27 are to be repeated for all Pole
AC Filter
S.No | SIGNAL NAME | TYPE
1 | AC FILTER BANK MVAR | AI
2 | FILTER PROTECTION TRIP | SPS
NOTE- 1) No. of Signals as per availability of AC Filters
NOTE- 1)For AC Side bays and convertor transformer, Typical datalist for AC Substation is to be referrred. 2) If any other signal is required for remote operation as per site condition, it needs to be incorporated in final signal list. 3)DPS for all HVDC Switchgear/Equipment to be added in NTAMC signal list for HVDC Station during detailed Engineering. 4) The list can be a basic guideline which has to be reviewed during detailed engineering and any modifications/new signal are required the same to be incorporated accordingly
NOTE- If any other signal is required for remote operation as per site condition, it needs to be incorporated in final signal list.