## Proposed list for TS
NTAMC TYPICAL SIGNALS FOR TS of STATCOM
STATCOM STATION |  |  | MSR/MSC |  |  | AUX-TRAFO
S.No | SIGNAL NAME | TYPE | S.No | SIGNAL NAME | TYPE | S.No | SIGNAL NAME | TYPE
1 | COOLING SYSTEM-1 TRIP | SPS | 1 | MSR-1 MAIN PROTECTION TRIP | SPS | 1 | MAIN PROTECTION TRIP | SPS
2 | COOLING SYSTEM-2 TRIP | SPS | 2 | MSR-1 MAIN LBB PROTECTION TRIP | SPS | 2 | BACKUP PROTECTION TRIP | SPS
3 | STATCOM BOTH STATION CONTROLLER FAILURE TRIP | SPS | 3 | MSR-1 BACKUP PROTECTION TRIP | SPS | 3 | MAIN PROTECTION RELAY FAILURE | SPS
4 | STATION CONTROLLER-1 START | SPS | 4 | MSR-1 BACKUP LBB PROTECTION TRIP | SPS | 4 | BACKUP PROTECTION RELAY FAILURE | SPS
5 | STATION CONTROLLER-1 STOP | SPS | 5 | MSR-1 MAIN PROTECTION RELAY FAILURE | SPS | 5 | TRIP RELAY-A(86A) OPERATED | SPS
6 | STATION CONTROLLER-2 START | SPS | 6 | MSR-1 BACKUP PROTECTION RELAY FAILURE | SPS | 6 | TRIP RELAY-B(86B) OPERATED | SPS
7 | STATION CONTROLLER-2 STOP | SPS | 7 | MSR-1 TRIP RELAY-A(86A) OPERATED | SPS | 7 | BUCHHOLZ RELAY TRIP | SPS
8 | STATCOM STATION RUNNING | SPS | 8 | MSR-1 TRIP RELAY-B(86B) OPERATED | SPS | 8 | WTI TRIP | SPS
9 | STATCOM STATION SEQUENCE FAIULRE | SPS | 9 | MSR-1 TRIP RELAY-A(86A) RESET | SPC | 9 | OTI TRIP | SPS
10 | UNIT-1 CONTROLLER START | SPS | 10 | MSR-1 TRIP RELAY-B(86B) RESET | SPC | 10 | BUCHHOLZ RELAY ALARM | SPS
11 | UNIT-1 CONTROLLER STOP | SPS | 11 | MSR-1 MVAR | AI | 11 | WTI ALARM | SPS
12 | STATCOM UNIT-1 STOPPED | SPS | 12 | MSR-1 PSD ON | DPS | 12 | OTI ALARM | SPS
13 | STATCOM UNIT-1 RUNNING | SPS | 13 | MSR-1 PSD BYPASS | DPS | 13 | TRIP CIRCUIT-1 FAULTY | SPS
14 | STATCOM UNIT-1 SEQUENCE FAIULRE | SPS | NOTE- Same siganals to be taken for MSR-2, MSC-1 & 2 |  |  | 14 | TRIP CIRCUIT-2 FAULTY | SPS
15 | UNIT-2 CONTROLLER START | SPS | STATCOM-1 |  |  | 15 | PRESSURE BLOCKING ALARM | SPS
16 | UNIT-2 CONTROLLER STOP | SPS | S.No | SIGNAL NAME | TYPE | 16 | SF6 GAS LOW ALARM | SPS
17 | STATCOM UNIT-2 STOPPED | SPS | 1 | MAIN PROTECTION TRIP | SPS | 17 | POLE DISCREPANCY ALARM | SPS
18 | STATCOM UNIT-2 RUNNING | SPS | 2 | MAIN LBB PROTECTION TRIP | SPS | 18 | AC FAILURE ALARM | SPS
19 | STATCOM UNIT-2 SEQUENCE FAIULRE | SPS | 3 | STATCOM-1 BOTH UNIT CONTROLLER FAILURE TRIP | SPS | 19 | TRIP RELAY-A(86A) RESET | SPC
20 | ONE KEY START | SPS | 4 | BACKUP PROTECTION TRIP | SPS | 20 | TRIP RELAY-B(86B) RESET | SPC
21 | ONE KEY STOP | SPS | 5 | BACKUP LBB PROTECTION TRIP | SPS | 21 | KW | AI
22 | AUTOMATIC START/STOP SEQUENCE RUNNING | SPS | 6 | MAIN PROTECTION RELAY FAILURE | SPS | 22 | KVAR | AI
23 | AUTOMATIC START/STOP SEQUENCE FAIL | SPS | 7 | BACKUP PROTECTION RELAY FAILURE | SPS | 23 | KVA | AI
24 | (STATION) HV SIDE OVERVOLTAGE TRIP | SPS | 8 | MASTER TRIP RELAY-A(86A) OPERATED | SPS
25 | (STATION) HV SIDE UNDERVOLTAGE TRIP | SPS | 9 | MASTER TRIP RELAY-B(86B) OPERATED | SPS | AUXILIARY
26 | (STATION) HV SIDE OVERCURRENT TRIP | SPS | 10 | STATCOM UNIT-1 CONTROLLER A FAILURE (COMM. FAIL / HW FAIL) | SPS | S.No | SIGNAL NAME | TYPE
27 | (STATION) HV IVT FAIL TRIP | SPS | 11 | STATCOM UNIT-1 CONTROLLER B FAILURE (COMM. FAIL / HW FAIL) | SPS | 1 | UPS-1 BYPASS FAILURE | SPS
28 | EMERGENCY STOP | SPS | 12 | (UNIT-1) COOLING SYSTEM ALARM | SPS | 2 | UPS-1 AC SUPPLY FAILURE | SPS
29 | GROUP MESSAGE : STATION CONTROLLER A FAILURE (COMM. FAIL / HW FAIL) | SPS | 13 | (UNIT-1) COOLING SYSTEM CONTROLLER-A ACTIVE | SPS | 3 | UPS-1 LOAD ON MAINS | SPS
30 | GROUP MESSAGE : STATION CONTROLLER B FAILURE (COMM. FAIL / HW FAIL) | SPS | 14 | (UNIT-1) COOLING SYSTEM CONTROLLER-B ACTIVE | SPS | 4 | UPS-1 LOAD ON MAINTENANCE BYPASS-MODE | SPS
31 | MANUAL Q CONTROL MODE SELECTED | SPS | 15 | (UNIT-1) COOLING SYSTEM CONTROLLER-A FAILURE | SPS | 5 | UPS-1 LOAD ON STATIC BYPASS-MODE | SPS
32 | AUTOMATIC VOLTAGE CONTROL MODE SELECTED | SPS | 16 | (UNIT-1) COOLING SYSTEM CONTROLLER-B FAILURE | SPS | 6 | UPS-1 LOAD ON INVERTER | SPS
33 | NEGATIVE SEQ. VOLTAGE CONTROL ENABLED | SPS | 17 | (UNIT-1) VALVE OVERCURRENT TRIP | SPS | 7 | UPS-1 BATTERY LOW/LOW DC VOLTAGE | SPS
34 | POD CONTROL ENABLE | SPS | 18 | (UNIT-1) COOLING SYSTEM TRIP | SPS | 8 | UPS-1 BATTERY MCCB OFF/TRIP | SPS
35 | SSOD CONTROL ENABLED | SPS | 19 | (UNIT-1) DC CT POWER FAIL | SPS | 9 | UPS-1 TROUBLE COMMON ALARM | SPS
36 | ADAPTIVE GAIN REDUCTION ENABLED | SPS | 20 | (UNIT-1) PHASE CONTROLLER FAILURE TRIP | SPS | 10 | UPS -1 FAN FAILURE | SPS
37 | ADAPTIVE GAIN CLACULATION ENABLED | SPS | 21 | (UNIT-1) VALVE ERROR TRIP | SPS
38 | MSC-1 CONTROL MODE - AUTO. CONTROL SELLECTED | SPS | 22 | (UNIT-1) SUB-MODULE FAILURE OR BYPASSED | SPS | NOTE- 1)NOTE- Same siganals to be taken for UPS-2 2) Other signals are to be taken from Auxiliary typical list.
39 | MSC-1 CONTROL MODE - AUTO. CONTROL SELLECTED | SPS | 23 | (UNIT-1) VALVE HALL-1 TEMPERATURE HIGH TRIP | SPS
40 | MSR-1 CONTROL MODE - AUTO. CONTROL SELLECTED | SPS | 24 | STATCOM UNIT-1 TRIP RELAY-A(86A) RESET | SPC
41 | MSR-2 CONTROL MODE - AUTO. CONTROL SELLECTED | SPS | 25 | STATCOM UNIT-1 TRIP RELAY-B(86B) RESET | SPC
42 | HV BR MAIN BAY CONTROL MODE - AUTO. CONTROL SELLECTED | SPS | 26 | STATCOM UNIT-1 MVAR | AI
43 | HV BR TIE BAY CONTROL MODE - AUTO. CONTROL SELLECTED | SPS | 27 | STATCOM UNIT-1 EMERGENCY STOP | SPC
44 | AHU STATCOM UNIT 1-A RUNNING | SPS | 28 | STATCOM UNIT-1 EMERGENCY STOP STATUS | SPS
45 | AHU STATCOM UNIT 1-B RUNNING | SPS | 29 | STATCOM-1 COOLING SYSTEM COMMAND | CMD
46 | AHU STATCOM UNIT 2-A RUNNING | SPS | 30 | STATCOM-1 COOLING SYSTEM STATUS | SPS
47 | AHU STATCOM UNIT 2-B RUNNING | SPS | 31 | STATCOM-1 READY FOR OPERATION | SPS
48 | V-REF SETTING | AI | 32 | STATCOM-1 SEQUENCE FAILURE | SPS | AVR
49 | SLOPE/DROOP SETTING | AI | 33 | STATCOM-1 SEQUENCE RUNNING | SPS | S.No | SIGNAL NAME | TYPE
50 | DEAD-BAND UP SETTING | AI | 34 | STATCOM-1 PSD ON | DPS | 1 | AVR FAIL ALARM | SPS
51 | DEAD-BAND DOWN SETTING | AI | 35 | STATCOM-1 PSD BYPASS | DPS | 2 | AVR STOP | SPS
52 | Q-REF SETTING | AI | NOTE- Same siganals to be taken for STATCOM-2 |  |  | 3 | AVR Warning ALARM | SPS
53 | CONTROL MODE : MANUAL Q CONTROL / AUTOMATIC VOLTAGE CONTROL | AI_CMD |  |  |  | 4 | AVR Transformer Alarm | SPS
54 | V-REF SETTING | AI_CMD
55 | DEAD-BAND UP SETTING | AI_CMD
56 | DEAD-BAND DOWN SETTING | AI_CMD | GROUND TRANSFORMER
57 | SLOPE/DROOP SETTING | AI_CMD | S.No | SIGNAL NAME | TYPE | TERTIARY TRAFO
58 | Q-REF SETTING | AI_CMD | 1 | MV BUSBAR BACKUP PROTECTION TRIP (GND TRAFO TRIP) | SPS | S.No | SIGNAL NAME | TYPE
59 | POD CONTROL ENABLE | AI_CMD | 2 | BACKUP PROTECTION RELAY FAILURE (GND TRAFO) | SPS | 1 | 33kV AUX. TR PROTECTION TRIP | SPS
60 | SSOD CONTROL ENABLE | AI_CMD | 3 | BUCHHOLZ RELAY TRIP | SPS | 2 | 33kV AUX. TR TRIP RELAY OPERATED | SPS
61 | NEGATIVE SEQ. VOLTAGE CONTROL ENABLE | AI_CMD | 4 | PRD TRIP | SPS | 3 | 33kV AUX. TR CB SF6 Loss Alarm | SPS
62 | ADACTIVE GAIN REDUCTION ENABLE | AI_CMD | 5 | WTI TRIP | SPS | 4 | 33kV AUX. TR CB SF6 Lockout Alarm | SPS
63 | ADACTIVE GAIN CALCULATION ENABLE | AI_CMD | 6 | OTI TRIP | SPS | 5 | 33kV AUX. TR CB Spring Charged | SPS
64 | MSC-1CONTROL MODE - AUTOMATIC / MANUAL | AI_CMD | 7 | BUCHHOLZ RELAY ALARM | SPS | 6 | 33kV AUX. TR CB DC 1/2 Fail Alarm | SPS
65 | MSC-2 CONTROL MODE - AUTOMATIC / MANUAL | AI_CMD | 8 | WTI ALARM | SPS | 7 | 33kV AUX. TR Bucholz Alarm | SPS
66 | MSR-1 CONTROL MODE - AUTOMATIC / MANUAL | AI_CMD | 9 | OTI ALARM | SPS | 8 | 33kV AUX. TR WTI Alarm | SPS
67 | MSR-2 CONTROL MODE - AUTOMATIC / MANUAL | AI_CMD | NOTE- Signals other than Switchgear Status, Interlock and command |  |  | 9 | 33kV AUX. TR OTI Alarm | SPS
68 | HV BR MAIN BAY CONTROL MODE - AUTOMATIC | AI_CMD |  |  |  | 10 | KW | AI
69 | HV BR TIE BAY CONTROL MODE - AUTOMATIC | AI_CMD | MV BUSBAR |  |  | 11 | KVAR | AI
70 | ONE KEY START | SPC | S.No | SIGNAL NAME | TYPE
71 | ONE KEY STOP | SPC | 1 | MV BUS VOLTAGE | AI
72 | TFR TRIGGER CMD | SPS | 2 | MV BUS PROTECTION TRIP | SPS
|  |  | 3 | MV BUS PROTECTION RELAY FAILURE | SPS
NOTE- 1. For 400KV bays, Typical datalist of respective bay is to be referred. 2. For all CB, ISOLATOR and Earthswitch, Typical list of Switchgears to be referred. 3. Grouping of Signals may be done as per site condition. 4. If any other signal is required for remote operation as per site condition, it needs to be incorporated in final signal list. 5. Indexing of Equipments in signal list may be done as per design and availability.
NOTE- If any other signal is required for remote operation as per site condition, it needs to be incorporated in final signal list.