## Sheet1
Clarification-I dated 24.04.2024 for Substation Package: SS128 (GIS) for (i) Up-gradation of 132kV Khliehriat s/s from AIS to GIS under NERES-XXI part A (ii) Extn. of 400 kV Bongaigaon S/S under NERES-XXII . Spec No. -CC/NT/W-GIS/DOM/A06/24/03462
Sl.No. | Document Name | Clause | Details | Bidder Query | POWERGRID Reply
1 | Section Project | 1.1.2 (ii) | De-commissioning of existing 420kV, 2 X 50MVAr bus reactors | We Understand that, The OEM Engineer for Supervison of De - Commissioning of Existing Reactors, Installation of New Owner Supplied Reactor is not in Bidder's Scope. Kindly confirm please. | Provision of Supervision by OEM engineers for Reactors is not envisaged under present scope.
Installation of a new 420kV 1X 125 MVAR bus reactor(OwnerSupplied) in one of the vacated bays after decommissioning of above mentioned 420kV, 2X 50MVAr bus Reactors
One of the existing 2 X 80MVAr Bus Reactors (presently installed in parallel in same bay) may be installed at Bongaigaon (POWERGRID) S/s in other vacated bay after decommissioning of above mentioned 420kV, 2X 50 MVAr Bus Reactor
2 | Section Project | 2.1.1.1. B , c) | CONTROL, RELAY & PROTECTION PANEL: The Scope shall also cover supply of matching Line Current Differential relays, for mounting in existing C&R Panels at remote end Substation by the contractor. Installation and commissioning along with communication, including all interface from existing FODP & Telecom equipment to C&R Panels at remote end stations are under present scope & is deemed to be included in the associated service item in the BPS . | As per clause iii, We Understand that, The OPGW, Approch Cable (Incase TL through OH) & UG FO Cable (incase TL through UG) is not in the Bidder's scope for Communication of Line Differential Relays. Also, Provide the Existing FODP & Telecom Equipments details of Remote End Station for Interface the C&R. Kindly confirm please. | As per the TS, All interface from existing FODP &Telecom equipment to C&R Panel shall be in the scope of contractor including all required material, FO cable etc. Bidder is advised to visit site as per clause 1.4 of Section project.
|  |  |  | Also, matching line differential relay to be supplied at remote end. We understand that our scope is limited to loose supply of line differential relay only. same shall be mounted/ installed in existing CRP only. Bidder scope is limited to testing & commissioning of supplied relay. Any integration of the relay with existing SAS/SCADA/RTU shall not be in Bidder's Scope. Kindly confirm Please. | The present scope of work associated with Line differential protection at remote end are as follow: -Supply, installation , testing and commissioning of Line differential relay - Integrating the relay with existing RTU/SAS. However, the data base upgradation is not envisaged under bidders scope.
3 | Section Project | 2.1.1.1. B , f) | DPC associated with both ends of 132kV lines emanating from Khliehriat (PG) Substations. Cabling between DPC & Communication equipment (for E1 interface) and power cables shall be in present scope. | Kindly provide the Existing Make of DPC & Communication Equipments details to take the Rates from OEM's. | New DPC is to be supplied under present scope of works only. For existing communication equipments, bidder is advised to visit site as per clause 1.4 of Section project. .
4 | Price Schdule - Sch- 1 | SS-128:NERES-XXI-Part-A - Sl.No. 34 ( Fire Protection System) | Diesel Engine driven Hydrant system with Water tank, Pump Room, DG Driven Pump, O/G & U/G piping, Hydrant Points for transformers, buildings, store yard and accessories etc. | We understand that, The Measurement & Payment for Construction of Fire Fighting Pump House, Water Tank will be claimed from Schedule - 3 (Item no - 92 & 93) of Price Schdule. Bidder not consider the Price for Construction of Pump House Water tank in Schedule - 1 (Item no 34) of Price schedule. Kindly confim please. | It is confirmed that the Measurement & Payment for Construction of Fire Fighting Pump House and Water Tank to be claimed from Price Schedule - 3 (Item no - 92 & 93). However excavation, PCC,RCC and reinforcement shall be paid seperately under relevant items of the price Schedule - 3
| Price Schdule - Sch- 3 | SS-128:NERES-XXI-Part-A - Sl.No. 92 ( Civil Works) | FFPH Building - Civil Works All civil works as per drawing and specifications complete, including - brickwork,finishing (externaland internal),windows etc.However, excavation, PCC,RCC and reinforcement shall be paid separately as per BPS
|  | SS-128:NERES-XXI-Part-A - Sl.No. 93 ( Civil Works) | All civil works as per drawing and specification but excluding excavation, PCC, RCC, reinforcement but including finishing (internaland external) etc & all civil works complete in all respect - Water Tank for Fire Fighting Pump House