Statement of Modifications in TS for Package FOTE-07: Communication System Schemes approved in 33rd NCT

| Section & Cl. no | Existing Clause | Modified Clause |
| --- | --- | --- |
| Section-01 Introduction, General Information and General Requirement | 1.8.2 Contractor's Responsibilities and Obligations Clause Added | 1.8.2 Contractor's Responsibilities and Obligations 33. In case, any hardware / software / equipment / component items of the systems supplied under the contract shall reach its End-of-Life (EOL) or End-of-Support (EOS) before Taking Over or scheduled end date of AMC period, the contractor shall replace such item with new Hardware or Software without any financial implication to employer. The contractor shall submit documentary evidence certified by OEM for the validity of End-of-Life/ End-of-Support during detailed engineering phase. |
| Section-02 Network Configuration and Equipment Characteristics | 2.1 Introduction Clause Added | 2.1 Introduction The Contractor shall submit a compliance statement. All changes including upgrade/update in the systems being supplied by the Contractor shall be done by him at his own cost. In case, any additional appliance or third-party hardware or third-party software is required for implementing the recommendation of the auditor, the same shall be provided by the Employer. The contractor shall also be responsible for providing patches/updates for the products supplied under the project. Further all vulnerabilities disclosed by auditor as well as by Govt. agencies / OEM shall be closed on priority. |
| Section-2, Network Configuration and Equipment Characteristics | Cl. 2.2.3.1 System Synchronization The Contractor shall synchronize all the new equipments under the contract using NavIC based reference clock/ GPS Clock. In addition to NavIC/GPS input reference, the synchronization clock must have provision to take input reference coming from other clock. | The Contractor shall synchronize all the new equipments under the contract using NavIC (with failback option to GPS) based time reference clock. In addition to input reference, the synchronization clock must have provision to take input reference coming from other clock. |
| Section-02 Network Configuration and Equipment Characteristics | 2.3.1.1 Functional Requirement If bidder is offering equipment with multifunction cards such as cross-connect or control card with optical interface/SFP or tributary interface, such type of multifunction card shall be considered as Common control card and shall be the part of base equipment. In case optical interface/SFP is embedded with control card, the adequate number of optical interface/ SFPs shall be offered to meet the redundancy requirements of the specifications. Further, main and protection channel shall be terminated on separate cards and there should be no single point of failure. The equipment shall be configurable either as Terminal Multiplexer (TM) as well as ADM with software settings only. (i) STM-4 (MADM) with 3 MSP/5 MSP protected direction. The aggregate interfaces shall be (at least) STM-4 towards at least three/five protected directions (Protected as specified in this specifications). At present the equipment shall be equipped with two (2 ) nos. E1 interface card with minimum 16 interfaces per card & two (2) nos. Fast Ethernet interface card with minimum 8 interfaces per card, as tributaries. The equipment shall provide non blocking cross connect capability of 64 STM-1 (bidirectional) at high order VC-4 level and as well as at low order VC-12 level. (ii) STM-16 (MADM) with 3 MSP/5 MSP protected direction. The aggregate interfaces shall be (at least) STM-16 towards at least three/five protected directions (Protected as specified in this specifications). At present the equipment shall be equipped with two (2 ) nos. E1 interface card with minimum 16 interfaces per card & two (2) nos. Fast Ethernet interface card with minimum 8 interfaces per card, as tributaries. Gigabit Ethernet (optical/electrical) interface shall also be provided if specified in BPS. The equipment shall provide non blocking cross connect capability of 256 STM-1 (bidirectional) at high order VC-4 level and 128 STM-1 (bi-directional) at low order VC-12 level. | If bidder is offering equipment with multifunction cards such as cross-connect or control card with optical interface/SFP or tributary interface, such type of multifunction card shall be considered as Common control card and shall be the part of base equipment. In case optical interface/SFP is embedded with control card, the adequate number of optical interface/SFPs shall be offered to meet the redundancy requirements of the specifications. Further, main and protection channel shall be terminated on separate cards and there should be no single point of failure. Further, to meet the aggregate direction requirements (MSP protected) as per BoQ, the bidder can offer one or more equipment. However, incase multiple equipment are offered, all common cards such as control cards, power supply card, optical card etc. shall be provided with redundancy as required in this specification. The equipment shall be configurable either as Terminal Multiplexer (TM) as well as ADM with software settings only. - STM-4 (MADM) with 3 MSP/5 MSP protected direction. The aggregate interfaces shall be (at least) STM-4 towards at least three/five protected directions (Protected as specified in this specifications). The directions (MSP protected) to be offered as per BoQ. At present the equipment shall be equipped with two (2 ) nos. E1 interface card with minimum 16 interfaces per card & two (2) nos. Fast Ethernet interface card with minimum 8 interfaces per card, as tributaries. The equipment shall provide non blocking cross connect capability of 64 STM-1 (bi-directional) at high order VC-4 level and as well as at low order VC-12 level. - STM-16 (MADM) with 3 MSP/5 MSP protected direction. The aggregate interfaces shall be (at least) STM-16 towards at least three/five protected directions (Protected as specified in this specifications). The directions (MSP protected) to be offered as per BoQ. At present the equipment shall be equipped with two (2 ) nos. E1 interface card with minimum 16 interfaces per card & two (2) nos. Fast Ethernet interface card with minimum 8 interfaces per card, as tributaries. Gigabit Ethernet (optical/electrical) interface shall also be provided if specified in BPS. The equipment shall provide non blocking cross connect capability of 256 STM-1 (bi-directional) at high order VC-4 level and 128 STM-1 (bi-directional) at low order VC-12 level. - STM-64 XC (100G XC) The equipment shall support STM-64 (at least 2 MSP), STM-16 (at least 5 MSP). The directions (MSP protected) to be offered as per BoQ. At present the equipment shall be supported with Minimum 2 nos of Gbe 1000 Mbps Ports, Minimum 8 nos of FE 10/100 Mbps ports per card , and Minimum 16 E1 interfaces per card or a combination of above. The Cross Connect Equipment shall be capable of high order level Cross Connection of at least 640 STM1 equivalent (bi-directional). The Equipment shall be capable of low order (VC-3 and VC-12) level single stage Cross Connection upto 512 STM-1s (bi-directional) equivalent out of total 640 STM-1s. Bidder to supply above mentioned cards in the equipment as per BOQ. |
| Section-02 Network Configuration and Equipment Characteristics | 2.8 Craft Terminal Each equipment on the fibre optic communication network shall include provision for connecting a portable personal computer (PC) to be known as craft terminal to support local commissioning and maintenance activities. Through the use of this PC and local displays/controls, the operator shall be able to: a. Change the configuration of the station & the connected NEs. b. Perform tests c. Get detailed fault information The craft terminal shall be connected to the interface available in the communication equipment. Portable (laptop) computers (Craft terminals), each complete with necessary system and application software to support the functions listed above, shall be supplied to the employer as per BOQ. | Clause Deleted |
| Section-02 Network Configuration and Equipment Characteristics | 2.9.1 Master Processor, Server/Workstation and Craft Terminal The server shall have minimum configuration of 2.4 GHz Quad-Core processor (same will be acceptable with turbo boost option also), 8 GB RAM, DVD-RW drive, redundant 320 GB internal Hard Disk Drive, 101-Enhanced style keyboards, mouse, serial, USB(2.0) ports and hot swap redundant power supply. VDUs shall be 19" TFT active matrix color LCD with a minimum resolution of 1024 X 768. Appropriate network drive card shall also be provided wherever required. However, the internal hard disk drive for the server shall be redundant and all the data shall be mirrored. Further, the TMN software shall support data mirroring on redundant disk drives. The workstation shall have minimum configuration of 3 GHz Core 2 Duo (same will be acceptable with turbo boost option also), 8 GB RAM, DVD-RW drive, 500 GB Hard Disk Drive, 101-Enhanced style keyboards, mouse, serial and USB (2.0) ports. VDUs shall be 19" TFT active matrix color LCD with a minimum resolution of 1024 X 768. Appropriate network drive card shall also be provided wherever required. CPU enclosures shall be desktop type and shall include available expansion slots except for the Craft Terminal which shall be a laptop. The craft terminal shall have minimum configuration of 2.4 GHz (same will be acceptable with turbo boost option also), 8 GB RAM, 256 MB Video Graphics Memory, , 320 GB Hard Disk Drive, keyboard, mouse/trackball etc., serial/USB (2.0) ports to accommodate printers, and a battery back-up of at least 3 hours. VDUs shall be 15" TFT active matrix color LCD/LED with a minimum resolution of 1024 X 768. | 2.9.1 Master Processor, Server/Workstation and Craft Terminal The server shall have minimum configuration of 2.4 GHz, 16 cores, 128 GB RAM, DVD-RW drive, redundant 480 GB internal SSD Drive (RAID-I), 101-Enhanced style keyboards, mouse, serial, USB ports and hot swap redundant power supply. VDUs shall be approximately more than 23.8" TFT color display with a minimum resolution of 1920 X 1080. Appropriate network drive card shall also be provided wherever required. Further, the TMN software shall support data mirroring on redundant disk drives. The workstation shall have minimum configuration of 3 GHz, 8 core, 64 GB RAM, 500 GB SSD, 101-Enhanced style keyboards, mouse, serial, USB ports. VDUs shall be approximately more than 23.8" TFT color display with a minimum resolution of 1920 X 1080. Appropriate network drive card shall also be provided wherever required. CPU enclosures shall be desktop type and shall include available expansion slots except for the Craft Terminal which shall be a laptop.. The craft terminal shall have minimum configuration of 2 GHz, 4 cores, 16 GB RAM, 500 GB Hard Disk Drive, keyboard, mouse/ trackball etc, serial/ USB ports to accommodate printers and a battery back up of at least 3 hours. VDUs shall be 14" approximately with TFT color display with a minimum resolution of 1920 X 1080. The configurations mentioned for server & workstation & craft terminal are minimum and the same shall be finalized during detailed engineering as per latest industrial standards. |
| Section-02 Network Configuration and Equipment Characteristics | - PABX # 2.11.1 General The bidder shall offer PABX equipment from a manufacturer who has been designing & manufacturing PABX equipment for the last three (3) years. The bidder shall submit with their proposal, performance certificates of the offered equipment from at least one power utility. The performance certificates shall provide evidence of successful operation of the proposed equipment in sub-station environment for at least 1 year as on date of opening of the bid. The PABX must be capable of operating in the high EMI environment of substations and power plants, and without air conditioning. ……………………………………. …………………………………… ……………………………….. # Testing & Inspection of PABX The offered PABX shall be type approved by TEC. The contractor shall submit the TEC certificate in support of the same. The FAT & SAT for PABX shall be conducted as per requirement specified in this Section. | 2.11 PABX Clause Deleted |
| Section-04 DC Power Supply System Requirements | 4.2 Cabling & Enclosure Requirements Clause added | - Power Cables - The contractor shall supply, install and commission all power cables, grounding cables, control cables, network interface cables, MCBs, fuses etc. of required size and capacity including associated hardware (lugs, glands, cable termination boxes, PVC pipe etc.) required to mechanically and electrically complete the installation of equipment and their successful operations. - The Contractor shall be responsible for cable laying and termination at both ends of the cable. The Contractor shall also be responsible for termination of feeder cables at Contractor’s equipment end including supply of suitable lugs, glands, terminal blocks, PVC pipe, etc. - The requirement of quantities of AC & DC cables for Equipment, DCPS, grounding cables, control cables, network interface cables, PVC pipe, MCBs (AC & DC) etc and others associated hardware (lugs, glands etc) shall be supplied by the contractor as per the actual requirement without any extra financial implication. The AC & DC cables as per site requirement will be ordered for following: - Connection from Equipment to existing DCPS (Only Equipment is supplied). - Connection from Rack (DCDB) to existing DCPS (Equipment along with Rack is supplied). - Connection from DCPS to AC mains (Equipment along with Rack & DCPS is supplied) - The DC cable for s.no.(a)&(b) of suitable rating, shall be supplied as per the site requirement. The cables shall be suitable for laying in racks, cable trays, ducts, trenches and conduits. - Earthing connection for Equipment/ DCPS/ Rack will be Extend from Site existing Earth pit. 4.2.1.6 All AC power cables shall be stranded Aluminium conductor armoured XLPE/ PVC insulated and sheathed conforming to IS 1554 Part-1/IS 7098. The cables shall be suitable for buildings and underground buried installations with uncontrolled backfill and chances of flooding by water. 4.2.1.7 All DC power cables shall be stranded Copper conductor, armoured XLPE/PVC insulated and sheathed, 1100V grade as per IS 1554 Part-1/IS 7098. - All wires used for manufacturing the cables shall be true circular in shape before stranding and shall be uniformly good quality and free from defects. The filler and inner sheath shall be of non-hygroscopic and shall be soften than insulation. Outer sheath shall be suitable for operating temperatures of cable. Repaired cables shall not be accepted. - All cables shall conform to relevant IS. - Each complete cable between electrical and mechanical assemblies, enclosures and distribution frames shall be identified at each end with an indelibly marked shrink-on sleeve which indicates the cable number, and the near-end and far-end destination. - All the required MCBs, fuses etc. required for safe operation of the equipment shall also be supplied and installed by the Contractor. Separate cables shall be laid for AC and DC. The cables shall be suitable for laying in cable trays, ducts, trenches, and conduits. |
| Section-06 Inspection & Testing | - Integrated Testing for PABX system The Contractor shall perform integrated system tests, check system configuration, check successful integration of supplied equipment & subsystems and demonstrate end to end communication network operation. The test program for the Integrated testing shall be sufficiently detailed and comprehensive to ensure and demonstrate to the satisfaction of the Employer, that - End to end voice and data connectivity is established and the end to end voice/ data channel quality is maintained. - The supplied PABXs inter-operate with each other and with existing equipment - PABX configurations are finalised and the telephony network operates as required and that overall the supplied PABX system operates as an integrated system. After the successful completion of the above tests and performing any necessary corrective actions and retesting, the PABX system in the batch under test shall be monitored for 24 hours. The PABX system shall operate satisfactorily without any failure or major alarms appearing on the system. However, minor alarms (not affecting the performance of the link) shall be acceptable during the 24 hour test period. | 6.5.1.4 Integrated Testing for PABX system Clause removed |
| Appendix-D Standard FAT Procedure-NMS |  | Added TPS-TMN-006: Demonstration of system hardening of NMS System |
| Appendix-E Standard SAT Procedure-NMS |  | Added TPS-20: Demonstration of system hardening of NMS system |

Package specific changes

| Section & Cl. no | Existing Clause | Modified Clause |
| --- | --- | --- |
| Appendix-A General Information & Implementation Schedule For Package FOTE-07: Communication Equipment (SDH) Supply & Installation Package for Communication Scheme approved in 33rd NCT | Table A-1 Implementation Schedule | Table A-1 Implementation Schedule - Supply & Installation 2 no. of STM-16 FOTE at Simbhavli (UP) and Shatabdi Nagar (UP) each under ISTS: 18 months - Supply & Installation of 1 No. of STM-16 FOTE each at Saharanpur (PG), Deoband (UP), Saharanpur (UP), Nanauta (UP) and Shamli (UP): 8 months - Supply and Installation of 1 no. FOTE alongwith Optical interfaces at Hassan S/s. 24 months - Replacement of 15 no. of FOTE at critical ISTS location in Southern Region: SRLDC (2no.), Somanhalli, Bidadi, Narendra, Madhugiri 765kV, Hiriyur, Kolar, Neelamangla, Davangere, Hoody, Sriperumbudur, Pudducherry, Hosur, Salem 400kV 12 months |
|  | Table A-2 Proposed FOTE locations | Table A-2 Proposed FOTE locations Note: - The subject package covers supply, installation & commissioning of FOTE for NR & SR. |