| ### Sr. No | ### Clause No. | ### Existing Clause | ### Bidder’s Query | ### Clarification |
| --- | --- | --- | --- | --- |
| 1 | Clause-1.2.1 , Section-I of Technical Specification, Volume-II |  | Since the subject package is a balance work, please furnish the Visual chart and Gantt chart indicating the work executed by the earlier EPC and the exact situation on ground pertaining to foundation, erection and stringing | Vide clause 1.2.1 of Section-I of Technical Specification, bidders are advised to visit the site address for more details on exact situation/status of balance works at ground level. |
| 2 | Clause- 1.3.1 ,Section-I Technical specification, Volume-II | The transmission line shall emanate from 400/132kV Biswanath Chariali substation/switchyard in the State of Assam and terminate at 400kV Lower Subansiri (NHPC) substation in the State of Arunachal Pradesh. The transmission line is passing through Plain/Hilly area. | Clause 1.3.1 of Technical specification states subject transmission line passes through Assam and Arunachal, please indicate the approximate percentage on line passing through two states mentioned. | Entire route length of transmission line which is emanating at Biswanath Chariali substation and terminating at Lower Subansiri is in Assam state except the span between the dead end tower and gantry at Lower Subansiri (HEP). |
|  |  |  | As per volume-II, Section-I, Clause No: 1.3.1 i.e. the transmission line shall emanate from 400/132kV Biswanath chariali substation/switchyard in the state of Assam and terminate at 400kV Lower Subansiri (NHPC) substation in the state of Arunachal Pradesh. So, we understood that the Tr. Line in package TW1B is from Biswanath Chariali to Lower Subansiri, and where as the Tr. Line package TW2B is from Lower Subansiri to Biswanath Chariali. Kindly confirm. |  |
| 3 | Clause- 1.1.5 ,Section-I Technical specification, Volume-II | In case, part quantity of Tower/Tower Parts and other line material viz. insulators, earthwire, hardware fittings, conductor & earthwire accessories etc. are supplied by the Employer or other Supplier, the contractor shall take delivery, carry out (unloading & stacking), ensure safe custody of materials at their stores including insurance cover as required &install the same in the transmission lines as stipulated in this specification. Some quantity of owner supplied transmission line items i.e Tower / Towers parts, Conductors, Insulators, hardware fittings and accessories for conductor & earth wire will be available in the existing stores located at: 1) Kherbari Biswanath Chariali Dist : Biswanath, Assam 2) Bihapukhuri Biswanath Chariali Dist: Biswanath, Assam 3) Kasamari North Lakhimpur Dist : Lakhimpur, Assam 4) Pathali pahar North Lakhimpur Dist : Lakhimpur, Assam The contractor, upon direction from Employer shall use the same for execution of the transmission line. In this regard, the responsibility of loading - unloading, transportation etc of these items from the existing stores till use on the line shall be that of the contractor and no additional cost shall be paid by Employer. | Please refer to clause 1.1.5 of Technical Specification, which mentions part quantity of towers, earthwire, hardware fittings, conductor and earthwire accessories etc., shall be supplied by M/s. PGCIL which is available at their stores mentioned. In view of the same please furnish the details of tower sections available and kindly also confirm whether the quantity of tower parts mentioned in supply schedule are for complete towers or for part towers as well whose part quantity is available at PGCIL stores. | Quantity in the price schedule is the tentative quantity for full towers and assorted tower parts combined. Detailed sections & full towers will be furnished during construction/detailed engineering stage. |
| 4 | Section-XI of Technical Specifications |  | The Hardware drawings of 400kV Twin ACSR Lapwing are missing. | The drawings are provided. Please refer Amendment-II. |
| 5 | Clause- 4.2 & 4.3, Section-I of Technical specification, Volume-II |  | Insulator details like string UTS etc. are not mentioned in the specifications. Please confirm. | The details for both composite long rod insulator and disc insulators are mentioned at clause no. 4.2 & 4.3 of Section-I of Technical Specification. |