| Sl. No | Ref Section | Provision in bidding document | Bidders Queries | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| 1. | Vol.II Section Project Cl. No. 2.1.1.1(b), 2.1.2.1(b), 2.1.4.1(b) and 8 (iii) | 2.1.1.1 (b) Digital RTCC panel: Existing 02 nos. 400/220/33kV 3-ph auto-transformers at 400/220kV Palakkad substation commissioned with parallel operation using Analogue RTCC Panels. The digital RTCC panel under present scope shall comprise of 4 Numbers of Digital RTCC Relays {One(1) as spare, One (1) for present scope transformer & Two(2) for existing transformers}. The Present Scope shall include all the required power, control & special cables cabling (supply & installation) between existing transformer RTCC panels/OLTC MB/Transformer MB and the Digital RTCC panel, wiring modifications in existing panels as per RTCC scheme requirement so as to enable parallel operation of transformer under present scope with existing transformers through Digital RTCC relays.Present scope includes, wiring between existing and new digital RTCC panel, modifications in existing panels as per RTCC scheme requirement so as to enable parallel operation of transformer under present scope with all the existing transformers through Digital RTCC relays. 2.1.2.1(b) Digital RTCC panel: Existing 07 nos. (400/√3)/(220/√3)/33kV 167 MVA, 1- ph auto-transformers (forming 2 banks of 3ph. 500MVA ICT with 1 single phase unit as spare) at 400/220kV Kolar substation is commissioned with parallel operation using Analogue RTCC Panels. The digital RTCC panel under present scope shall comprise of 4 Number of Digital RTCC Relays {One(1) as spare, One (1) for present scope transformer & Two(2) for existing 2 banks of transformers}. The Present Scope shall include all the required power, control & special cables cabling (supply & installation) between existing transformer RTCC panels/OLTC MB/Transformer MB and the Digital RTCC panel, wiring modifications in existing panels as per RTCC scheme requirement so as to enable parallel operation of transformer under present scope with existing transformers through Digital RTCC relays. 2.1.4.1(b) Digital RTCC panel: Presently, 5 nos. digital RTCC relay (M/s a-eberle make) are mounted on digital RTCC panel is available at site. Out of the five digital RTCC relays, 3 nos. relays are already in use for existing ICT-1, 2 and 3 and the fourth one shall be used for 4th ICT mentioned at Sl. no. 2.1.3 above and fifth one is kept as spare. Under present scope, contractor shall provide a new digital RTCC relay for the 5th ICT to be mounted in a new digital RTCC panel which shall be compatible with the existing digital RTCC relays. Present scope includes, wiring between existing and new digital RTCC panel, modifications in existing panels as per RTCC scheme requirement so as to enable parallel operation of transformer under present scope with all the existing transformers through Digital RTCC relays. 8.0 Exclusions: iii) Auxiliary power and control cables from control room/SPR to marshalling box of transformer | Query No. 1 M/s POWERGRID to kindly confirm the scope of supply of power & Control cable as clause 2.1.(1,2,4).1 (b) and Clause 8 are contradictory. Query No. 2 At present, Palakkad and Kolar S/s ICT’s are working via analog AVR and as per scope we have to replace existing analog AVR with digital type AVR. Our understanding is that we can provide Digital RTCC relay as per PGCIL's approved make as there is no specific make required. Kindly confirm. Query No. 3 The Present Scope shall include all the required power, control & special cables cabling (supply & installation) between existing transformer RTCC panels/OLTC MB/Transformer MB and the Digital RTCC panel, wiring modifications in existing panels as per RTCC scheme requirement so as to enable parallel operation of transformer under present scope with existing transformers through Digital RTCC relays. In view of the above and to estimate the cost we request to provide the following at the earliest, a. What type of cable ( cable details) is used in existing transformer? b. What is the distance between the existing Transformer RTCC panels/OLTC MB/Transformer MB and New Digital RTCC panel , for which the cable run is required? c. Scope of modification in existing panel. d. Distance of control room from new transformer and existing transformer Query No. 4 Under present scope, contractor have to provide a new digital RTCC relay for the 5th ICT to be mounted in a new digital RTCC panel which shall be compatible with the existing digital RTCC relays hence we request you to provide configuration details of existing Digital RTCC Relay i.e a-Eberle make to check the compatibility with new DGITAL RTCC Relay. | - For scope of Power, control and special cable under present package, following is clarified: For Kolar and Palakkad S/s: Power, control and special cable, from MB/OLTC MB of Present scope and Existing Transformer to New Digital RTCC panel pertaining to parallel operation of the existing and present scope ICT through new digital RTCC panel, shall be supplied under present scope. Other Power and control cable between Transformer MB and control room/SPR shall be supplied by substation contractor under separate package. Cable between existing transformer and conventional RTCC panel may be reused in case sufficient length is available to terminate it to present scope new digital RTCC panel. No cable joint shall be permitted. However, if new cables or additional cables are required to complete the present scope of work then the same shall deemed included in present scope of work. Existing conventional RTCC panel shall be dismantled and placed at suitable location inside the S/s as per direction of POWERGRID substation incharge. For Tuticorin S/s for 4th ICT: Power, control and special cable, from MB/OLTC MB of Present scope Transformer to Existing Digital RTCC panel shall be supplied under present scope. Other Power and control cable between Transformer MB and relay panel room shall be supplied by substation contractor under separate package. For Tuticorin S/s for 5th ICT: Power, control and special cable, from MB/OLTC MB of Present scope Transformer to new Digital RTCC panel shall be supplied under present scope. Further wiring between existing and new digital RTCC panel, pertaining to parallel operation of existing and present scope Transformer through Digital RTCC relays shall also be supplied under present scope. Other Power and control cable between Transformer MB and relay panel room shall be supplied by substation contractor under separate package. - At present, Conventional RTCC panels is available for existing ICT at Palakkad and Kolar S/s. Under present scope the existing conventional RTCC panels to be replace with new Digital RTCC panel. Digital RTCC relay may be of any POWERGRD approved make. - Bidders are requested to visit site and assess required inputs. - Bidders are requested to visit site and assess required inputs. |
| 2. | Completion Schedule |  | With reference to above captioned project, we would like to bring in your kind notice that we cannot meet the completion period mentioned in bid document i.e. 12 [Twelve] Months [Sec-III/BDS/ITB 24.1(c)], considering the scopes in each location. In this regard, we request you to kindly amend the completion period as 15 [Fifteen] months for enable us to participation in this bid. | No Change Bidder to quote in line with the provision of Bidding Documents. |