| Sl. No. | Clause No. | Existing clause | Amendment |
| --- | --- | --- | --- |
| 1 | Volume II, Section 1 A, Clause 1.6, Point 5, Sag-Tensions under Condition-II (S/C Line) S/C portion between tapping point of 400kV Cuddapah -Somnahalli line LILOed at NP Kunta & Kolar. | Sl. No.; Parameters; Requirement. 5; Sag-Tensions under Condition-II (S/C Line) S/C portion between tapping point of 400kV Cuddapah-Somnahalli line LILOed at NP Kunta & Kolar.. i); Sag for ruling span at designed maximum temperature & no wind condition (m); ≤12.82. ii); Sag for ruling span at minimum temp (0 deg C) and no wind condition (m); ≥9.67. iii); Tension at 32°C and full wind condition (45 Kg/m2 wind pressure); ≤ 4278 kg & not exceeding 70% of UTS of proposed conductor. iv); Tension at designed maximum temperature and Full wind condition (45 Kg/m2 wind pressure); ≤ 4278 kg & not exceeding 70% of UTS at designed maximum temperature of proposed conductor. v); Tension at 32°C and 2/3rd wind condition (30 Kg/m2 wind pressure); ≤ 4473 kg & not exceeding 70% of UTS of proposed conductor. vi); Tension at designed maximum temperature and 2/3rd wind condition (30 Kg/m2 wind pressure); ≤ 4473 kg & not exceeding 70% of UTS at designed maximum temperature of proposed conductor. vii); Tension at knee point temperature & no wind condition (Kg); Not exceeding 40% of UTS of core@ of proposed conductor. | Sl. No.; Parameters; Requirement. 5; Sag-Tensions under Condition-II (S/C Line) S/C portion between tapping point of 400kV Cuddapah-Somnahalli line LILOed at NP Kunta & Kolar.. i); Sag for ruling span at designed maximum temperature & no wind condition (m); ≤12.82. ii); Sag for ruling span at minimum temp (0 deg C) and no wind condition (m); ≥9.67. iii); Tension at 32°C and full wind condition (45 Kg/m2 wind pressure); ≤ 4278 kg & not exceeding 70% of UTS of proposed conductor. iv); Tension at designed maximum temperature and Full wind condition (45 Kg/m2 wind pressure); ≤ 4278 kg & not exceeding 70% of UTS at designed maximum temperature of proposed conductor. v); Tension at 0°C and 2/3rd wind condition (30 Kg/m2 wind pressure); ≤ 4473 kg & not exceeding 70% of UTS of proposed conductor. vi); Tension at designed maximum temperature and 2/3rd wind condition (30 Kg/m2 wind pressure); ≤ 4473 kg & not exceeding 70% of UTS at designed maximum temperature of proposed conductor. vii); Tension at knee point temperature & no wind condition (Kg); Not exceeding 40% of UTS of core@ of proposed conductor. |
| 2 | Volume II, Section VII B, Clause 1.7.1. 3 | Joints shall be made by cold pressure butt welding and shall withstand a stress of not less than the breaking strength of individual strand guaranteed | Joints shall be made by electric butt welding, electric butt cold upset welding or cold pressure butt welding and shall withstand a stress of not less than the breaking strength of individual strand guaranteed |