| Sl. No. | Existing clause | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- |
| 1 | Volume II, Section 1 A, Clause 1.6, Point 5, Sag-Tensions under Condition-II (S/C Line) S/C portion between tapping point of 400kV Cuddapah -Somnahalli line LILOed at NP Kunta & Kolar. V); Tension at 32°C and 2/3rd wind condition (30 Kg/m2 wind pressure); ≤ 4473 kg & not exceeding 70% of UTS of proposed conductor. | Kindly re-confirm , Tension at 32°C and 2/3rd wind condition (30 Kg/m2 wind pressure)- ≤ 3930 kg Or Tension at 0°C and 2/3rd wind condition (30 Kg/m2 wind pressure)- ≤ 4473 kg | Refer Amendment no.1 |
| 2 | Volume II, Section VII B, Clause 1.7.1. 3 Joints shall be made by cold pressure butt welding and shall withstand a stress of not less than the breaking strength of individual strand guaranteed | Kindly Added as follows, Joints shall be made by electric butt welding, electric butt cold upset welding or cold pressure butt welding and shall withstand a stress of not less than the breaking strength of individual strand guaranteed | Refer Amendment no.1 |
| 3 | Volume II, Section VII B, Clause 1.9.2.3 The aluminium cladding of wires shall be of aluminum having purity not less than 99.5 % and shall be thoroughly bonded to the core wire strand(s). The minimum conductivity of offered aluminium clad wire shall be 14% of IACS. The minimum thickness of aluminium cladding shall be 3% & 5% of nominal wire diameter, for 14% & 20% IACS conductivity respectively | Kindly modify as, The minimum conductivity of offered aluminium clad wire shall be 14% of IACS. The minimum thickness of aluminium cladding shall be as per relevant standard (BS EN 50540), for 14% & 20% IACS conductivity respectively. | No change in provisions of TS is envisaged. |
| 4 | Volume II, Section VII B, Clause 2.11.11 Before reeling, card board or double corrugated or thick bituminised water-proof bamboo paper shall be secured to the drum barrel and inside of flanges of the drum by means of a suitable commercial adhesive material over which HDPE sheet to be provided. In case of steel drum, for securing HDPE sheet onto the bamboo paper & drum flanges, the HDPE sheet shall be secured onto the drum by means of a commercial adhesive/self-locking nylon cable zip ties such that there is no protrusion above the general surface that may cause damage to the conductor strands. After reeling the conductor, the exposed surface of the outer layer of conductor shall be wrapped with thick plastic sheet secured using adhesive tapes to preserve the conductor from dirt, grit and damage during storage, transport and handling. Medium grade craft/crepe/polythene paper shall be used in between the layers of conductor. Additionally, in case of Annealed aluminium being used for aluminium layers of offered HTLS conductor, medium grade kraft paper of 90 to 100 mm width shall be wrapped over HTLS conductor during production and re-winding such that the no conductor layer is directly in contact with other side, below & upper conductor layers in a drum. | Kindly remove additional requirement of kraft paper for annealed aluminum layers, Before reeling, card board or double corrugated or thick bituminised water-proof bamboo paper shall be secured to the drum barrel and inside of flanges of the drum by means of a suitable commercial adhesive material over which HDPE sheet to be provided. In case of steel drum, for securing HDPE sheet onto the bamboo paper & drum flanges, the HDPE sheet shall be secured onto the drum by means of a commercial adhesive/self-locking nylon cable zip ties such that there is no protrusion above the general surface that may cause damage to the conductor strands. After reeling the conductor, the exposed surface of the outer layer of conductor shall be wrapped with thick plastic sheet secured using adhesive tapes to preserve the conductor from dirt, grit and damage during storage, transport and handling. Medium grade craft/crepe/polythene paper shall be used in between the layers of conductor. Additionally, in case of Annealed aluminium being used for aluminium layers of offered HTLS conductor, medium grade kraft paper of 90 to 100 mm width shall be wrapped over HTLS conductor during production and re-winding such that the no conductor layer is directly in contact with other side, below & upper conductor layers in a drum. | No change in provisions of TS is envisaged. |
| 5 |  | PGCL to confirm continuous outlet outages for reconductoring of gap conductor as gap conductor require pre tensioning while execution. | Bidder may refer Section-1 A, clause 1.4 of TS regarding shutdown. No change in provisions of TS is envisaged. |
| 6 | Volume II Section-VI B, Clause 1.6.7, Slip strength of the offered suspension clamp shall be within 12% to 18% of UTS of the offered HTLS Conductor. | As per Technical Specification clause 1.6.7, Slip strength of the offered suspension clamp shall be within 12% to 18% of UTS of the offered HTLS Conductor. Major factor to be considered is that Outer layer of HTLS conductor is made of very soft annealed Aluminum Alloy. Hence slip strength of same can’t be similar to that of conventional conductor since Slip strength is based on capability of conductor as well without deformation. As per IS 2486 Part -1, clause 11.1.1 slip strength required range is 8% to 15 % of conductor UTS. We therefore kindly request to revise the Slip strength requirement as per IS referred above. | No change in provisions of TS is envisaged. |
| 7 | Volume II Section-VI B TABLE-1 (Details of Materials) point no. 4 (a), (a); Outer Sleeve (for Annealed Aluminium Conductor); Al Alloy 19500; Extruded; IS 733. | Kindly request to include “Grade 6060” as per EN 573 as well in material of Outer sleeve - Dead End Assembly and Mid span joint for Annealed Aluminum Conductor, which meets both electrical as well mechanical reqts. | No change in provisions of TS is envisaged. |
| 8 | Volume II Section-VI B Clause 1.7.1.4 The length and diameter of each rod shall be furnished by the bidder in the GTP. The tolerance in length of the rods between longest and shortest rods in complete set should be within the limits specified in the relevant Indian/International Standards. The ends of armour rod shall be parrot billed. | Request to include “Ball ended” as well which meets both electrical as well mechanical requirements. | No change in provisions of TS is envisaged. |
| 9 | Volume II Section-VI B, Annexure-A, Clause. 2.6,Tests on Hardware Fittings 2.6 Thermal Profile test The fitting/ accessories under the test shall be installed on conductor and current shall be passed through the conductor to achieve steady state conductor temperature corresponding to the designed maximum temperature of the offered HTLS conductor. Temperature achieved in different components of fittings/ accessories shall then be measured. The temperature of the components shall be below the specified maximum allowable temperature of the materials of those components. Maximum allowable temperature for aluminium/ aluminium alloy components shall be limited to 93 Deg C. | This Test requirement is moreover similar to Heating cycle. kindly clarify whether shall be performed once again. | No change in provisions of TS is envisaged. |
| 10 | Volume II Section- VIII Composite Long rod Insulator, CL. No. 4.1.1, On the complete composite Long Rod Insulator String with Hardware Fittings: | We confirm specification ss per specification. Regarding the type tests the required strings are HTLS Twin Moose conductor ,hence please confirm whether HTLS ACS 559 conductor is applicable or not. | For composite insulators, String test using ACSR/AAAC/Al59 Moose conductor or its equivalent HTLS conductor is acceptable. |
| 11 | Volume II, Section VII B, Clause 2.1.1, (i), point (n) Salt Spray Test (applicable for stranded composite core conductors having galvanic protection layer not conforming to ASTM B987) | Please remove this requirement | No change in provisions of TS is envisaged. |
| 12 | Volume II, Section VII B, Clause 2.1.1(ii) On Conductor Strand/core | Please add following, In the case of composite core conductors, the tests specified under Clause “On Conductor Strand/core” shall be carried out before stranding on as-manufactured samples. | No change in provisions of TS is envisaged. |
| 13 | Volume II, Section VII B, Clause 2.2, point (t) Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductors having galvanic barrier layer conforming to ASTM B987) | Please amend as follows; Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductors having galvanic barrier layer conforming to ASTM B987) | No change in provisions of TS is envisaged. |
| 14 | Volume II, Section VII B, Clause 2.2 Note: All the above tests except (m) shall be carried out on Aluminium Alloy and core strands after stranding only. | Please add following, For composite core, all acceptance tests shall be carried out before stranding. | No change in provisions of TS is envisaged. |  |  |
| 15 | Volume II, Section VII B, Annexure A, Clause 1.24 Torsion and Elongation Tests on Core wire/ Composite core ii) Torsion Test : The purpose of the test is to determine the resilience of the composite core to twisting and to show that after the composite core has experienced the prescribed twisting, it will not crack or have a loss in tensile strength due to the twisting. The sample length shall be such that the gauge length in between the gripping fixtures is 170 times the diameter of the core in case of High Strength Grade composite cores and 340 times the diameter of the composite core in case of Extra High strength composite core. However, the gauge length shall not be more than 4m. One grip shall then be fixed so that it does not twist and the other end shall be twisted a full 360 degrees and then fixed in this position for 2 minutes. Once the twist time is completed, the core is untwisted an inspected for any crazing or other damage. If no damage is observed, the composite core is then tensile tested to failure and the final load recorded. For the test to be accepted, the composite core must withstand at least 100% of its rated tensile strength. Two samples need to be completed in order to satisfy the testing requirement. | Please amend as follows; ii) Torsion Test: The purpose of the test is to determine the resilience of the composite core to twisting and to show that after the composite core has experienced the prescribed twisting, it will not crack or have a loss in tensile strength due to the twisting. The sample length shall be such that the gauge length in between the gripping fixtures is 170 times the diameter of the core. For core lengths less than 170 times the core OD, rotate the core to maintain the same rotation to length ratio. In case of High Strength Grade composite cores and 340 times the diameter of the composite core in case of Extra High strength composite core. For core lengths less than 340 times the core OD, rotate the core to maintain the same rotation to length ratio However, the gauge length shall not be more than 4m. One grip shall then be fixed so that it does not twist and the other end shall be twisted a full 360 degrees and then fixed in this position for 2 minutes. Once the twist time is completed, the core is untwisted an inspected for any crazing or other damage. If no damage is observed, the composite core is then tensile tested to failure and the final load recorded. For the test to be accepted, the composite core must withstand at least 100% of its rated tensile strength. Two samples need to be completed in order to satisfy the testing requirement. | No change in provisions of TS is envisaged. |
| 16 | Volume II, Section VII B, Annexure A, Clause 1.25 Breaking load test on Aluminium/Aluminium Alloy & Composite core/ Core wires and D.C Resistance test on Aluminium/ Aluminium Alloy wire The above tests shall be carried out as per IEC: 60888/60889 or relevant international standards and the results shall meet the requirements of the specification. | Please add as follow for composite core; For composite cores, the breaking load shall be performed as described in Section 9 of ASTM B987. | It is clarified that Breaking load test can be carried out as per IEC 888/ 889 or relevant international standards including ASTM B987, if applicable. |
| 17 | Volume II, Section VII B, Annexure A, Clause 1.33 Bending Test on Polymer Composite Core (as Type Test) Bending test on polymer composite core (CFC) before stranding shall be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from composite core at conductor manufacturing unit before stranding of conductor. Alternatively, supplier may carry out bending test on polymer composite core (CFC) before stranding on the samples taken at the core manufacturing unit, from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Bending test on polymer composite core (CFC) shall also be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: For high strength grade CFC: 60 times the diameter of CFC For Extra high strength grade CFC: 70 times the diameter of CFC | Please amend as follows, Bending test on polymer composite core (CFC) before stranding shall be performed as per ASTM B987/B987M-20 on polymer composite core samples taken from composite core at conductor manufacturing unit before stranding of conductor. Alternatively, supplier may carry out bending test on polymer composite core (CFC) before stranding on the samples taken at the core manufacturing unit, from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Bending test on polymer composite core (CFC) shall also be performed as per ASTM B987/B987M-20 on polymer composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: For high strength grade CFC: 60 times the diameter of CFC For Extra high strength grade CFC: 70 times the diameter of CFC | No change in provisions of TS is envisaged. |
| 18 | Volume II, Section VII B, Annexure A, Clause 1.34 Bending test on polymer composite core (as Acceptance test) Bending test on polymer composite core (CFC) shall be performed as per ASTM B987/ B987M-17 on polymer composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: 1) For high strength grade CFC: 60 times the diameter of CFC 2) For Extra high strength grade CFC: 70 times the diameter of CFC | Please amend as follow, Bending test on polymer composite core (CFC) shall be performed as per ASTM B987/ B987M-20 on polymer composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: 1) For high strength grade CFC: 60 times the diameter of CFC 2) For Extra high strength grade CFC: 70 times the diameter of CFC | No change in provisions of TS is envisaged. |