| Sl. No. | Clause ref | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- |
| 1. | Volume II, Section IA, Annexure-A | Pile undertaking (PROFORMA OF UNDERTAKING BY THE PROPOSED AGENCY FOR PILE FOUNDATION) is not furnished in the tender documents. We request you to provide the same. | Bidder may refer Annexure-A, Section 1A of technical specification wherein “PROFORMA OF UNDERTAKING BY THE PROPOSED AGENCY FOR PILE FOUNDATION” is attached |
| 2. | Volume II, Section IA, Clause 1.5.1 | We request you to provide the route survey details for visiting the transmission line to acquaint with the terrain and site conditions. | Bidders may refer Clause 1.5.1, Section-IA, Volume-II (Technical specifications) which interalia indicates that bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines. For this purpose they are requested to contact the following address: Chief General Manager (Engg) POWER GRID CORPORATION OF INDIA LTD. Northern Region Transmission System-I Faridabad, Haryana |
| 3 | General | Please clarify whether the JDU or MAF from Monopole Manufacturer should be submitted at the bidding stage. If, Joint Deed of Undertaking by the Monopole Manufacturer is to be submitted than please provide us the format of JDU and also confirm the appropriate value of stamp paper. | It is clarified that JDU shall be applicable for monopole manufacturer and same shall be submitted during detail engineering based on the formats which shall be provided in post-award stage. |
| 4 | General | We understand that JDU is applicable only for lattice structure. In case the bidder proposes to supply monopole from other manufacturers, bidder will only need to submit Authorization Certificate issued by the manufacturer. Please confirm our understanding. | Refer clarification at Sr. No 3. |
| 5 | Volume-II, Section IVF, Clause 1.2.1.d | We understand that if design criteria requires Twin Poles for any of the type of Poles provided in the BOQ, bidder will have the liberty to propose the same. Kindly confirm. Besides, type test will not be required for Poles (all types) designed with Reliability level 3. | It is clarified that twin pole is permitted for PD type poles only. It is confirmed that prototype testing shall not be required for pole structures designed with Reliability level 3. |
| 6 | Volume-II, Section IVF, Clause 1.2.4 | We understand that the Monopole is to be designed and tested considering higher of the sag and loads due to Twin ACSR Moose conductor as well as proposed Twin HTLS conductor. In case the sag of one conductor comes higher and the corresponding tension comes lower, then the tower is deigned considering higher sag of one conductor and higher tension of the other conductor and vice versa. Please confirm. | Bidder understanding is correct. |
| 7 | Volume-II, Section IVF, Clause 1.7 | 400 kV Multicircuit Poles are envisaged to have large diameter greater than 3m, thereby making it necessary to galvanize it in multiple halves owing to the limitations of galvanization bath size PAN India, as the maximum width of galvanization bath size available in India is 2.5 meters. The maximum number of Poles which are to be supplied for this project will have base plates & sections having diameter more than 2.5 meters and, in such case, it will be inevitable to resort to galvanizing in multiple parts which fit into the galvanizing bath then seamlessly weld the sections and then metallize it. Hence, we kindly request you to modify the clause as below: In case of restriction due to the size of hot dip galvanizing bath, pole segments having outer diameter more than 1 meter, fabrication & galvanization is permitted in multiple halves but limited to maximum four parts. We would further like to point that PGCIL in its earlier tenders have allowed galvanization in upto 4 halves. | Refer Amendment-I |
| 8 | General | In BOQ Lattice tower weights are given in MT. But, we would like to know the type of tower is going to be used in this line it is a Normal / Narrow base Tower. Please confirm. | This is to be clarified that both normal and narrow base towers are envisaged. |
| 9 | General | Please confirm whether erection and stringing to be carried out on pile foundation is for Tower or Monopole. | This is to be clarified that pile foundation is envisaged with lattice tower. |
| 10 | General | As per scope, River Crossing is involved but no separate quantities for stringing is given. We request you to kindly furnish the same. | For river crossing locations, RC towers are not envisaged. As such, separate stringing item for river crossing stretch is not applicable. |
| 11 | General | We understand that JDU and PBG is applicable only for lattice structure and not on monopole. Please confirm our understanding. | Refer clarification at Sr. No 3. |
| 12 | General | Kindly provide the details of River on which Pile foundation is to be carried out. Please also confirm whether Pile is in water or land and provide coordinates of location requiring Pile. | Refer clarification at Sr. No 2. |
| 13 | Volume-II, Section IVF, Clause 1.2.1 (d) | Is there any ROW or Footprint restrictions for Twin Pole? | Bidders may decide footprint/outer diameter considering the limitation during execution at site. Further bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines. For this purpose they are requested to contact the following address: Chief General Manager (Engg) POWER GRID CORPORATION OF INDIA LTD. Northern Region Transmission System-I Faridabad, Haryana |
| 14 | Volume-II, Section IVF, Clause 1.2.2 | Please provide sag-tension template for HTLS conductor/TS of HTLS conductor. | Bidders may refer Section IA and section VII B for design of HTLS conductor. |
| 15 | Volume-II, Section IVF, Clause 1.2.3 | There's no drawing attached with TS. Kindly Provide | Refer Amendment -I |
| 16 | BPS | Soil investigation report along with Bore log details are required for design of Pier foundation for Monopole structures, Kindly furnish the same | Refer clarification at Sr. No 2. |
| 17 | BPS | In the price bid, mentioned as the 400kv multi circuit monopole has to be designed for Twin ACSE Moose.” Kindly confirm, this is for Twin ACSR Moose conductor or HTLS Moose Conductor. | Bidder may refer clause no 1.5, section IVF, of TS Multi circuit Pole structures shall be designed considering higher of the sag and loads due to Twin ACSR Moose conductor as well as proposed Twin HTLS conductor. |
| 18 | General | Complete line is pass through in NCR region, We request you to provide the Route details for carrying out site survey and Exact locations GPS Coordinates for Monopole Towers. | Refer clarification at Sr. No 2. |
| 19 | General | Is there is any limitation on the base width for Monopole Tower design. | Refer clarification at Sr. No 13. |
| 20 | Volume-II, Section IA, Clause 1.4 | Kindly clarify whether the mentioned tension values @32 DegC & full wind condition and designed maximum temperature and full wind condition are maximum tension or horizontal tension. | It is to clarified that tension values considered are the horizontal tension. |
| 21 | Volume-II, Section IA, Clause 1.4 | Requesting to allow the nominal mass of complete conductor (kg/m) equivalent to that of ACSR moose conductor i.e (2.004kg/m) | Refer amendment 1. |
| 22 | Volume-II, Section IA, Clause 1.4 | We have worked out various HTLS conductor design variant option. However, due to limiting condition of achieving minimum sag of 11.69m for multi circuit tower (normal) and 11.09mtr for multi circuit towers (narrow base) for top conductor of top ckt is difficult to achieve max sag limit of 15.46m at designed maximum operating temperature of core corresponding to conductor surface temeparature capable to carry 1596Amp. Requesting PGCIL to reduce the minimum sag level to 9.6m | Refer amendment 1. |
| 23 | BPS | The number of Pile foundation is not available. Please provide. | Bidders may refer BOQ indicating three nos of river crossing locations where pile foundation has been envisaged. |
| 24 | BPS | As per clause, details of multicircuit towers (narrow base) are available. But the Price schedule does not mention any configuration as normal and narrow base tower. Pl confirm | Refer clarification at Sr. No 8. |