| Sl. No. | # Ref Section | # Provision in bidding document | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- |
|  | Cl No. 6.4 of Technical Specification | Type test requirement & it’s validity The offered Reactor or the Reactor, the design of which is similar to the offered Reactor, should have been successfully type tested. Manufacturer may use same or different approved make of Bushings and other accessories used in type tested or short circuit tested unit in their Reactor. Further, type test report of Reactor shall only be acceptable provided the offered Reactor has been manufactured from the same plant. | Since this tender specification floated under vendor development and allows to manufacturers who have manufacturing and testing facilities for 345 KV or above class reactor in India and have supplied the transformers/reactors upto 220 kV class, therefore this clause not applicable against this tender specification, please clarify. | Since this tender is under vendor development, if the vendor does not have any prior POWERGRID-approved type test report for a Reactor of similar design, then the vendor will be required to carry out the complete type testing as per Technical specification on the first Reactor offered under this tender without any additional cost and time implications to POWERGRID. |
|  | Section-VI Sample Forms and Procedures | Refer to your Price Adjustment clauses (Appendix-2) | We would like to submit that Most of Transmission Utilities, NTPC etc has adopted IEEMA Price Variation formula for awarding price variation for Transformers, therefore we request to kindly consider IEEMA Price Variation formula for this tender specification also. | The provisions of the Bidding Documents shall remain unaltered and the same shall prevail. |
|  | - | Format for GTP | The format of Guaranteed Technical Particulars of 125 MVA, 420kV Shunt Reactor not given in the tender specification, please provide. | GTP is to be submitted as per CEA standard specification Annexure-C during detailed engineering. However, for subject tender compliance to POWERGRID 400kV Shunt Reactor Specification Annexure-A Technical Parameters may be provided. |