## Clarification No-I
Clarification No-I dated 25.06.2025 to the Bidding Documents of “Power Supply arrangement comprising Solar and BESS as a pilot project for meeting the construction power supply requirement at Pang HVDC station”; Specification No.: CC/NT/W-SOLAR/DOM/A01/25/06750
Sl.No | Existing provision of the Bidding document | Clarification sought by the Bidder | POWERGRID Reply
1 | 1.4 Project location Sl.No Description HVDC Pang UT of Ladakh 1 Altitude 4700 m (Approx.) 2. .................. ----- 3. Minimum temparature -35 Deg. C . . . 20. | As per market standards, all grid-tied inverters are designed to operate at a maximum altitude of 4000 meters and a minimum ambient temperature of -30°C. However, the tender document specifies an altitude of 4700 meters and a minimum operating temperature of -35°C. Kindly confirm if specialized inverter models will be required to meet these site-specific environmental conditions, or if any derating/compensation measures are acceptable. | Inverters shall be suitable for the environmental conditions mentioned at Clause 1.4 of Technical Specifications and shall meet the Technical requirements mentioned at Clause 4.3 . Specilaized Inverter Models and existing models with suitable derating /Compensation measures both shall be accpetable suject to compliance of relevent IEC and IEEE/ANSI standards and Technical specifications.
2 |  | The tender mentions that the PV + BESS system is intended for powering the constructional site. Please clarify what technical or operational provisions must be incorporated in the system to manage scenarios where solar generation exceeds the site’s power/energy requirements. Should the system be designed to curtail excess generation, store it, or is grid export allowed under any operational scenario? | Capacity of Solar with BESS system is derived from Generation and Load Profile as attached as Annexure-A Technical specifications. In line with the Brief Scope of Work mentioned at Cluase No. 2.0 of Section Project, Bidde shall offer a provison for integration with Grid . Accordingly, the proposed integrated system shall have the capability of curtail, store and export the excess generation to Grid , based on the actual load profile of the site , after commissioning.
3 | 1.4 Project location Sl.No Description HVDC Pang UT of Ladakh 1 …................ …............................... 2. 3. . . 8. Nearest Sourec of No Auxiliary power available at site Auxiliary Power. . 20. | As mentioned in tender document, no auxiliary power availability at site. Considering the remote and environmentally sensitive nature of the site, kindly clarify whether there is an existing diesel generators (DG sets) which will be facilitated by PGCIL during project timeline . | As no auxiliary power is available at site, Contractor has to make suitible arrangements for construction power requirements during the period of execution of the Project.
4 | Technical specification; A Electrical System: 1.1 Technical Requirements : ------------------------------ ----------------------------- Supplier Qualification Criteria 1.1.1 The PV Modules Supplier should have supplied minimum 1 MW capacity in the past 5 years (as on the last date of Bid submission). The PV Module supplier shall be Class-I local supplier as per MNRE Order dated 23rd Sep, 2020 on Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of Renewable Energy (RE) Sector. | if the module to be used for this project shall be with solar cell manufactured domestically with Domestic Content Requirement (DCR) i.e. solar cell and solar module both of Domestic Content Requirement (DCR) or domestically manufactured solar modules with any solar cell shall be allowed | As per A.1.1 Technical requirements of Photovoltaic cells of Technical specifications "Photovoltaic Modules shall be domestically manufactured" . Supplier shall also meet the supplier qulification criteria mentioned at A.1.1.1 of Technical specifications