## Sheet1
Clarification No-III dated 25.07.2025 to the Bidding Documents of “Power Supply arrangement comprising Solar and BESS as a pilot project for meeting the construction power supply requirement at Pang HVDC station”; Specification No.: CC/NT/W-SOLAR/DOM/A01/25/06750
Sl.No | Existing provision of the Bidding document | Clarification sought by the Bidder | POWERGRID's Reply
1 |  | Could you please specify the required Capacity Utilization Factor (CUF) and Performance Ratio (PR) for the project? | Performance Ratio(PR) : 82 % Minimum Capacity Utilization Factor (CUF) : 30 % Also refer Amendment No-II.
2 |  | As per the schematic, it is mentioned that Powergrid will provide the space for the LT switchgear. In this regard, we would like to clarify whether the construction and supply of the LT panel is included in the bidder’s scope. If so, does the bidder’s scope also include the supply and installation of control room equipment such as LED lighting, fans, air conditioners, and other related items? | Yes. Please refer Caluse no 7.2 of the Technical Specifications regrading Supply& Installation of LT Panels in the space provided by the Employer No. Bidder scope only includes Supply & Installation of LT Panels
3 |  | We propose to use hybrid string inverters in place of separate DC-DC converters and BESS PCS. Would this configuration be acceptable under the technical specifications of the tender? | Please refer footnotes mentioned at Annexure-B-Schematic of Technical Specifications. Footnote 2 reads as under: "The bidder may propose suitable Schematics for meeting the functional requirement of the Plant i.e 2.1MWp Solar PV with 300kW/ 1200 kWh BESS to meet maximum Construction load of 1000kW"
4 |  | Is there any scope of work related to termination at the HT line under the bidder’s responsibility? | No. HT lines termination is not envisaged under the scope of present contract
5 |  | As per the tender, a load profile and corresponding solar generation profile have been provided. Kindly confirm whether the bidder is responsible for ensuring that the demand-generation gap is fully met through the proposed Solar PV and BESS system. | Capacity of Solar with BESS system is derived from Generation and Load Profile as attached as Annexure-A Technical specifications. Generation-Demand gap shall be within the maximum allowable Energy in kWh , as mentioned in the schematic.
6 |  | Please clarify whether the isolation transformer is to be supplied and installed by the bidder, or if it will be provided by PGCIL. Kindly provide the detailed specifications and requirements for the AC Distribution Board (ACDB), including number of inputs/outputs, rated current, protection components, and metering provisions, to enable accurate estimation and costing | Supply of all the required type & Quantity of transformers required to meet the functional requirements of the Project shall be in the scope of the Bidders. Please refer Cause no. 7.2 of the Technical specifications for indicative requirements and specifications of AC Distribution Board (ACDB)