| S N | Clause | Provision of Bidding Documents | Bidder’s Query | POWERGRID's Reply |
| --- | --- | --- | --- | --- |
|  | Vol-II, Part-B, Appendix-P, Sr.no 21 Pg 25 of 28. | 21. Substation Switches Sr.no -25: Mounting: Rack mounting | 21. Substation Switches Please amend the requirement as DIN RAIL/ RACK Mounting as to offer suitable mounting as per site requirement | Bidders to comply TS. |
|  | Vol-II, Part-B, Appendix-P, Sr.no 21 Pg 25 of 28. | 21. Substation Switches Sr.no -26: Operating temperature 0° to 70° C | ## Please amend the requirement as 0° to 60° C | Bidders to comply TS. |
|  | Vol-II, Part-B, Appendix-P, Sr.no 21 Pg 25 of 28. | 21. Substation Switches Sr.no -27: Dual Power Supply: 110V DC/220V DC (+10% & -15%) (as per site requirement) | 21. Substation Switches Few OEMs offer 48V DC with converter to convert 110V DC/ 220V DC. We understand that this is an acceptable solution. Please confirm | Bidders to comply TS. |
|  | Vol-II, Part-B, Appendix-P, Sr.no 22 Pg 27 of 28. | 22. Router Cum Firewall Sr.no 17: Support IEEE 802.3u, 802.1p, 802.1Q, 802.1d, 802.1w | ## Please relax the 802.1w compliance as it is RSTP (L2 redundancy protocols) which are not expected in firewall being L3 based device. | Bidders to comply TS |
|  | Vol-II, Part-B, Appendix-P, Sr.no 22 Pg 27 of 28. | 22. Router Cum Firewall Sr.no 19: Traffic prioritization for routed IP flows/ports. | 22. Router Cum Firewall Sr.no 19: Traffic prioritization for Internet application based on Priority, Order, Jitter, MoS and Packet | Bidders to comply TS. |
|  | Vol-II, Part-B, Appendix-P, Sr.no 22 Pg 27 of 28. | 22. Router Cum Firewall Sr.no 20: Shall have multicast support such as PIM (Protocol Independent Multicast) | 22. Router Cum Firewall ## Sr.no 20: Please accept IGMP (v1, v2 & v3) as it also comes under Multicast support | Bidders to comply TS. |
|  | Vol-II, Part-B, Appendix-P, Sr.no 22 Pg 27 of 28. | 22. Router Cum Firewall Sr.no 22: Shall have provision to configure multiple IP Sec VPNs, at least 25 nos. Shall support redundant operation with a similar router after creation of all the IP Sec VPN. IPSec VPN shall be with encryption protocols as AES128, AES256 and hashing algorithms as MD5 and SHA1. IPSec VPN throughput - 200 Mbps Threat Prevention Throughput – 50 Mbps | 22. Router Cum Firewall ## Some OEM Firewall throughput is 3.5GBPS and resources are dynamically distrubuted to support the functionalities like IPSec VPN and Threat Prevention. Hence please accept as overall throughput | Bidders to comply TS. |
|  | Vol-II, Part-B, Appendix-P, Sr.no 22 Pg 28 of 28 | 22. Router Cum Firewall Sr.no 28: Shall have subscription for the NGFW services (IPS, Antivirus etc.) till completion of AMC period). | 22. Router Cum Firewall ## Please accept NGFW service with Stateful Packet Inspection , IPSec VPN, IDS etc | Bidders to comply TS. |
|  | Vol-II, Part-B, Appendix-P, Sr.no 22 Pg 28 of 28 | 22. Router Cum Firewall Sr.no 30: Certification: Shall be tested and certified for ISO15408 Common Criteria for least EAL4+. | 22. Router Cum Firewall ## Please accept IEC62443-4-1 & IEC62443-4-2 cyber security certification as well. The IEC62443 is a global standard applicable for cybersecurity of Industrial Control Systems. | Bidders to comply TS. |
|  | Vol-II, Part-B, Appendix-P, Sr.no 22 Pg 28 of 28 | 22. Router Cum Firewall Sr.no 32: Operating temperature: 0° to 70° C | 22. Router Cum Firewall Please amend the requirement as 0° to 60° C. | Router cum Firewall is envisaged for substation environment. Bidders to comply TS |
|  |  |  | Change required as 0° to 40° C. |  |
|  | Vol-II, Part-B, Appendix-P, Sr.no 22 Pg 28 of 28 | 22. Router Cum Firewall Sr.no 33: Dual Power Supply : 110V DC/220V DC (+10% & -15%) (as per site requirement) (Contractor can provide power supply converter suitable to substation environment if required) | Requesting to have Single power supply unit as the devices would work in HA mode and in case of any failure the other device would. | Bidders to comply TS. |
|  | Vol-II, Part-B, Appendix-P, Sr.no 10 Pg 17 of 28 | 10. 82” LED Screen Sr.no; Description of Feature; Minimum Features. 6; Anti-glare & Anti-Static; Yes. 7; Colour Support; 200 Trillion. 8; Brightness; 1800 cd/m2. 9; Contrast Ratio; 8000:1. 10; Response Time; 8ms. 11; Interfaces; HDMI IN x 2, Display Port IN x 2, HDMI OUT x 1, VGAIN x 1, AUDIO-IN x 1, LAN IN x 1, AV IN x 1, AV x 1. 12; Control; RS232-IN x 1, RS232-OUT x 1. 13; Speaker; 10W x 2 (Provision for External Speaker). | 10. 82” LED Screen Datasheet from OEMs of following materials doesn’t provide details asked under Appendix-P (DRS). Sr. no; Description of Feature; Minimum Features. 6; Anti-glare & Anti-Static; To removed.. 7; Colour Support; To removed.. 8; Brightness; To removed.. 9; Contrast Ratio; To removed.. 10; Response Time; To removed.. 11; Interfaces; HDMI OUT/AV IN. 12; Control; To removed.. 13; Speaker; Wattage to be removed. | Refer Amendment-VII |
|  | Vol-II, Part-B, Appendix-P, Sr.no 1 Pg 17 of 28 | Application Communication and Other Servers (VOIP server) | ## Functionality asked can be achieved by appliance-based solution, we request to allow appliance-based solution. Spare hardware related to VOIP server also need to be removed. | Refer Amendment-VII |