| S N | Clause | Provision of Bidding Documents | Bidder’s Query | POWERGRID's Reply |
| --- | --- | --- | --- | --- |
|  | Vol-II Part-A, clause 1.9 (i), Sec-1, Pg.12 of 29 | 1.9. Scope of work A database/display development tool shall be provided for creating database for SCADA, RAS, AFAS, VMS, VoIP, Data Historian, NMS etc. Population & development of complete database & displays including the power system database for SCADA, RAS, AFAS, VMS, VoIP, VPS, Data Historian, NMS, Dashboards and Cybersecurity system etc. is in Contractor’s scope | 1.9. Scope of work We understand here the Power System database is SCADA Database. Kindly confirm. | Bidders to comply TS. |
|  | Vol-II Part-A, Clause 3.7, Sec-3, Pg. 14 of 21 | 3.7 Documentation Where a document is revised for any reason, each revision shall be indicated by a number, date, and description in a revision block along with an indication of official approval by the Contractor’s project manager. Each revision of a document shall highlight all changes made since the previous revision. | 3.7 Documentation ## No capping is defined for document approvals time and no. of revisions. We recommend that any document/drawing shall not exceed 3 revisions, and the document approval time shall be 15 days. | Bidders to comply TS. |
|  | Vol-II Part-B, clause .2. 2.10.1, Sec-2, Pg.31 of 42 | 2.2.10.1. Configuration of the data historian at Main and Backup STAMC The users from substations shall be able to view and download historian reports from the Corporate Historian systems at Main STAMC. | 2.2.10.1. Configuration of the data historian at Main and Backup STAMC As per the BOQ & TS, we understand users from substations shall be able to view & download historian reports from the Corporate Data Historian. What will happen in case of failure/disconnection of Corporate Data Historian in Main STAMC? | Refer Vol-II, Clause 1.5.1 of Section-1, Part-B for methodology for accessing reports from remote substation users. |
|  | Vol-II Part-B, clause 5.2.3, Sec-5, Pg.10 of 25 | Anti-APT (Advanced Persistent Threat): Additional 1no. Hardware Based purpose-built appliance) shall be provided along with 1 pair of Firewall of same OEM at Main STAMC & Back up STAMC for Anti-APT. Anti-APT shall be connected with External Firewalls i.e. Type-I & Type-III. The RTAMCs firewalls shall be integrated with Main STAMC & Back up STAMC’s Anti-APT (Sandboxing) to perform Anti-APT, Sandboxing, Threat extraction, Mail Inspection etc. | Anti-APT (Advanced Persistent Threat): We understand the hardware appliance asked in the respective clause is for Anti-APT Sandbox appliance. Kindly confirm. | Bidders to comply TS. |
|  | Vol-II Part-B, clause 5.9, Sec-5, Pg.15 of 25 | Type Test Reports shall be provided for VPS and accessories during engineering approvals. The Type Tests should have been carried out at nationally/internationally accredited labs. | Request POWERGIRD to amend this clause and allow relevant BIS certificates to be submitted in place of Type Test reports. | Refer Amendment-1 |
|  | Vol-II Part-B, Clause 6.0, Sec-6, Pg.3 of 12 | 6.0 Redundancy Web cum Replica Data Server system shall be configured as redundant | 6.0 Redundancy As per the specification web cum replica data server shall be redundant but only 1 Replica server is mentioned in BOQ. Bidder request to amend the BOQ by adding 1 more replica server. | Refer Vol-II, Para-1 at Clause 1.5.1 of Section-1 & Clause 2.1.1 of Section-2 of Part-B. |
|  | Vol-II Part-B, Appendix-G, Pg.1 of 25 | General Query | We understand that Backup STAMC shall have the same capabilities like Main STAMC & shall be equipped with dedicated servers. But as per the Hardware BOQ ,only 1EA Unit of PMS server mentioned in Backup STAMC, whereas 2 EA unit of PMS Server is mentioned in Main STAMC. There is no concept of redundancy. Kindly confirm. | Refer Amendment-1 |
|  | Vol II Part-C, Appendix-A, Pg.1 of 9 | General Query | Pls Confirm DR collection and Remote Accessibility is required only for upstream bays. | Refer Vol-II, Part-C, Clause-1.2 & Appendix-A of Part-C for List of Substations with Bay details for DR Collection. |
|  | Vol II Part-E, Clause 1. Pg.4 of 36 | 1.Introduction Further, OPTCL has already installed and commissioned a CCTV system with few IP cameras and a Network Video recorder in various substations under Operation. Functionally similar systems are also being installed in some of the new stations. The existing Cameras installed at the respective substations are to be integrated with the Visual Monitoring System. | 1.Introduction We request you to share the detail of the existing cameras such as Make and Model and technical specifications. | Please refer Appendix-A of Part-E for number of existing cameras. The make & model of existing cameras shall be as per Detail Engineering based on Survey. Bidders to comply TS. |
|  | Vol II Part-E, Clause 3 (h), Pg.5 of 36 | 3. Design Criteria VMS system shall be able to exchange information through published API as well as web services in Simple Object Access Protocol (SOAP) and Representational State Transfer (REST) architectural style using high-level programming languages (preferably Python). These APIs along with SOAP & REST web services shall be well documented and the source code for the same shall be supplied along with the system. | 3. Design Criteria We understand that as part of the project scope, we need to integrate VMS systems with third-party systems. Further, these integrations can be done via API, REST/SOAP API, or another way to integrate the systems, and it is not mandatory to integrate only the systems via SOAP and REST. we request you to Kindly amend this clause as “VMS system shall be able to exchange information through published API as well as web services in Simple Object Access Protocol (SOAP)/ Representational State Transfer (REST) architectural style using high-level programming languages (preferably Python). These APIs along with SOAP/REST web services shall be well documented and the source code for the same shall be supplied along with the system". | Bidders to comply TS. |
|  | Vol II Part-E, Clause 3.1, Pg.5 of 36 | 3. 1 Functional Requirement NVR shall have the capability/provision to support a minimum of 50 cameras in each NVR. | 3. 1 Functional Requirement As we understand, 50 camera connection licenses and 50 video analytics licenses have to be considered at each substation location. Kindly confirm if our understanding is correct. | Bidders to comply TS. |
|  | Vol II Part-E, Clause 3.2, Pg.6 of 36 | 3.2 Visual Monitoring System Architecture The Visual Monitoring System shall be hierarchical in nature based on distributed architecture multi-server, synchronized database solution designed for the Company with multiple facilities spread across large geographical areas as shown in figure-1. | 3.2 Visual Monitoring System Architecture As we understand, the synchronized database solution functions as follows: For instance, when users create accounts or modify camera configurations at STAMC centers, these changes are automatically synchronized with RTAMC and Substation servers. Users at STAMC are given the highest priority, followed by RTAMC and local substation levels. Furthermore, users with high-priority permissions can assume control of the cameras. Kindly confirm if our understanding is correct. | Bidders to comply TS. |
|  | Vol II Part-E, Clause 3.2, Pg.7 of 36 | 3.2 Visual Monitoring System Architecture Level -I: Main STAMC & Back up STAMC The Servers and Applications for VMS system shall be installed at both Main and Backup Control Centre in redundant configuration in hot standby mode. The hot standby server shall takeover in the event of failure of active server. Applications at Back-up shall takeover after failure of both the servers/Applications at Main STAMC. The databases at Main STAMC and Back-up STAMC shall be synchronized at least once in every hour. | 3.2 Visual Monitoring System Architecture As we understand, sufficient network bandwidth should be provisioned according to our recommendation to ensure seamless data transfer between STAMC and Backup STAMC . Kindly confirm if our understanding is correct. | Refer Vol-II, Clause-1.6 of Section-1, Part-A (Pg. 8 of 29) for bandwidth details. Bidder to comply with TS |
|  | Vol II Part-E, Clause 3.2, Pg.7 of 36 | 3.2 Visual Monitoring System Architecture Typical Architecture of Main STAMC There shall be dedicated client workstations for performing the functions of VMS system at Main STAMC and Back up STAMC, The Video wall installed for SCADA at Main STAMC and Back up STAMC shall also be used for performing the functions of VMS system. | 3.2 Visual Monitoring System Architecture How many dedicated client workstations are envisaged in the STAMC and Back up STAMC for VMS functionality? | Refer Vol-II, Clause-5.2.6 of Section-5, Part-B for tentative break-up of workstations at Control Centres. Bidder to comply with TS |
|  | Vol II Part-E, Clause 3.2, Pg.8 of 36 | 3.2 Visual Monitoring System Architecture Level -II: Regional Transmission Asset Management Centers (RTAMCs) At RTAMC end, Failover NVR server shall serve as a back-up/failover hardware to the Network Video Recorders of the Substation Network Video Recorder (NVR) of a region. Along with Failover NVR there shall be dedicated client work stations for performing the functions of VMS system at RTAMCs | 3.2 Visual Monitoring System Architecture As we understand, RTAMC servers are provided as a backup for sub-station levels under the jurisdiction of the respective RTAMC. Whichever server at the substation goes offline or down, this backup server takes over the VMS functionality. Once the substation-level VMS server comes back online, the video recording operation is reinstated on the substation-level server, and it is assumed that each RTAMC server can provide backup for just one substation server at a time. Kindly confirm if our understanding is correct. | Bidders to comply TS. |
|  | Vol II Part-E, Clause 3.2, Pg.8 of 36 | 3.2 Visual Monitoring System Architecture Level -II: Regional Transmission Asset Management Centers (RTAMCs) At RTAMC end, Failover NVR server shall serve as a back-up/failover hardware to the Network Video Recorders of the Substation Network Video Recorder (NVR) of a region. Along with Failover NVR there shall be dedicated client workstations for performing the functions of VMS system at RTAMCs | 3.2 Visual Monitoring System Architecture Kindly confirm if there would be any hot stand by server within the RTAMC for the failover server of substations? | Refer Vol-II, Part-E, Sr.no-3 of Clause-3.14 at Page 26 of 36 & Typical RTAMC Architecture at Page 8 of 36. Bidders to comply TS. |
|  | Vol II Part-E, clause 3.2, Pg.8 of 36 | 3.2 Visual Monitoring System Architecture At Substation end, Network Video Recorder (NVR) shall be installed to continuously record the video from the cameras installed at all the substations. One client PC along with the required software shall be provided at these substations to perform all VMS functions. | 3.2 Visual Monitoring System Architecture How many dedicated client workstations are envisaged at the substation level for VMS functionality? | Refer Vol-II, Clause 3.2 of Part-E. Bidders to comply TS. |
|  | Vol II Part-E, Clause 3.2 Pg.8 of 36 | Level -II: Regional Transmission Asset Management Centers (RTAMCs) | At the substation end, multiple servers will be provided with a single failover server at the jurisdiction of the respecting RTAMC, following an N:1 redundancy configuration. Kindly confirm if our understanding is correct. | Bidder to Comply with TS. |
|  | Vol II Part-E, Clause 3. 3, Pg.9 of 36 | 3. 3 System sizing and Expandability The Video Management System shall be sized such that they can accommodate 100% expansion of the present requirement in number of devices (Cameras, NVR, equipment) connected to it and 100% expansion in number of remote clients. The present requirement stands for 210 NVR, 2000 Cameras (Cameras that shall be supplied under this project, existing cameras) and 210 numbers client at Substations. | 3. 3 System sizing and Expandability As we understand, the proposed solution should be scalable up to 10500 cameras (considering to support 50 cameras per location). Additionally please clarify whether the software license should be considered for 4000 cameras, as its asked for 100% expansion. Request you to please clarify. | The scalability is required up to 4000nos cameras, 420nos NVR & 420nos Client. However, NVR shall be sized to support minimum 50nos. cameras. Bidder to Comply with TS. |
|  | Vol II Part-E, Clause 3. 3, Pg.9 of 36 | 3. 3 System sizing and Expandability Processor and database sizing at Main and Back up Control Centre server needs to be sized considering 100 alarms/2500 events per day per substation for Visual Monitoring System | 3. 3 System sizing and Expandability The definition of 100 alarms or 2500 events per day per substation is not clear. As per our understanding, the 100 alarms refer to VA alerts/alarms, with each alert/alarm requiring at least 1 associated image and a 10-second video clip as pre and post-event footage. However, we would appreciate further clarification regarding the concept of 2500 events per substation per day. Could you please specify the nature of these events? | Refer Vol-II, Clause-3.2, last para of “Level-I- Main STAMC & Back up STAMC” at Page 8 of 36 for “storage of video clipping” . Alarms meant for Camera Offline/ Online etc. and Events are meant for Intrusion detected, Motion Detection etc. However, the details shall be finalized during detailed engineering. |
|  | Vol II Part-E, clause 3.3. Pg.9 of 36 | 3.3. System sizing and Expandability The Video Management System shall be sized such that they can accommodate 100% expansion of the present requirement in number of devices (Cameras, NVR, equipment) connected to it and 100% expansion in number of remote clients. The present requirement stands for 210 NVR, 2000Cameras (Cameras that shall be supplied under this project, existing cameras) and 210 numbers client at Substations. | 3.3. System sizing and Expandability As we understand, proposed solution should be scalable to support upto 10500 cameras (considering to support minimum 50 cameras per location). The license to be supplied is 2000 or to be considered 50 VMS per NVR. Kindly clarify. | Refer Sr.no 19. |
|  | Vol II Part-E, Clause 3. 3, Pg.9 of 36 | 3. 3 System sizing and Expandability Online storage for VMS servers in SAN system shall be considering storage of all alarm and event logs for a period of 3 months. It shall automatically overwrite after utilization of 70% of total memory. However, all the events and alarm logs shall be available in archive system for a period of 1 year. It shall be possible to export the data to off-line storage devices in a text/csv format. | 3. 3 System sizing and Expandability Please clarify as where is the archive system planned? As a part of VMS is there any NAS Box required at STAMC? Where these logs to be maintained? AT STAMC, RTAMC or substations? | Bidder to Comply TS. |
|  | Vol II Part-E, Clause 3.8 (f), Pg.13 of 36 | 3. System Requirements for Visual Monitoring System The software shall have inbuilt facility to store configuration of Network Video recorders and cameras So that in case of replacement of faulty NVR and camera the settings can be pushed directly from the central VMS application. | 3. System Requirements for Visual Monitoring System we understand that NVR configuration data such as camera settings etc. has to be restored, in case of replacement of a faulty NVR. Kindly confirm if our understanding is correct. | Bidder to Comply TS. |
|  | Vol II Part-E, clause 3.8 (5.h) Pg.17 of 36 | 5.Live Video Modify video analytics settings and tuning for: • Video motion detection • Object tracking • Object classification | 5.Live Video Does object tracking mean that the PTZ has to follow a moving object in its FOV. Kindly confirm if our understanding is correct. | Bidders to comply TS. |
|  | Vol II Part-E, clause 3. 9, Pg.20 of 36 | 3. 9 Video Management Video Management Application of VMS System shall be capable to configure Users, Roles, Devices, etc. The application shall have a facility to integrate with the Authentication Server provided under Part-B, Section-1, Para 1.7. The application shall contain a database of all network-connected cameras, NVRs, clients’ workstations, client licenses, etc., and their configuration settings. | 3. 9 Video Management Kindly provide the detailed technical specification for the authentication server as we are unable to locate the detailed technical specification as outlined in Part-B, Section-1, Paragraph 1, as it appears to be missing. Request you to please clarify. | Refer Vol-II, Clause-1.7 of Section-1, Part-B. (Refer PDF 2_Vol-II Part-B (Part 2 of 4)) |
|  | Vol II Part-E, Clause 3.14, Pg.24 of 36 | 3. 14 Technical Specifications of Network Video Recorder (NVR) The Network video Recorder shall be located at each of the substations and all the camera recording shall be done locally. It shall be possible to store data for at least 15 days locally and can be viewed & playback from remote through client licensee. The NVR application software and hardware shall comprise of a single unit. | 3. 14 Technical Specifications of Network Video Recorder (NVR) There is no video analytics server being asked in the RFP Technical specification. Please consider adding a minimum of one Analytics Server per substation, each meeting the following computing requirements" 8 cores at 2.2 GHz or higher, 32 GB of RAM, 500 GB HDD/SSD, 1 X Nvidia RTXA4000 GPU card with 16 GB of memory, an operating system of Linux Ubuntu, and 6 TB of usable storage for VA event". Request you to please confirm. | Bidders to comply TS. |
|  | Vol II Part-E, Clause 3.14, Pg.26 of 36 | The Back-up/Failover NVR shall be located at each of the RTAMCs and Back-up STAMC cum RTAMC. Respective RTAMC location NVR shall act as a back-up for failed NVR of the substation under jurisdiction of the respective RTAMC. Back-up NVR at Back-up STAMC shall act as a back-up for failed NVR of the substation under West zone RTAMC jurisdiction. Back up NVR shall have the same feature as specified above for NVR. | As we understand, RTAMC servers are provided as a backup for sub-station levels under the jurisdiction of the respecting RTAMC. Whichever server at the substation goes offline or down, this backup server takes over the VMS functionality. Once the substation-level VMS server comes back online, the video recording operation is reinstated on the substation-level server. Additionally, the recorded video data from the failover NVR/server at the RTAMC center will be synchronized back to the respective substation server/NVR. Request you to please confirm our understanding. | Bidders to comply TS. |
|  | Vol II Part-E, Clause 5.1, Pg.30 of 36 | The contractor shall supply a comprehensive Video Content Analysis (VCA) solution in the proposed Visual Monitoring system. These VCA are to be provided for all the cameras envisaged under this project. The VCA software shall be part of the Visual Monitoring System, any additional hardware if required shall be in the scope of the contractor without any financial implication to Employer. The VCA software shall have following features: | We kindly request that you provide us with detailed break up of video analytics use cases per substation. This information will allow us to determine the appropriate computing power per substations. | Bidders to comply TS. |
|  | Vol II Part-E Clause 6, Pg.33 of 36 | 6.Integration with existing CCTV system The VMS Solution shall be capable for integration of existing cameras which are IP based. The tentative no. of existing cameras are enclosed in Appendix- A of Part-E. The details of existing camera shall be finalized during detail engineering based on survey details submitted by Contractor. The required license for integration at control center end is in the scope of Contractor. | 6.Integration with existing CCTV system We request that you share the details of the existing cameras, such as the make and model and technical specifications. Additionally, there are a few models that are not ONVIF compliant, obsolete and even the brand itself is not existing anymore. Please confirm how the support for APIs or SDKs is expected on those cameras. | Refer Sr.no-9 for clarification regarding make & model of existing cameras. Refer Vol-II, Part-E, Sr.no-1 of Clause 3.8. |
|  | Vol II Part-E, Clause 7.2. Pg. 35 of 36 |  | This clause is usually applicable for SCADA or other low compute requirement systems. If we anticipate about 30% utilization post 50 cameras loading, then compute has to be planned for at least 150 cameras which will lead to higher specifications and compute requirements. Kindly confirm if our understanding is correct. | Bidders to comply TS |
|  | Vol II Part-E, Clause 3.8, Pg.17 of 36 | Additional recommended point | The proposed VMS software should have been tested successfully by a government agency to verify the security of all the information access points, including the API services, thick client, and web client. The test should have been performed to identify vulnerabilities, OWASP security risks and should have included a code review of the application and the third-party dependencies such as libraries and components, if any. Documentary evidence must be furnished to ascertain the software's information security resilience. | Bidders to comply TS |
|  | Vol II Part-E, Clause 3.8, Pg.17 of 36 | Additional recommended point | The OEM should have ISO 27001:2013, ISO 14001:2015, CMMI Level 3 and ISO 9001:2015 certifications. | Bidders to comply TS. |
|  | Vol II Part-E, clause 3.8, Pg.17 of 36 | Additional recommended point | Considering the project scope, it is strongly recommended to have the solution from a single OEM for seamless operation. Therefore, we request that you please amend this clause as follows: "VMS should be from the same OEM as video analytics for seamless integration." | Bidders to comply TS. |
|  | Vol II Part-E, Clause 3.8, Pg.17 of 36 | Additional recommended point | Considering the criticality of surveillance project, operator chat functionality to exchange the information for effective surveillance is a must feature. We strongly recommend to consider the following clause : "The system should have collaborative vigilance functions. It should offer chat room for exchange of information such as text messages, user selectable files, archived video link, camera layouts, incident snap, clip and VA alerts for collaboration among the operators. The chat window should show color coded status for messages which are sent, delivered and read. The administrator should have access to all the messages being exchanged among the operators. To assist in collaborative investigation of an event, the operator should have the function of sharing the camera matrix with a mix of live as well as playback videos to the fellow operators or to the Supervisor. This function should also allow sharing an event along with event video, stitched video of a matrix recorded on the operator workstation, any other video clips received from external sources, etc." | Bidders to comply TS. |
|  | Vol-II Part-A, Clause 1.13.6, Sec-1, Pg.28 of 29 | Additional recommended point | We request POWERGRID to kindly allow bidder to propose self developed/New RAS product for a more competitive bid. The bidder proposed RAS product may be allowed to run for a certain period of time for performance checking and payment may be made only after successful operation. | Bidders to comply TS. |
|  | Vol-II Part-A, Clause 1.13.7, Sec-1, Pg.28 of 29 | Additional recommended point | We request POWERGRID to kindly allow bidder to propose self developed/ New AFAS Solution for a more competitive bid. The bidder proposed AFAS solution may be allowed to run for a certain period of time for performance checking and payment may be made only after successful operation. | Bidders to comply TS. |