| SL. NO. | CLAUSE / DWG NO. | Clause Description | QUERY DESCRIPTION | CLARIFICATION |
| --- | --- | --- | --- | --- |
|  | Section- 765kV Auto Transformer ( Rev.08) Clause no. 6.1.8 | Tank MS plates of thickness >12 mm should undergo Ultrasonic Test (UT) to check lamination defect, internal impurities in line with ASTM 435 & ASTM 577. | Ultrasonic test shall be done on Raw material at tank supplier end. | Noted. |
|  | Section- 765kV Auto Transformer ( Rev.08) Clause No. 6.1.10.b | Specific area shall not be provided for jacking pad in the foundation as jacking shall be done by laying temporary metal plates size 400 mm x 400 mm x 32 mm (min) thick. One set of metal plates for jacking of Transformer shall be provided by manufacturer. | Bidder will provide pressure of the jacking point. Design of Metal plate (Size, thk. & Load bearing capacity) shall be decided by foundation/customer civil engineer. | Bidder has to supply metal plates as per the requirement of bidding document. |
|  | Section- 765kV Auto Transformer ( Rev.08) Clause no. 6.4 | The rail track gauge shall be 1676 mm. Four rails shall be provided as per the drawing mentioned in Annexure-C. | Rails shall not be in bidder scope. Please confirm Also, drawing referred in Annexure C is not available with the given specification Rev08. Kindly provide the drawing. | Regarding Rails, bidder understanding is correct. Drawing referred in Annexure-C is available at page 80 of 156 of Technical Specification. |
|  | Section- 765kV Auto Transformer ( Rev.08) Clause no. 6.4 | All fittings (Foundation bolts, supports, embedded plates if any) including anchor fastener with chemical grouting are in the scope of contractor. | Kindly accept mechanical grouting also. (Anchor Fastener) | Bidder to comply the requirement of bidding document. |
|  | Section- 765kV Auto Transformer ( Rev.08) Clause no. 6.9 & 6.10 | Plug & socket type arrangement with factory fitted cable of adequate length shall be supplied by OEM | For the factory fitted cable, length variation due to the practical laying of cable at site up to marshaling box may initiate joint in control cable, which is not recommended by bidder. Hence suggesting to allow connection of plug & socket at site. | Bidder to comply the requirement of bidding document. |
|  | Section- 765kV Auto Transformer ( Rev.08) Clause no. 13.2 | Sufficient number of thermometer pockets fitted with captive screw cap on the inlet and outlet of tank side pipe of cooler bank shall be provided to record temperature during temperature rise test. Suitable arrangement shall be made for bank mounted cooler arrangement. | Thermometer Pocket on 80 NB pipe will restrict the oil flow, Hence, requesting the same shall be provided on common Header & not for all radiators. | Thermometer pockets at bottom header (pipe of cooler bank) may be provided in line with Technical Specification. |
|  | Section- 765kV Auto Transformer ( Rev.08) Cl. No 13.4.3 | Auxiliary power supply distribution scheme shall be submitted for approval. Supply and laying of Power, Control and special cables from common marshaling box to individual MB/Cooler Control Cubicle (including spare unit) & further distribution from IMB/CCC to all accessories is in the scope of the contractor. Further any special cable (if required) from CMB to Owner’s Control Panels/Digital RTCC panels are also in the scope of the contractor. | Pl share distance from CMB to control room, cable trench layout to be provided | Detailed information shall be provided to the successful bidder during detailed Engineering. However, an approximate length of 700 meter may be considered from CMB to Control Room. |
|  | Section- 765kV Auto Transformer ( Rev.08) Clause No. 13.5.8 | Valve Sr. No. Type 6) Sudden pressure relay - Gate 7) OLTC-tank equalizing valve - Gate/Needle 8) OLTC drain cum filling valve - Gate 10) Conservator Drain valve - Gate 12) Valve for Conservator vacuum (top) - Gate | Kindly accept our comment as below for the type of valve. 6) Valve is not recommended by bidder. 7) Gate / Globe / Ball / Needle 8) Gate / Globe 10) Gate / Globe 12) Gate / Globe | Bidder to comply the requirement of bidding document. |
|  | Section- 765kV Auto Transformer ( Rev.08) Clause No. 16 | SCADA Integration and Interconnection | We will provide 4-20mA output for OTI, WTI. Kindly accept | For OTI & WTI 4-20mA output is acceptable. However, bidder to comply SCADA Integration and Interconnection in line with the requirement of bidding document. |
|  | Section- 765kV Auto Transformer ( Rev.08) Clause No. 16.1.1 & 16.1.2 | All required power & control cables including optical cable, patch chord (if any) upto Common MB shall be in the scope of contractor. Further, any special cable between CMB to switchyard panel room/control room shall be under the present scope. All cable from RTCC to OLTC Drive Mechanism Box shall be provide (if applicable). Fiber optic cable, power cable, control cables, as applicable, between CMB to switchyard panel room/control room and power supply (AC & DC) to MB and integration of above said IEC-61850 compliant equipment with Substation Automation System shall be under the scope of EPC contractor | All power & control cables from transformer / Reactor accessories to marshaling box shall be in Bidder's scope of supply. Any other control cable / Power cable / FO cable / special cable and accessories shall not be in Bidder's scope. Kindly confirm. | Please refer to Clause 2.2.1 (c) of Section Project for scope of Cable. |
|  | Section- 765kV Auto Transformer ( Rev.08) Clause No. 18 x | Fibre optic sensor based temperature measuring system (if applicable) | Fiber optic sensor based temperature measuring system is removed from the scope as per section project. Hence all relevant clauses are not applicable. Kindly confirm | Noted. |
|  | Section- 765kV Auto Transformer ( Rev.08) Clause No. 26.3 | Type Tests on fittings: 1) Bushing Type Test as per IS/ IEC:60137 for all voltage class (Seismic test on 400kV and 800kV Bushings) 2) OLTC (as per IS 8468 / IEC:60214 including IP-55) 3) Marshaling & Common Marshaling Box and other outdoor cubicle (IP-55) 4) RTCC (IP-43) | Seismic test on bushings shall be conducted inline with requirement however there will be delay in delivery of bushings. Requested PGCIL to accept seismic calculations | Bidder to comply the requirement of bidding document. |
|  | Section- Project ( Rev.0) Clause No. 2 (i) & Clause No. 2.2.1 (d) | These transformers bank will be connected with common spare ICT unit, which is already existing. Existing Spare Transformer shall be used with this transformer bank. | Connection of main unit to spare unit is excluded from bidder's scope. Kindly confirm | Interconnection of control cables of spare unit with main unit at CMB /RTCC panel /SPR (as applicable) in line with technical specification shall be in the scope of bidder. |
|  | Section- Project (Rev.0) Clause 2 (i) & Clause No. 2.2.1 (b) | At Bhadla-II, necessary integration with existing Digital RTCC for this bank is under present scope. Digital RTCC panel with relay for present ICT is existing. Wiring & Integration of the same for above ICT is in present scope of work. (Each digital RTCC relay shall be used to control 1 bank of transformers (i.e. 3 Nos. 1-Phase units or 1 No. 3-Phase unit).Cost of the same shall be built in Installation cost of Auto –Transformer. | Request PGCIL to provide make and details of existing digital RTCC relays and requirement of no of relays & panel in this bid | Bidder to quote as per provisions of bidding document. Make/model of existing RTCC Relay is of M/s Pradeep Sales. |
|  | Section- Project (Rev.0) Clause No. 2.2.1 (e) | Specified Impedance of Transformers which are existing / being procured under separate package and are to be operated in parallel of these transformers is same as specified under subject package. However measured values of those transformer impedances shall be shared during detailed engineering. | As we do not have any details of existing transformer, Kindly provide the existing transformer details e.g. Rating and diagram plate etc. Offered transformer can be run in parallel with identical technical parameter i.e. same voltage rating, same polarity, same percentage impedance and same phase sequence. | Please refer Technical Particulars / Parameters of Transformers mentioned at Annexure-A 1.0 of Technical Specification. |
|  | Section Project - Cl. No. 2.2.1 | d. Existing Spare Transformer shall be used with this transformer bank. e. Specified Impedance of Transformers which are existing / being procured under separate package and are to be operated in parallel of these transformers is same as specified under subject package. However measured values of those transformer impedances shall be shared during detailed engineering. | We understand that the offered transformers are to be operated with the existing ICT at site, please specify whether existing Transformer is with OLTC Or Without OLTC. If with OLTC, whether we have to consider the OLTC for the present transformers or not. If OLTC is to be considered for the present transformer, Request you to kindly provide the Tapping Range. | Please refer Technical Particulars / Parameters of Transformers mentioned at Annexure-A 1.0 of Technical Specification. |
|  | Section Project - Cl. No. 2.2.1 | b. Digital RTCC panel with relay for present ICT is existing. Wiring & Integration of the same for above ICT is in present scope of work. (Each digital RTCC relay shall be used to control 1 bank of transformers (i.e. 3 Nos. 1-Phase units or 1 No. 3-Phase unit).Cost of the same shall be built in Installation cost of Auto –Transformer. | We understand that Digital RTCC relays for present scope of 3Nos. X 500MVA, 765/400kV 1-Ph ICT are already existing at site, bidder has to only consider the Wiring for the same. We request you to kindly provide the Digital RTCC Make and Model. | Bidder’s understanding is generally in order. Make/model of existing RTCC Relay is of M/s Pradeep Sales. |