| SL. NO. | CLAUSE / DWG NO. | Clause Description | QUERY DESCRIPTION | CLARIFICATION |
| --- | --- | --- | --- | --- |
|  | General / Cable Route Length | …………………………… | Request you to kindly provide the existing layout of substation by showing the location of new transformers, existing spare transformer MB & existing Digital RTCC Panel or request you to please provide the cable route length for below mentioned location:- - From Existing Spare Transformer MB to New CMB transformer. - From Existing RTCC panel to New CMB transformer. - From CRP Room to New CMB transformer. | Please refer to Clause 2.2.1 (c) of Section Project for scope of Cable. Further, bidder is requested for Site visit for any further Clarity. |
|  | Section Project - Cl. No. 2.2.1 | d. Existing Spare Transformer shall be used with this transformer bank. e. Specified Impedance of Transformers which are existing / being procured under separate package and are to be operated in parallel of these transformers is same as specified under subject package. However measured values of those transformer impedances shall be shared during detailed engineering. | We understand that the offered transformers are to be operated with the existing ICT at site, please specify whether existing Transformer is with OLTC Or Without OLTC. If with OLTC, whether we have to consider the OLTC for the present transformers or not. If OLTC is to be considered for the present transformer, Request you to kindly provide the Tapping Range. POWERGRID Reply:- Please refer Technical Particulars / Parameters of Transformers mentioned at Annexure-A 1.0 of Technical Specification. Query: The mentioned clause Annexure- A 1.0 of technical specification Rev 08 which refers to “technical particulars of transformer without OLTC”, but as per section project scope cl.no:2.2.1 it is mentioned “Digital RTCC panel with relay for present ICT is existing. Wiring & Integration of the same for above ICT is in present scope of work” which requires a OLTC. Please confirm OLTC requirement, if OLTC is applicable for this project referred clause shall be Annexure A 2.0 of technical specification, please confirm. | Please refer to Clause 2.2.1 (b) of Section Project where scope of Digital RTCC is clearly mentioned. Therefore, Transformer with OLTC is to be considered accordingly. |
|  | Section- Project (Rev.0) Clause No. 2.2.1 (e) | Specified Impedance of Transformers which are existing / being procured under separate package and are to be operated in parallel of these transformers is same as specified under subject package. However measured values of those transformer impedances shall be shared during detailed engineering. | As we do not have any details of existing transformer, Kindly provide the existing transformer details e.g. Rating and diagram plate etc. Offered transformer can be run in parallel with identical technical parameter i.e. same voltage rating, same polarity, same percentage impedance and same phase sequence. POWERGRID Reply: Please refer Technical Particulars / Parameters of Transformers mentioned at Annexure-A 1.0 of Technical Specification. Query: Please note that referred Technical Particulars / Parameters of Transformers mentioned at Annexure-A 1.0 of Technical Specification is for Transformer without OLTC. We understand that since, integration with existing RTCC panel is required, hence Transformer shall be of with OLTC and technical details shall be as per Annexure-A 2.0 of Technical Specification instead of Annexure-A 1.0. Kindly confirm. | Please refer to Clause 2.2.1 (b) of Section Project where scope of Digital RTCC is clearly mentioned. Therefore, Transformer with OLTC is to be considered accordingly. |
|  | Section Project - Cl. No. 2.2.1 | d. Existing Spare Transformer shall be used with this transformer bank. e. Specified Impedance of Transformers which are existing / being procured under separate package and are to be operated in parallel of these transformers is same as specified under subject package. However measured values of those transformer impedances shall be shared during detailed engineering. | We understand that the offered transformers are to be operated with the existing ICT at site, please specify whether existing Transformer is with OLTC Or Without OLTC. If with OLTC, whether we have to consider the OLTC for the present transformers or not. If OLTC is to be considered for the present transformer, Request you to kindly provide the Tapping Range. POWERGRID Reply: Please refer Technical Particulars / Parameters of Transformers mentioned at Annexure-A 1.0 of Technical Specification. Query: Please note that referred Technical Particulars / Parameters of Transformers mentioned at Annexure-A 1.0 of Technical Specification is for Transformer without OLTC. We understand that since, integration with existing RTCC panel is required, hence Transformer shall be of with OLTC and technical details shall be as per Annexure-A 2.0 of Technical Specification instead of Annexure-A 1.0. Kindly confirm. | Please refer to Clause 2.2.1 (b) of Section Project where scope of Digital RTCC is clearly mentioned. Therefore, Transformer with OLTC is to be considered accordingly. |