| SL. NO. | CLAUSE / DWG NO. | Clause Description | QUERY DESCRIPTION | CLARIFICATION |
| --- | --- | --- | --- | --- |
|  | Section Project - Cl. No. 2.2.1 | d. Existing Spare Transformer shall be used with this transformer bank. e. Specified Impedance of Transformers which are existing / being procured under separate package and are to be operated in parallel of these transformers is same as specified under subject package. However measured values of those transformer impedances shall be shared during detailed engineering. | We understand that the offered transformers are to be operated with the existing ICT at site, please specify whether existing Transformer is with OLTC Or Without OLTC. If with OLTC, whether we have to consider the OLTC for the present transformers or not. If OLTC is to be considered for the present transformer, Request you to kindly provide the Tapping Range. POWERGRID Reply:- Please refer Technical Particulars / Parameters of Transformers mentioned at Annexure-A 1.0 of Technical Specification. Query: The mentioned clause Annexure- A 1.0 of technical specification Rev 08 which refers to “technical particulars of transformer without OLTC”, but as per section project scope cl.no:2.2.1 it is mentioned “Digital RTCC panel with relay for present ICT is existing. Wiring & Integration of the same for above ICT is in present scope of work” which requires a OLTC. Please confirm OLTC requirement, if OLTC is applicable for this project referred clause shall be Annexure A 2.0 of technical specification, please confirm. | Please refer to Clause 2.2.1 (b) of Section Project where scope of Digital RTCC is clearly mentioned. Therefore, Transformer with OLTC is to be considered as per Annexure A 2.0 of Section 765kV Auto- Transformer (Rev.08). |
|  | Section- 765kV Auto Transformer( Rev.08) Clause No. 18 (V) | On-line insulating oil drying system included with each Transformer. | Section–Project/Rev 00 Cl.no: 3.0 Exclusions & C/ENGG/SPEC/SEC- PROJECT/SPECIFIC REQUIREMENT Rev. no 06 in Annexure-II. Online dry out system does not mention in exclusions of both the specifications, kindly confirm the requirement, as it is required to be considered as per technical specification R08. | On line Insulating Oil drying System is not considered in present scope. Bidder to quote as per BPS. |