|  | Section Project & Price Schedule, Schedule 3, sl no. 36, 99 & 121 | PLCC Modification | Modification of Existing CRP and PLCC Panels for lines under the present supply scope. In this regards, kindly note that the frequency change in a same PLCC panel for different communication mode is not possible. One set of PLCC panel (one for each line) can only be tuned for one frequency either for F1 or F2.Hence for the requirement under the present scope, we have to supply the new PLCC Panel for all the lines. Hence you are requested to revise the supply price schedule accordingly with the actual requirements. | In bypass mode, for teleprotection purpose, signal transfer is to be achieved by suitable schematic arrangement with the help of existing panel. |
| --- | --- | --- | --- | --- |
|  | Section Project, 3.2.1.1, vii | Protection coupler | Protection coupler “Spare channel in Spare Output code in protection coupler shall be wired to send signal “Bay in bypass mode” to remote end.” This requires a continuous transmission of command (spare) in protection coupler to remote end indicating bay in bypass mode. Continuous transmission of commands is not feasible in protection coupler (with PLCC) as the equipment is designed to block the transmission if the command persists for more than few seconds. Please clarify. | Status change for two modes mentioned in the said Clause is to be communicated. |
|  | Amendment No-II, SL No.-12 | 400kV Hissar | Further Bhiwani PG (Via Bhiwani BBMB) – Hissar (PG) 400kV line and Moga (Via Fatehabad) – Hissar (PG) 400kV line shall be bypassed at Hissar substation by closing tie breaker and opening both the main breakers. During operation, following two modes of operation are envisaged. (i) Bhiwani PG (Via Bhiwani BBMB) – Moga (Via Fatehabad) 400kV line in bypass condition by closing Tie Breaker. (ii) Bhiwani PG (Via Bhiwani BBMB) – Moga (Via Fatehabad) 400kV line will be connected to Hisar Buses when main breakers are in closed positions The first mode of operation is applicable only if both lines are in same dia and both have common Tie breaker. But as per Tender stage SLD & Layout, it is observed that One diameter consists of Moga-1 Line-Tie-Patiala Line and another different diameter consists of 315MVA ICT-1-Tie-Bhiwani Line. Hence we understand that Moga-1 Line & Bhiwani Line can be bypassed from Hissar SS only by closing of Line bypass Isolators as shown in SLD. Please confirm the same. | At Hisar S/s following lines will be operated in two modes as specified in Sl. no 12 of Amendment-II. - Hisar - Bhiwani –1 (BBMB) & HIsar-Fatehabad TL (bypassing to be achieved by Tie CB closing and main CB opening). - Hisar – Bhiwani (PG) & Hisar Moga-I (Bypassing is to be achieved by isolator to be installed under present scope). For comment, Sr no. 12, Para (i) is corresponding to (1) above, Sl no. 12 Para (ii) is corresponding to (2) above of respective amendment-II. |
|  | SECTION- PROJECT. Cl No. 3.2.2.1. xx) | 400kV Bhiwani | (i) Mohindergarh (Ckt. III & IV) – Hissar (Ckt. II & III) line in bypass condition by closing bypass isolator. (ii) Mohindergarh (Ckt. III & IV) – Hissar (Ckt. II & III) line will be connected to Bhiwani Buses when bypass isolator in open position. To achieve the specified bypass philosophy PLCC communication is required for which we need to consider the existing wave trap of the lines also. Therefore , please note that we need to shift the position of GIS bypass isolator between the existing line isolator and wave trap. With reference to this, existing line equipments would have to be dismantled and re-erected to create space for erection of GIS bypass isolator. As the above scope of re-erection is not mentioned in the BPS we understand that this shall be in the scope of PGCIL. Please confirm. | Bidder to comply the provision of Bidding Document. |
|  | General | TRV Capacitor | As per Section projects and BPS ,TRV capacitors are to be considered after systems Studies for Minimization of TRV and RRRV peaks, However no inputs is provided in the bid documents for performing the same. Please Issue below inputs for TRV Capacitors Calculations, which can't be assumed.. - Short-circuit power at the Remote terminal substation of each incoming / outgoing line. - Short-circuit power at the secondary side of each autotransformer. - Characteristics (R, L, C and length) of each incoming / outgoing line. - Characteristics (capacitance values) of each CVT at the substation. - Characteristics (reactance value, stray capacitance) of each shunt reactor (magnetizing curve will be estimated). - TRV capability and location of the concerned all circuit breaker. | Both Steady State(PSS/E - .sav) and dynamics(PSS/E - .snp) simulation files are provided for calculation of short circuit level, line parameters, connectivity and other network related parameters. However, the simulation files(.sav & .snp) are indicative in nature and same shall be revised based on updated data after award of contract. Further, Available data/document shall be provided to successful Bidder. Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. |
|  | General | TRV Capacitor | We are given to understand that TRV capacitor requirement/ specification was not given in the tender document of your earlier awarded package and successful bidder have to bear severe commercial impact. Hence, requesting you to please provide the above data enabling us to quote most competitive techno-commercial bid to you. | Bidders are required to compute TRV capacitor requirements. |
|  | Standard Models for STATCOM/SVC of NR |  | Standard Models for STATCOM/SVC of NR has been provided by PGCIL. We presume that it is not applicable for this Tender. Kindly confirm. | Rating of SVC/STATCOM of Northern Region has been provided. Standard dynamic models of the SVC/STATCOM may be considered for transient stability studies. Details of the dynamic models shall be discussed after finalization of the vendor. |
|  | BDS 41, ITB 29 & Annexure D, BDS | Section-III, Vol-I | ............... Further, for the purposes of comparison of bidder’s evaluated price with Indicative Estimated Cost for e-RA, the total differential price on account of difference(s) between the guaranteed loss parameter(s) quoted by the bidder and the corresponding loss figure(s) considered in the Indicative Estimated Cost shall be applied for the bid in the manner and for the equipment(s), as specified in ITB Clause 27 Kindly elaborate the analogy for calculation of evaluated bid price based on which the bidder shall be eligible to participate in e-Reverse auction. | Comparison of bidder’s evaluated price with Indicative Estimated Cost for e-RA inter-alia including differential price on account of difference(s) between the guaranteed loss parameter(s) quoted by the bidder and the corresponding loss figure(s) considered in the Indicative Estimated Cost shall be in accordance with the Provisions of Clause no. 29 of Section-III BDS read along with the provisions of Annexure-B (BDS). |
|  | ITB 27.5(c) BDS 38 | Section-II & III, Vol-I | Differential Price Factors for Evaluation Please clarify whether the losses shall be evaluated to arrive L1 Price or not according to this clause. | Bidders attention is drawn to the Provisions of Bidding Document inter-alia Clause no. 27.4, 27.5 & 27.6 of ITB Section-II of Volume-I, which are amply clear. |