|  | Section Project Cl.3.2.1.1. a. I, CT data |  | We have not received the CT parameters completely. Kindly provide the detailed CT parameters for the 2 core CT as mentioned in the section project. | Please refer reply against similar query in previous clarification (Sr. no 153 Clarification-II). |
| --- | --- | --- | --- | --- |
|  | BOQ Sr No. 70 |  | Bay Control unit (IED) of each Type. We would like to inform you that BCU shall not be part of GIS/LCC. So we have excluded the same from our scope. Kindly confirm the same. | Bidder has to quote as per requirement of bidding documents. |
|  | Section Project, BOQ & Amendment-II Cl. 9.0 Spares for 420kV GIS |  | We would like to inform you that, as per the Amendment-II received. Under point 13, it mentioned that spares for the project should be considered as per the "Annexure-10 rev01, of section GIS 5A, for GIS Spare." However, in this project, only DS, ES & CT is required and CB is not in scope. Shall we provide spares relevant to DS, ES & CT only? Please also update whether new S/s GIS spare quantities are to be quoted or for Extension project S/s GIS spare quantities are to be quoted. Kindly provide us a list (if any) of spares specifically required for this project. | Please refer Note-I of Annexure-10 Rev01 of section, GIS 5A. Further, as subject scope of work is extension work of respective substation, hence applicable spares mentioned in Colum-5 {Quantity(Extn S/S)} shall be applicable. |
|  | Section Project Cl.3.2.1 & Cl.3.2.2 3 Phase ES & DS |  | 3 Phase ES & DS is required. As per the overall layout received, we would like to inform you that we provide single phase individually operated ES & DS. Kindly accept the same. | Single phase individually operated ES & DS are acceptable, however these shall be electrically ganged operated suitably. |
|  | Section Project Cl.3.2.1 & Cl.3.2.2 Location of LCC |  | Kindly provide the location of LCC, whether it is located in the switchyard or control room. Kindly let us know the distance between GIS to control room. | LCC shall be installed outdoor. |
|  | Section Project Cl.3.2.1 & Cl.3.2.2 No of LCC |  | Kindly let us know the quantity of LCC required for the GIS. Shall we consider one LCC for one substation? Kindly clarify the same | Bay wise LCC shall be provided in respective substations. |
|  | Drawings |  | Kindly Provide us the Auto CAD drawing for the existing substation for better understanding of the connection between present scope and existing scope. | Required drawing/documents in requisite format has already provided with the bidding document. |
|  | ITB Clause 27.5(c) in BDS, | Section-III, Volume-I | As per Section III BDS clause no ITB 27.5(c) differential price factors for evaluation for losses of series reactor. Kindly clarify to us whether the price factor is applicable only for main reactor or for spare coil part. | Mandatory Spare envisages supply of each type of coil (depending upon the design) which may not necessarily be complete series reactor hence differential loading for series reactor coil under mandatory spare is not envisaged. |