|  | Extension of 400kV Kanpur SS including 6 Nos 400kV , 12 Ohm , 1 ph , Series line reactors, |  |  |  |
| --- | --- | --- | --- | --- |
|  | BOQ Item 08 & 10 |  | SF6 Gas leakage detector mentioned 2 Nos. Please check and re-confirm the supply scope. | Please refer amendment no-1 |
|  | BOQ Item 09 & 11 |  | SF6 Gas processing unit mentioned 2 – Nos. Please check and re-confirm the supply scope. | Please refer amendment no-1 |
|  | Section Project 3.2.1 _ VI. C |  | Augmentation of existing RTU. We assume that sufficient spare cards are available in the existing RTU for present scope of augumentation. Please confirm | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs and quote based on requirement to complete the scope of work and cost of the same is inclusive in 400kV Reactor protection panel. |
|  | Section Project, 3.2.1_ VI. D |  | Status of All isolators and protection operated signals. We assume that sufficient spare cards are available in the existing Event logger for present scope of augmentation. Please confirm | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs and quote based on requirement to complete the scope of work and cost of the same is inclusive in 400kV Reactor protection panel. |
|  | Section Project TRV Study Inputs |  | Please Provide Below Data required for TRV study: • Network data: • Network data in PSS/E data format. • Network data shall comprise all the three sequence impedance data information for accurate symmetrical and unsymmetrical fault currents. • The maximum and minimum (3ph-G and 1Ph-G) short circuit current information and corresponding X/R ratios at the network buses under the scope of study. • Details of the Breakers with the following name plate ratings: • Nominal Voltage rating (kV) • Continuous current capability (Amp) • BIL and BSL levels • Maximum Interrupting rating/short circuit current rating • Capability standard (IEEE/ANSI or IEC) • Details of the surge arrestors installed. • Rated voltage (kV) • Type of arrestor • Maximum residual voltage with 8/20 us current wave at 5/ 10 kA • Maximum residual voltage with 30/60 us current wave at 1/ 2 kA • Number of parallel columns • Energy capability per column • VI characteristic • Geometry of transmission lines/ Cables • Tower structure • Phase conductors’ position on Tower • Ground wire position on Tower • Transmission line conductor data • Transmission line ground wire data • Ground resistivity (transmission line path way) • Length of transmission line • Geometry of the cable, details of conductor core and sheath etc. • Stray Capacitance data for Substation equipment • Disconnectors (open & close) • Circuit breakers (open & close) • Current transformers (CTs) • Voltage transformers (VTs) • Surge arrestors • Bus support insulators • Substation transformers | Both Steady State(PSS/E - .sav) and dynamics(PSS/E - .snp) simulation files are being provided for calculation of short circuit level, line parameters, connectivity and other network related parameters. However, the simulation files(.sav & .snp) are indicative in nature and same shall be revised based on updated data after award of contract. However, Available data/document shall be provided to successful Bidder. Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs |
|  | BPS S.no 43 |  | Upgradation of existing 420kV, 2000A rated Isolators to 3000A current rating by replacing the current carrying parts etc. We understand that existing make of Manufacturer has stopped producing these ISOLATORS at there India factory long back, thus it would not be possible to get a backup offers for this and we have to take offers from some abroad factory and it would be expensive than the total cost from the current market level in India, Thus request you to please change this items as new supply of same ratings as it would equivalent for all the bidders and will not give any bidder undue advantages. | Bidder is to quote as per BPS. However, it is clarify that in case of inability to upgrade the exiting Isolator as specified in bidding documents, new Isolator meeting required current rating and isolator specification are acceptable without any additional cost implication to POWERGRID on this account. |
|  | Extension of 400kV Bhiwani SS including 3 Nos 400kV ,12 Ohm,1 ph series Bus reactor |  |  |  |
|  | BOQ Item 36 & 37 |  | Double Break with E/S -3Nos and Without E/S - 1No mentioned in BOQ. However in SLD shown all the Isolators are With E/S. Please clarify. | SLD and BPS are in agreement, bidder may examine again. Bidder has to quote as per BPS. |
|  | BOQ Item 39 |  | 420kV, 1 ph CT quantity - 24 Nos. As per the Layout and SLD drawings 420kV, 1 ph CT quantity - 27Nos . Please confirm. | Please refer amendment no.-1 |
|  | BOQ Item 39 |  | 420kV , 1 ph Bus CVT quantity - 06 Nos. Monitoring Unit for CVT shall be inbuilt of reactor Bay BCU. Please confirm. | The bidder has to comply the respective clause of technical specification. |
|  | BOQ Item 39 |  | 420kV , 3 ph CB quantity - 02 Nos for MOGA SS Please confirm whether the installation, Testing and commissioning of MOGA End CB is in vendor Scope. | In Bhiwani substation BPS, 420 kV CB with PIR are considered in two separate line items each having 2 number of 3-ph CB. First line item is for Bhiwani end and second line item is for Moga end. Further in schedule -3, at Bhiwani end for existing 400 kV CB dismantling and re-erection is considered and for Moga end existing 400 kV CB only dismantling is considered. |
|  | Section Project 3.2.2_ VII |  | Trafo Bay 416 Jack bus to be removed and connect to 419 Bay Can we re-use the Existing Transformer protection relays and panel. Please confirm. | Bidders understanding is generally in order. Please also refer clause no- 3.2.2.1XVII |
|  | Section Project TRV Study Inputs |  | Please Provide Below Data required for TRV study: • Network data: • Network data in PSS/E data format. • Network data shall comprise all the three sequence impedance data information for accurate symmetrical and unsymmetrical fault currents. • The maximum and minimum (3ph-G and 1Ph-G) short circuit current information and corresponding X/R ratios at the network buses under the scope of study. • Details of the Breakers with the following name plate ratings: • Nominal Voltage rating (kV) • Continuous current capability (Amp) • BIL and BSL levels • Maximum Interrupting rating/short circuit current rating • Capability standard (IEEE/ANSI or IEC) • Details of the surge arrestors installed. • Rated voltage (kV) • Type of arrestor • Maximum residual voltage with 8/20 us current wave at 5/ 10 kA • Maximum residual voltage with 30/60 us current wave at 1/ 2 kA • Number of parallel columns • Energy capability per column • VI characteristic • Geometry of transmission lines/ Cables • Tower structure • Phase conductors’ position on Tower • Ground wire position on Tower • Transmission line conductor data • Transmission line ground wire data • Ground resistivity (transmission line path way) • Length of transmission line • Geometry of the cable, details of conductor core and sheath etc. • Stray Capacitance data for Substation equipment • Disconnectors (open & close) • Circuit breakers (open & close) • Current transformers (CTs) • Voltage transformers (VTs) • Surge arrestors • Bus support insulators • Substation transformers | Please refer reply against similar query above. |
|  | Extension of 400kV Hissar Substation |  |  |  |
|  | General 3.2.3_ C |  | By Pass isolator to be provided. Presently In the Existing bay has Line reactor in service. Bhiwani PG to Moga dia are bypassed via bypass isolator and hence no protection isolation for reactor. Protection for the line reactor to be ensured by PGCIL. | Bidder is to quote as per provision of bidding documents. |
|  | General 3.2.3_ C |  | (i) Bhiwani (PG) – Moga - I line in bypass condition by closing bypass isolator. (ii) Bhiwani (PG) – Moga - I line in bypass condition by closing bypass isolator. The 2 Modes are mentioned typically same. Please confirm. | Please refer amendment-I |
|  | General |  |  |  |
|  | Drawings |  | Existing Cable Trench details of Hissar Required. | Available details/drawings of existing cable trench details shall be provided to successful bidder by POWERGRID. However, Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. |
|  | Drawings |  | Earthing Layout of Kanpur SS Required ( Jaipur SS EL provided) | Earthing layout attached with Bidding document is of Kanpur S/s. |
|  | General/Drawing |  | SAS Architecture of Bhiwani and Hissar Required | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful bidder by POWERGRID during detail engineering. |
|  | General |  | We understand that existing 415V AC system & 220V DC system is sufficient to cater the load requirements of the equipment's under present scope of works. Hence, same is not envisaged in the present scope of work of bidder. Kindly confirm whether our understanding is correct. | Bidders understanding is generally in order. |
|  | Drawings |  | Existing LTDB board , Battery Charger Spare Terminal Details Required | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | Drawings |  | Existing Fire Fighting Tapping Point details Required. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | General |  | We understand that any future scope enhancement will be granted with proper price amendment and time extension | Condition of Contract agreement shall prevail. |
|  | General |  | We understand that there is sufficient space is available inside the existing control room building or in Kiosk for housing CRP and others panels under present scope of works. Kindly confirm | Bidder’s understanding is generally in order. |
|  | Bhiwani | Clause no 3.2.2.1.XII | Please confirm whether Existing CB foundations at bay no 417 & 418 are to be dismantled and new foundations are to be constructed for new CBs | Possibility of reuse of foundations to be explored, however, same shall be decided during detailed engineering based on finalized make of CB’s. |
|  | Bhiwani | Clause no 3.2.2.1.XII | Please confirm at Bay No 419 & 420 where Existing CB and its structures & cables which are to re erected are in good condition and can be reused. New Foundation Bolts, Gas for the same will be provided by PGCIL . Please provide the drawings and schemes of the same | Bidder is advised to visit site as per Cl. 3.5 of section project to get required inputs. Further, foundation bolts & GAS has to be included by bidders in erection price component of BPS. No separate payment shall be made in this account. |
|  | Bhiwani |  | As there is no provision of Kiosk or CRB Cable Sealing arrangement or Rubber mat Not Required | In existing CRB/SPR, if cable sealing is existing, same is to be used for cable entry. Rubber mat is to be provided for additional panels to be supplied in subject package. |
|  | Bhiwani |  | For 420 kV 2000 A GE (Alstom make) Isolator only the current carrying part are to be replaced. Insulator, Base Plate, Structure, Foundation and Mechanism Box Can be reused. Please share detailed drawings of these Isolators, Insulators and structures so that we can check the possibilities of the said retrofitting | Please refer reply against similar query above. |
|  | General |  | REF protection is not applicable for series reactors & hence not envisaged. Please confirm. | Bidder’s understanding is generally in order. However, instead of REF, High impedance reactor differential protection is to be provided for Series reactor, in addition to other protections as per relevant clauses of section project. |
|  | Bhiwani |  | Please share detailed Schematic and setting of existing CSD relay | Bidder is advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | Bhiwani |  | Please share details of and setting of existing PLCC Devices | Bidder is advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | General |  | For retrofitting activates mentioned in the contract Employer will provide necessary 'Shutdown' within 7 days contractor's request | For necessary shutdown, contractor is required to coordinate with Engineer in-charge during execution stage. |
|  | General |  | For NTAMC integration PGCIL will arrange all the necessary coordination within 7 Days of contractor's request | For necessary information/details regarding integration, contractor is required to coordinate with Engineer in-charge during execution stage . POWERGRID will share available details/data. |
|  | Bhiwani |  | Please share schematic drawings (Clearly showing available Ports) of BCU , where GIS signals are to be integrated . | Bidder is advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | General |  | No Warranty has to be provided by the Contractor for the items which will be reused or retrofitted . | Noted. For retrofitted new parts technical and operational heartiness is required to be established. |
|  | General |  | We understand that existing Gravel is of 40 mm Gravel . Hence we'll consider 40 mm Gravel as 'matching Gravel' | Provision of bidding documents shall prevail. |
|  | Bhiwani |  | Please provide existing Drain layout (with available Discharge points ) for extension of Drain Network | Bidder is advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | Hissar |  | Annexure IV ( Mandatory Spares ) mentioned in section project is missing | Please refer amendment-I |
|  | Hissar |  | Any repair activity of Road and Drains will be restricted within the designated working area of present contract and shall be payable presuming 'new construction' as no separate item is mentioned in BPS for Repair | Provision of bidding documents shall prevail. |
|  | General |  | Please specify the training requirement (Type of Training, Man days required etc.) | Training not envisaged. |
|  | General |  | Kindly share the specification of Temporary Housing arrangment for Dust Free Work at GIS Installation Work | Same shall be as per guidelines of respective GIS manufacture. |
|  | General |  | Kindly elaborate the point ' The Duct Connections should be such that it is possible to remove reactor for repair and maintenance' | Duct installation & connection should be such that, it should not hinder removal of reactors in case of replacement/maintenance.. |
|  | Kanpur |  | Kindly confirm Foundations of existing is to be dismantled or not if required then add separate line item under civil work | Please refer our reply above for similar query |
|  | General | Volume-II | We understand, bidder scope is limited to integration of supplied BCU's with existing NTAMC gateways at substation end. Supply of NTAMC gateways (AFAS, RAS gateway, ACS) is excluded from bidder scope. And Integration/database updating works at NTAMC end is also excluded from bidder scope. Please confirm | Provision of bidding documents shall prevail. |
|  | General | Volume-II | Kindly Confirm whether the required Partial Discharge monitoring system is offline or online type | Portable type as mentioned in section project, Technical specification. |
|  | General |  | As per Section projects and BPS ,TRV capacitors are to be considered after systems Studies for Minimization of TRV and RRRV peaks, However no inputs is provided in the bid documents for performing the same. Please Issue below inputs for TRV Capacitors Calculations, which can't be assumed1) Short-circuit power at the Remote terminal substation of each incoming / outgoing line2) Short-circuit power at the secondary side of each autotransformer3) Characteristics (R, L, C and length) of each incoming / outgoing line4) Characteristics (capacitance values) of each CVT at the substation5) Characteristics (reactance value, stray capacitance) of each shunt reactor (magnetizing curve will be estimated)6) TRV capability and location of the concerned all circuit breaker | Please refer our reply above for similar query |
|  | Kanpur |  | We feel same PR Line no 80 & 90 has been repeated in BPS in PR Line no 100 & 110 . Please confirm whether we need to quote on both the lines or not | Please refer amendment no-1 |
|  | General |  | Please provide Short circuit current and X/R ratio of the Substation for simulation study | Please refer our reply above for similar query. |
|  | General |  | The foundation of the Air Core Reactor shall be of Special type with GFRB ( Glass Fiber Reinforced Polymer ) materials kindly confirm | It shall be governed by magnetic field of Air core reactor and shall be decided during detailed engineering. In case Glass Fiber Reinforced Polymer is required, same is included in present scope of work. |
|  | General |  | Please provide the detail of existing CBs connected to these reactors, same is required to check its suitability as per the TRV requirements. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | General |  | Please also provide the transformer data including its capacitance values | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | General |  | Please provide the drawing of existing of control room and C&R-Panel to check the feasibility of augmentation work. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | General |  | Please provide the Existing drawing and calculation of AC LT, DG Set, DCDB, Battery & Charger, Air-conditioning system etc. for checking the feasibility of expansion/modification of auxiliary system | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | General |  | Soil type / data, Seismic zone, Wind etc. are required (of each site location) for bid. Please provide the same | Soil data shall be collected from the respective sub-stations. For seismic and wind zones refer IS 1893 (Part 1) and IS 875 (Part 3) respectively. |
|  | General |  | Please provide the Gantry/Structure drawing of Line bay. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | General |  | Please confirm that any material or equipment etc. which needs dismantled /removal can be reutilized under present scope of work. | Provision of bidding documents shall prevail. |
|  | General |  | As per Section projects and BPS ,TRV capacitors are to be considered after systems Studies for Minimization of TRV and RRRV peaks, However no inputs is provided in the bid documents for performing the same. Please Issue below inputs for TRV Capacitors Calculations, which can't be assumed 1) Short-circuit power at the Remote terminal substation of each incoming / outgoing line 2) Short-circuit power at the secondary side of each autotransformer 3) Characteristics (R, L, C and length) of each incoming / outgoing line 4) Characteristics (capacitance values) of each CVT at the substation 5) Characteristics (reactance value, stray capacitance) of each shunt reactor (magnetizing curve will be estimated) 6) TRV capability and location of the concerned all circuit breaker | Please refer our reply above for similar query. |
|  |  |  | Please make separate Line Items for TRV Capacitors in BPS, as the Suppliers of these Capacitors are different from the reactor supplier and probably from a different geographical region, it will not be commercially possible to club the same in one consignment. Also this will make provision for taking-off the contract prices of capacitors, if not required after simulation study | Provision of bidding documents shall prevail. Bidder is to quote accordingly |
|  | General |  | Please arrange to provide Input network file required for simulation study | Please refer our reply above for similar query. |
|  | General |  | Kindly confirm that existing line protection relays are suitable for Line with series compensation. | Confirmed that existing line protection relays are suitable for Line with series compensation. |
|  | General |  | Please confirm whether CT of Bay Number 419 for Bhiwani S/stn is in present scope or not. | Confirmed. Please refer Amendment-I. |
|  | General |  | As per Existing Eartmat Layout for Bhiwani S/stn Main Mat need to be extended for at Series Reactor Area and at Bypass arrangement area. However in BPS there is no separate item for Mainmat. | Main earthmat is existing in proposed Reactor area or in vicinity of proposed Reactor area. For Series reactor earthing and its connection to main earth is part of Miscellaneous item. Further due to magnetic field consideration, modification if any, required in existing earthmat, same shall be in the present scope of work and cost of same shall be inclusive under Miscellaneous item( material code 1000033477 and service code 100003828) for respective work. |
|  | General |  | Isolators before ICT are not getting modified to 3000 A. We consider Jackbus and dropper associated that Isolator would be of Twin Moose. | Bidder to consider, jack bus and Isolator dropper associated with isolator would be Twin Bersimis. |
|  | General | Volume-II | Up-gradation of existing Twin Moose Jack Bus & Droppers are limited to two dia i.e. 416-417-418 and 422-423-424. | Existing Twin ACSR Bersimis/moose jack bus ( over the 420kV Main bus )& dropper conductor including associated hardware, clamp & connector etc, as required shall be replaced to Quad Moose for bay no 416 & 422 to make subject bay/Diameter suitable for 3150Amp. |
|  | General |  | Please confirm whether existing cables of 417-CB and 418-CB at Bhiwani S/stn can be re-used. | Bidder has to do the de-erection and re-erection of CB’s along with support structure only in other Dia. However, depending on condition of cable cables can be re-used at same place; same shall be decided, subjected to re-usable condition.. |
|  | General |  | In price schedule Sch-3, Sl No-90, PR No 7000009657 6Nos 3-ph GIS Isolator considered however as per SLD and physical requirement number would be 2. | Please refer amendment no-1 |
|  | General |  | In Bhiwani Substation DSLP design is in contractor's scope however no additional LM considered. Please clarify. | No LM is envisaged. Area under consideration is under protection Zone. However during detailed engineering for installed equipment, DSLP shall be checked. |
|  | General |  | Please confirm whether Mainmat is existing for the area under Series Reactor for Bay#429 at Kanpur Substation. | Main earthmat is existing in proposed Reactor area or in vicinity of proposed Reactor area. For Series reactor earthing and its connection to main earth is part of Miscellaneous item. Further due to magnetic field consideration, modification if any, required in existing earthmat, same shall be in the present scope of work and cost of same shall be inclusive under Miscellaneous item( material code 1000033477 and service code 100003828) for respective work. |
|  | General |  | Rerouting of existing road (if required) for Kanpur S/stn is in scope of Contractor however in price schedule there is no such item. Please clarify. | Re-routing is not envisaged, at this stage, however due to site constraint, if required, same shall be dealt as per the provision of contract. |
|  | General |  | In Hissar As per Price Schedule 1 ph Isolator (Sl. N0 96) is in scope. However from the Section Project and Tender drawings requirement of the same are not clear. Please clarify. | Kindly refer amendment No 1. |
|  | General |  | Line item for Miscellaneous Items like earthing material, erection Hardware, spacers, conductor, connectors etc is missing in Hissar S/stn. Please clarify. | Please refer clause number 3.2.3 (h) of section project. All required materials for line bypass arrangement mentioned in above clause is inclusive in material code 1000011324. |
|  | General |  | Portable partial discharge monitoring system is mentioned in section project. However the same is not reflecting in Price Schedule. | Kindly refer amendment No 1. |
|  | General |  | Please confirm the New Line length of Mohindergarh - Hissar Line during bypassed condition at Bhiwani S/stn. | During By-passing condition at Bhiwani, Mohindergarh - Hissar line length will be approximate 110km. |
|  | General |  | Please confirm the New Line length of Bhiwani -Moga D/C Line during bypassed condition at Hissar S/stn. | During By-passing condition at Hissar, Bhiwani -Moga line length will be approximate 280km.. |
|  | General |  | Please confirm whether Existing Cable Trenches has capacity to accommodate the new cables in all three S/stn. | Bidder is advised to visit site as per Cl. 3.5 of section project to get required inputs. In case space is available, same may be used, otherwise new cable trenches will be constructed based on requirement in line with provision of bidding document. |
|  | General |  | Please provide Existing PLCC equipment Details | Bidder is advised to visit site as per Cl. 3.5 of section project to get required inputs |
|  | General |  | BPS line item 'Upgradation of PLCC' missing. Please include the same | Please refer item service code 100007682 of Schedule –III, which include CRP and PLCC related up-gradation/modification to suit the by-passing state. Further it is clarified that 1 set include the complete requirement for 1X400 kV line by-passing arrangement as specified in Technical specification at respective substation ends. |
|  | Section Project : Cl.3.3 | System Engineering and Studies | The Contractor shall carry out transient simulation studies as specified in Section - Series Reactors. The Contractor shall be responsible for overall system studies, engineering and detailed design for all elements, systems, facilities and equipment. This shall include proper definition of all interfaces with the existing systems of Owner and including the material and services as listed in the specification, which are to be provided to the contractor by Owner for incorporation into the works. The contractor shall carryout all the studies which may be necessary for completion of the design and engineering whether, these have been mentioned in the Bid by the Bidder or not. Kindly Provide the system parameter data, Line Data of each substation for system studies | Please refer our reply above for similar query. |
|  | Cl. No. 3.2.2.1. XII. | Section Project | New Circuit breaker with PIR supplied in present scope shall be erected at Bay no. 417 and 418. We understand that existing CB foundation will also have to dismantled and new to be made. Please confirm the same. | Please refer reply against similar query above. |
|  | Section Project. Cl. No. 3.2.2.1. XIII. | Section Project | Existing circuit breaker (main and tie) at 765/400 kV Moga S/s installed in 400 kV Moga-Bhiwani Line are without PIR and hence shall be replaced by Circuit breaker with PIR. Any additional connector, clamps, conductor The dismantled breaker shall be handed over to POWERGRID site incharge. Please confirm the requirement as there is no Bhiwani-Moga line shown in latest Bhiwani layout and also not mentioned in Hissar Layout. | During By-passing stage at Hisar, 400kV Hisar-Bhiwani and 400kV Hisar-Moga line will act as Bhiwani- Moga line. |
|  | Section Project. Cl. No. 3.2.2.1. XIV. | Section Project | Dismantling and re-erection of existing 400kV BPI of bay no. 422 & 424 to change the phase sequence of the diameter as shown in GA. Please confirm whether we can re-use dismantled BPI Structure, Clamp connector, AL Tube, corona bell & Tube to conductor interconnector during change of phase sequence. | Bidder understanding is generally in order. However, depending on condition of clamp connector, AL Tube, Corona bell & tube to conductor interconnection can be re-used, subjected to re-usable condition. |
|  | C/ENGG-SS/NR/BHIWANI EXTN/LAYOUT/201822 (Sheet 1 of 4). Note-2 |  | Dismantled CT of 2000A shall be dismantled from bay-417 and shall be re erected at bay-419. We understand that existing CT support structure and connector will also be re used at bay-419 and we can mount structure on existing foundation at bay 419. Please confirm. | Bidder understanding is generally is in order. However, depending on condition of clamp connector, can be re-used, subjected to re-usable condition. |
|  | Section Project. Cl. No. 3.2.2.1. VII. | Section Project | Termination of existing 400 kV jackbus at Bay no. 416 to be removed and relocated to bay no. 419. For re use of jack bus conductor from 765kV Tower to 400kV Tower at bay 419, we suggest to use new conductor instead of using existing one. Because as per layout Existing jack bus conductor length shall not be enough to re erect at bay 419. Please confirm. | Bidder understanding is generally is in order. For jack bus conductor from 765kV Tower to 400kV Tower at bay 419 new conductors is to be used. |
|  | Section Project. Cl. No. 3.2.2.1. VII. | Section Project | Termination of existing 400 kV jackbus at Bay no. 416 to be removed and relocated to bay no. 419. We understand that we can re-use not only conductor but also insulator, hardware, spacers and connectors from bay 416 to bay 419. | Please refer reply above. However insulator hardware, spacer and connector can be re-used, subjected to re-usable condition. |
|  | Section Project. Cl. No. 3.2.2.1. XI. | Section Project | Upgradation of the existing twin moose ACSR Jack Bus (jack bus only for series bus reactor feeder bay 416 and 422) and droppers (including associated hardware, clamps and connectors), over the 420kV Main Bus, to Quad Moose ACSR. The removed / replaced equipments and items, etc., will be shifted to POWERGRID site store. - We understand that dismantled equipment, structure, conductor, Tube, insulator, hardware, connector and spacers shall be shifted to power grid site store except those quantities which can be re used at bay 419 ICT bay. Please confirm. - We understand that upgradation of Conductor, insulator, hardware are not required at bay 418, 421, 424. Already Quad Moose is available at those bays. Please confirm. | - Bidder understanding is generally is in order. - No, Please refer reply for similar query above. |
|  | General |  | Bus Conductor. Please confirm the existing 400kV bus conductor is AAC Quad Bull. | Confirmed, 400kV main Bus Conductor at Bhiwani S/s is Quad AAC Bull. |
|  | Section Project. Cl. No. 3.2.2.1. XI. | Section Project | Upgradation of existing twin moose Jack bus & droppers (including associated hardware like clamps, connectors, terminal connectors, etc. ) to quad moose for existing diameter. - But Section Shows existing conductor is Twin Bersimis. Please confirm actual existing conductor type. - We understand that existing Tower & Beam are suitable for 4T/ phase Tension under normal condition as quad moose shall be used instead of twin conductor. | - Existing conductor is Twin Bersimis. - Bidder understanding is generally in order. |
|  | Section Project. Cl. No. 3.2.2.1. XV. | Section Project | 400kV Reactor Protection Panel (with Automation) and 400kV Circuit Breaker Relay Panel without Auto Reclose (with Automation): Complete relay and protection system for 400kV bays as per Section–Control and Relay panels for the substation extension inter-alia Reactor protection and Circuit Breaker Protection. - Customer to confirm that existing 400kV SPR has enough place to mount Control Relay Panel for Series Bus reactor. - Please confirm that Control & indication function of new bus sectionalizer isolators shall be included in New Series bus reactor panel. | - Bidder understanding is generally in order. - Confirmed. |
|  | General |  | Space in cable Trench. Customer to confirm that existing cable trench shall have suitable empty space to lay new cables. | Please refer our reply above against similar queries. |
|  | General |  | GIS Isolator. Kindly clarify, can we use outdoor isolator instead of using GIS Isolator for bus sectionalizer. | Bidder has to quote as per provision of bidding documents. |
|  | General |  | Earthmat Extension. As Earth mat is existing. Client to confirm that no more further earthing calculation is required. We will extend the mat as per requirement. | Bidder understanding is generally in order. |
|  | General |  | DSLP. Kindly provide Existing lightning Protection Layout for every substation. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | General |  | SPR & CRB Equipment Layout. Kindly provide Exting SPR & CRB Layout for existing panel arrangement. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | General |  | Hissar Section drawing. Kindly provide section drawing of 400/220kV Hissar SS | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | General |  | Re use of Conductor and accessories in Hissar SS. We understand that removal of jumper, spacer, connector can not be re used in 400kV Hissar SS. New Twin moose conductor and accessories, 4" AL Tube shall be used. | Bidder understanding is generally in order. |
|  | General |  | Modification in Line CRP in Hissar. We understand that new GIS Isolator Control & Indication function shall be done from existing Line CRP. Augmentation and modification in Line CRP is required only. Please confirm. | Bidder has to quote as per provision of bidding documents. |
|  | Drg No. 013031-E-SY-SY-EL-0302_Equipment Layout Plan & section of Kanpur |  | Space for Line Reactor in Kanpur. Customer to confirm that sufficient space is available after existing fence area near bay-427 & 429 to locate 400kV Line Reactor. | Space for series line reactor is available at Kanpur S/s. |
|  | Drg No. 013031-E-SY-SY-EL-0302_Equipment Layout Plan & section of Kanpur |  | Land Levelling in Kanpur Line side area. Customer to confirm that required land for placing line reactor to be levelled by customer in Kanpur SS if required. | Land is fairly leveled. No further leveling will be carried out by employer. |
|  | Drg No. 013031-E-SY-SY-EL-0302_Equipment Layout Plan & section of Kanpur |  | Dismantling & Reconstruction of Existing fence at line side. Kindly confirm that dismantling & re construction of existing Fence is in scope of bidder. | Bidder has to quote as per provision of bidding documents. |
|  | Drg No. 013031-E-SY-SY-CL-0305_Switchyard cable routing & Trench Layout |  | Space in existing Cable Trench. It is observed from refered Cable trench drawing that existing 4-4 cable trench shall not be sufficient to lay cables of New Line reactor and isolators. Hence, customer to confirm that whether bidder can modify the existing trench or bidder to construct separate cable trench of section 2-2 for laying new cables. | Please refer our reply above against similar queries. |
|  | Section Project. Cl. No. 3.2.1.1. V. | Section Project | Dismantling and re erection of existing LM. Kindly confirm the requirement and if required then provide existing LM Location. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. |
|  | General |  | Conductor & Tube size. Please confirm that existing AL tube size is 4" and Line conductor is Quad Moose in Kanpur SS. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. |
|  | Section Project. Cl. No. 4 | Section Project | Spare LT Feeders. Please confirm that required AC/DC feeders are available in existing ACDB & DCDB. Only power cable we have to lay and terminate. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. Bidder is to quote as per provision per provision of bidding documents. |
|  | Section Project. Cl. No. 5.2 | Section Project | Meteorological Data. Kindly provide wind speed, soil bearing capacity and Sismic zone. | Soil data shall be collected from the respective sub-stations. For seismic and wind zones refer IS 1893 (Part 1) and IS 875 (Part 3) respectively. |
|  | General. |  | Outdoor lighting fixture type. kindly Confirm the type of outdoor lighting fixtures for all packages. Whether this is LED type or HPSV? | Bidder is to quote as per provision per provision of bidding documents. |
|  | General. |  | Power supply for site construction. Please confirm that power supply for site construction shall be provided by cutomer. | Please refer clause no 14.3.1 of Technical Specification , Section GTR- Rev 14. |
|  | General. |  | Water supply for site construction. Please confirm that water supply for site construction shall be provided by customer. | Please refer clause no 14.3.2 of Technical Specification , Section GTR- Rev 14. |
|  | General. |  | Level difference. Please confirm that area for extension work shall be in same RL with existing land area. No level difference shall be there. | Extension area will be at same RL. Land is fairly leveled. |
|  | Section Project. Cl. No. 3.2.2.1. XI. | Section Project | Upgradation of the existing twin moose ACSR Jack Bus (jack bus only for series bus reactor feeder bay 416 and 422) and droppers(including associated hardware, clamps and connectors), over the 420kV Main Bus, to Quad Moose ACSR. It is understood from existing section drawing that, all jack bus conductor is twin Bersimis. Hence, all conductor of jack bus under present scope shall be upgraded to quad moose as we are increasing all equipment ratings to 3150A. But In section project only jack bus upgradation has been mentioned for bay 416 & 422. Kindly clarify the requirement. | Please refer reply of similar query. |
|  | Section Project. Cl. No. 3.2.2.1. VII. | Section Project | Termination of existing 400 kV jackbus at Bay no. 416 to be removed and relocated to bay no. 419. We understand from section project that for shifting of ICT bay, There is no modification required at existing Tower & Beam at bay 419. It is already suitable for 30 degree deviation horizontally & vertically. | Bidder understanding is generally in order. |
|  | Section Project. Cl. No. 3.2.2.1. VIII. | Section Project | CSD device for Main breakers (Bay no. 419&422) and existing Tie Breakers (Bay no. 420 & 423). CSD device for bay no. 416 & 417 is already existing and shall be used for switching of series bus reactor. We understand 4 nos of CSD is required for bay 419,422,420 & 423. Please confirm. | Bidder is to quote as per provision per provision of bidding documents. |
|  | Section Project. Cl. No. 3.2.2.1. XXI. | Section Project | Piping for fire protection system shall be extended from nearest hydrant point. One no. Hydrant point shall be provided for each bank of 3 Ph. series reactor. Kindly provide existing fire fighting & hydrant layout for Bhiwani & Kanpur SS to know nearest hydrant point. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | General |  | Line Conductor Kindly provide existing 400kV Line conductor details for Bhiwani, Hissar & Kanpur SS. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | General |  | Re use of cable, earthing risers. We understand that cable and earthing riser material shall be required only for new equipment’s to be supplied. Please confirm. | Please refer reply for similar query. |
|  | Section Project. Cl. No. 3.2.2.1. XXI. | Section Project | Up-gradation of existing 420kV, 2000A, 40kA DB Isolators (M/s GE (previously Alstom) make) to 3000A Current Rating by replacing the current carrying parts, etc., as per requirements. We understand that no modification required at existing Isolator (2000A) Pipe Structure after upgrading current carrying parts to 3150A. Please confirm. | Bidder understanding is generally in order. |
|  | Section Project. Cl. No. 3.2.2.1. VI. | Section Project | Integration of Line Series Reactor equipments in existing NTAMC BCU We understand the Existing BCUs is having sufficient Input / Output Terminals and only wiring Modifications shall be required to incorporate the Line Series Reactor equipments. No additional Panel / BCUs are require for the modification work. Kindly Confirm. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs and quote based on requirement to complete the scope of work and cost of the same is inclusive in 400kV Reactor protection panel. |
|  | Section Project. Cl. No. 3.2.2.1. VI. | Section Project | Augmentation of Existing M/S Alstom Make RTU We understand exiting RTU panel is having sufficient space to accommodate the Cards and additional wiring of Series Reactor equipments. Kindly Confirm. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs and quote based on requirement to complete the scope of work. |
|  | Section Project. Cl. No. 3.2.2.1. VI. | Section Project | Signals connection to the existing M/S Qualitrol make event logger We understand exiting Event logger is having sufficient inputs to accommodate the additional signals of Series Reactor equipments. No additional Cards are require for the modification work Kindly Confirm. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs and quote based on requirement to complete the scope of work |
|  |  | Illumination | - We understand that the auxiliary AC and DC supply to the equipments in the present scope can be provided from the existing yard BMKs. Please confirm. - We understand that the existing BMKs have the provision of tapping AC and DC supplies from the same BMK. Please confirm. | - Bidder understanding is generally in order. - Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  |  | Auxiliary Power | - We understand that the auxiliary AC and DC supply to the equipments in the present scope can be provided from the existing yard BMKs. Please confirm. - We understand that the existing BMKs have the provision of tapping AC and DC supplies from the same BMK. Please confirm. - We understand that the existing ACDB and DCDB have sufficient number of spare feeders to cater for the present scope of work and the bidder need not supply any new panel for the same. Please confirm. | - Bidder understanding is generally in order. - Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. - Bidder understanding is generally in order. |
|  |  | Cabling | - We request you to provide the cable route length from the existing control room buiding to the switchyard area in the present scope of works. Please confirm. - We understand that the existing cable trenches in yard have sufficient space to accommodate the power and control cables for the present scope of works and the bidder need not require to make new cable trenches. Please confirm. | - Bidder has to ascertain the cable route length based on route available at site. - Please refer reply against similar queries above. |
|  |  | VMS | General We understand that any CCTV/ Surveillance (monitoring via camera) is not included in the present scope of work.Please confirm. | Confirmed |
|  | Civil works |  | Please provide soil data/ soil report for all three substations. | Please refer reply for similar query. |
|  | Civil works |  | Please provide contour report of all three S/Stns to envisage any cutting- filling quantities. | Land is fairly leveled. Bidders are advised to visit site as per Cl. 3.5 of section. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | Civil works |  | Kindly inform us about the Finished Ground Level of all three substations | Finished ground level details shall be shared during detailed engineering. However the bidder may visit the site for the same. |
|  | Civil works | Price Schedule | As all the items are quantified by PGCIL. Kindly confirm, any increase in quantified BOQ items during execution will be paid extra through an amended order value. | Provision of Bidding document shall prevail. |
|  | Civil works | Support Structure | Pipe supporting structures & foundations shall be designed by bidder or standard drawings shall be issued from customer for execution as per project specific requirement | Bidder is to quote as per provision per provision of bidding documents. |
|  | Civil works |  | Kindly confirm that the stone spreading is only for present scope area. | Bidder understanding is generally in order. |
|  | Civil works | Price Schedule | For Reactor foundations GFRP is to be used. But in customer specified BOQ no such item avilable. Kindly confirm this requirements. | It shall be governed by magnetic field of Air core reactor and shall be decided during detailed engineering. In case Glass Fiber Reinforced Polymer is required, same is included in present scope of work. |
|  | Drawings |  | Requirement of Drawings. Kindly provide the AutoCAD drawings of layouts for all three substation. | Available data/document shall be provided to successful Bidder. |
|  | Section GIS_Rev 5A 5.8 |  | The material and thickness of the enclosures shall be such as to withstand an internal flash over without burns through for a period of 300 ms at rated short time withstand current. The Value shall be in line with the requirement of IEC 62271-203. Request a concurrence on the same. | Bidder to comply the requirement of Technical specification. |
|  | BPS |  | Mandatory spares. We request customer to provide us the list for all the mandatory spares part for all equipments as listed in the BPS | Please refer reply against similar query above. |
|  | Section GIS_Rev 5A 5.9 |  | Inspection windows (View Ports) shall be provided for Disconnect Switch and both type of earth switches i.e. Maintenance and fast operating. Inspection windows shall be provided for Disconnector enclosures . Provision of Observation windows for Earth switches is not envisaged as such. Request you to kindly accept the same. | Bidder to comply the requirement of Technical specification. |
|  | Section GIS_Rev 5A 5.21. |  | The GIS shall be designed, so as to take care of the VFT over voltages generated as a result of pre-strikes and re-strikes during isolator operation. Maximum VFT over voltages peak shall not be higher than rated lightning impulse withstand voltage (LIWV) of the equipment. Necessary measures shall be under taken by GIS manufacture to restrict maximum VFT over voltages lower than the LIWV. Manufacturer shall submit the study report of VFTO generated for GIS installation. The GIS has already been Type Tested for certain VFT values which are lower than LIWV. We understand that no additional VFT study needs to be performed for the system. We request you to kindly confirm the same. | Bidder to comply the requirement of Technical specification. Related documents shall be reviewed during detail engineering. |
|  | Section GIS_Rev 5A 5.41. Gas Insulated Bus (GIB) layout |  | The horizontal clearance between GIB and GIS building /any other building wall shall be preferably three (3) meters. The space/area utilization for such a configuration is very high and request customer to accept the standard spacing's between circuits considering the fact that the Bus-ducts are passive and requires almost no maintenance. Request PGCIL to accept the same. | Bidder to comply the requirement of Technical specification. |
|  | Section GIS_Rev 5A 7.2.5 |  | For motor-operated disconnect switches, the control should be electrically and/or mechanically uncoupled from the drive shaft when the switch is operated manually to prevent coincident power operation of the switch and the drive mechanism(s). Only electrical inter-locks possible between DS & ES are provided. Request you to kindly accept | Bidder to comply the requirement of Technical specification. |
|  | Section GIS_Rev 5A 7.2.10 |  | Each disconnector shall be supplied with auxiliary switch having additional 8 NO (Normally Open) and 8 NC (Normally Closed) contacts for future use over and above those required for switchgear interlocking and automation purposes. These spare NO and NC contacts shall be wired up to the local control cabinet. Auxiliary switches are of standard design/size suitably designed for the available space. Hence the required additional 8 NO (Normally open) and 8 NC (normally closed) contacts shall be provided through contact multiplication relays at LCC. Request you to kindly accept our proposal. | Noted |
|  | Section GIS_Rev 5A 7.2.13 |  | The disconnectors and safety grounding switches shall have a mechanical and electrical inter-locks to prevent closing of the grounding switches when isolator switches are in the closed position and to prevent closing of the disconnectors when the grounding switch is in the closed position. Integrally mounted lock when provided shall be equipped with a unique key for such three phase group. Master key is not permitted. The disconnectors and the safety grounding switches are separate modules in GIS design and shall have only electrical inter-locks between them. However the required padlocking facility shall be provided for the manual interlocking for additional protection. Request you to kindly accept | Bidder to comply the requirement of Technical specification. |
|  | Section GIS_Rev 5A 8.3 |  | Each safety grounding switch shall be electrically interlocked with its associated disconnectors and circuit breaker such that it can only be closed if both the circuit breaker and disconnectors are in open position. Safety grounding switch shall also be mechanically key interlocked with its associated disconnectors. The disconnectors and the safety grounding switches are separate modules in GIS design and shall have only electrical inter-locks between them. However the required padlocking facility shall be provided for the manual interlocking for additional protection. Request you to kindly accept our proposal. | Bidder to comply the requirement of Technical specification. |
|  | Section GIS_Rev 5A 8.6 |  | Each ground switch shall be fitted with auxiliary switches having 4 NO (Normally Open) and 4 NC (Normally Closed) contacts for use by others over and above those required for local interlocking and position indication purposes. Auxiliary switches are of standard design/size suitably designed for the available space. Hence the required additional 4 NO (Normally open) and 4 NC (normally closed) contacts shall be provided to customer through contact multiplication relays at LCC. Request you to kindly accept our proposal. | Noted |
|  | Section GIS_Rev 5A 11.3.2 |  | Surge arrestor shall be disconnect-link type and be attached to the gas-insulated system in such a manner that they can be readily disconnected from the system while the system is being dielectrically tested. Kindly confirm the requirement of GIS LA for this requirement. We infer that GIS LA are not required as per the BOQ and Section project. If any additional requirement is observed during detail engineering stage, the same shall be associated with additional price implication. Please take note of the same. | Bidder to comply the requirement of Technical specification. |
|  | Section GIS_Rev 5A GSLD |  | Provision of Gas Segregation The Provisions of Service Continuity for Repair and Maintainance and the GIS Technical specifications can be confirmed with the manufactures specific GIS Gas segregation proposal. We request you to kindly accept. | Bidder to comply the requirement of Technical specification. |
|  | Transient Simulation Study Cl. 3.3 : Section Project |  | As per the scope of present package the lines Hissar-2 and Hissar-3 lines shall be connected directly to Mohindergarh-2 and Mohindergarh-3 lines. Kindly confirm whether the short circuit contribution from these lines should be considered or not. | Short Circuit contribution from HVDC is minimal. However, the same may be considered as per international practices for simulation of series reactors. |
|  | Transient Simulation Study Cl. 3.3 : Section Project |  | As per the scope of present package the lines Kanpur and Panki D/C lines shall be connected. Kindly confirm whether the short circuit contribution from these lines should be considered or not. | Simulation studies are to be carried out considering all possible network configurations as some/all lines that are being re-configured in this scheme may be required to be restored at times based on operational requirement. |
|  | Inputs Required: Transient Simulation Study Cl. 3.3 : Section Project |  | With reference to TRV studies as envisaged under present scope we request you to kindly provide us inputs in terms of parameters for the Kanpur and Bhiwani Substation to conduct the studies. In this regard you are requested to refer the Annexure-A,B & C enclosed herewith & provide the requested data as per the same. | Please refer reply for similar query. |
|  | 400 kV Series Reactor at 400/220KV KANPUR SS |  |  |  |
|  | General |  | Existing conductor details of Kanpur and Bhiwani. Kindly provide the existing 400KV conductor details as:- 1). Jack/Dropper Conductor 2). Equipment Interconnection 3). Main Bus 4. Line Length & conductor details 5. Fault Level | Please refer already exiting drawing for subject data. Fault level already provided in Section project Claus no 10.5. However, Available data/document shall be provided to successful Bidder. |
|  | General |  | Existing electrical layout and tender layout. Line side equipment in existing layouts are to be shifted by 3 meters w.r.t to tender layout. So we understand that sufficient space is available for GIS bushing and reactor. | Bidder to comply the requirement of Technical specification. |
|  | General Existing cable trench |  | We understand that there is sufficient space available in the existing outdoor and indoor cable trench for laying of power and control cables under present scope of works. Kindly confirm. | Please refer reply for similar query. |
|  | Sec: project 3.2.1.1 VII) |  | Presently One circuit of 400 kV Fatehpur – Panki line is in same diameter. For other circuit to be in same diameter, 400 kV Fatehpur – I Line shall be swapped with 400 kV Allahabad – I line. The swapping of above lines is not in bidder’s scope. Please confirm whether swapping of C&R panels and PLCC Panels of these two lines are also envisaged or C&R panels will be retained as it is. Kindly confirm the scope. | Swapping of C&R panels and PLCC of these two lines not envisaged, however modification in CRP/PLCC wiring etc. shall be done matching with lines. |
|  | Sec: project 3.2.1.1 VII) |  | Presently One circuit of 400 kV Fatehpur – Panki line is in same diameter. For other circuit to be in same diameter, 400 kV Fatehpur – I Line shall be swapped with 400 kV Allahabad – I line. The swapping of above lines is not in bidder’s scope. If swapping of C&R panels of these two lines is also envisaged, please confirm that this work is also covered in separate package. | Please refer reply for similar query. |
|  | Sec: project 3.2.1.1 VII) |  | Modification of Existing CRP and PLCC Panels for line bypass arrangement: Fatehpur–Kanpur (old) 400kV D/c and Kanpur (old)-Panki 400kV D/c lines are to be bypassed at Kanpur (old) end to form Fatehpur-Panki 400 kV D/c line. The bypass shall be carried out by opening both the main breakers and closing tie breakers in both the diameters We understand that, no additional modifications in existing CRP & PLCC is required in case of operating these lines with bypassing through Tie bays. Existing designed scheme is having such type of operational flexibility. Please confirm. | Bidder to comply the requirement of Technical specification. |
|  | SLD |  | Existing Line Isolator dismantling. We understand that, Line Isolators of Kanpur GIS-I & II line bays may not be required after installing Series Reactors for these lines. Hence same needs to be dismantled. Please confirm this dismantling scope. | Bidder to comply the requirement of Technical specification & quote as per BPS. |
|  | Sec: project 3.2.1.1 VI) |  | VI. Reactor Protection Panel: Complete relay and protection system for series line reactor as per Section–Control and Relay panels We understand that, existing control panel modifications like mimic change etc.. are not envisaged. Since Series reactor bay equipment supplied under this contract shall be controlled from local LCC & NTAMC BCU only. Controlling of these new equipment from existing control panel is not envisaged. Please confirm. | Bidder to comply the requirement of Technical specification. |
|  | Sec: project 3.2.1.1 VI) |  | VI. Reactor Protection Panel: Complete relay and protection system for series line reactor as per Section–Control and Relay panels We understand that, new C&R panels & LCC shall be placed in new KIOSK near to series reactor. Please confirm. | New C&R panels & LCC shall be housed in Existing Control room. |
|  | C/ENGG-SS/NR/KANPUR-EXTN/SLD/201822/00, REV.00, SLD of Series line reactor at 400KV at Kanpur SS |  | Kindly provide the 400KV, 2500A GIS CT core details along with class, accuracy, burden etc. since same is not available in the tender documents. | For GIS CT parameters details mentioned for core-1 in Table-3B, Section GIS Rev05 shall be applicable. |
|  | Section project |  | 3.3 System Engineering and Studies 3.4 The Contractor shall carry out transient simulation studies as specified in Section - Series Reactors. The Contractor shall be responsible for overall system studies, engineering and detailed design for all elements, systems, facilities and equipment. This shall include proper definition of all interfaces with the existing systems of Owner and including the material and services as listed in the specification, which are to be provided to the contractor by Owner for incorporation into the works. The contractor shall carryout all the studies which may be necessary for completion of the design and engineering whether, these have been mentioned in the Bid by the Bidder or not. As per Section projects and BPS ,TRV capacitors are to be considered after systems Studies for Minimization of TRV and RRRV peaks, However, no inputs is provided in the bid documents for performing the same. Please issue below inputs for TRV Capacitors Calculations, for Kanpur and Bhiwani both Substation, which are essential for estimation : 1) Short-circuit power at the Remote terminal substation of each incoming / outgoing line 2) Short-circuit power at the secondary side of each autotransformer 3) Characteristics (R, L, C and length) of each incoming / outgoing line 4) Characteristics (capacitance values) of each CVT at the substation 5) Characteristics (reactance value, stray capacitance) of each shunt reactor (magnetizing curve will be estimated) 6) TRV capability and location of the concerned all circuit breaker | Please refer reply for similar query. |
|  | Section Project System Engineering and Studies |  | Please arrange to provide Input network file required for simulation study for Kanpur and Bhiwani both Substation. | Please refer reply for similar query. |
|  | 400 kV Series Reactor at 400/220KV Bhiwani SS |  |  |  |
|  | General |  | Existing cable trench drawing Kindly provide the existing cable trench drawing of 400/220KV Bhiwani SS since same is not available with the tender documents. | Please refer reply for similar query. |
|  | C/ENGG-SS/NR/BHIWANI-EXTN/SLD/201822/00, REV.00, |  | SLD of Series line reactor at 400KV at Bhiwani SS Kindly confirm the LCC requirement for bypass GIS Isolator like other GIS isolators, since same is not available in the tender documents. | Bidder to comply the requirement of Technical specification. |
|  | Sec: project 3.2.2.1 XVI) |  | The existing distributed Numerical Duplicate Bus bar protection schemes at 400 kV side of Bhiwani S/S is P743 of M/s GE make and the same shall be augmented under present scope by providing necessary bus bar bay units, trip relays/auxiliary relay, wiring/cabling and necessary modification in Bus bar main unit for the bays covered under present scope. We understand that, new bus bar protection bay units are not required since no new dia are adding under this package. Only re-configuration of existing scheme is envisaged. Please confirm. | Please refer amendment no-1 |
|  | 400 kV Series Reactor at 400/220KV Hissar SS |  |  |  |
|  | SLD |  | By-pass Isolator connection We understand that, By-pass Isolator tapping point shall be after the Line isolator, CVT & LA. But Moga line tapping point is shown before line isolator. Please confirm & revise the SLD, if required. | Bidder to comply the requirement of Technical specification. |
|  | Sec: project 3.2.3.1 b) |  | Bhiwani (PG)–Hissar (PG) 400kV D/c line (one circuit via Bhiwani (BBMB)) and Hissar (PG)–Moga (One circuit via Fatehabad) 400kV line to be by-passed at Hissar end so as to form direct Bhiwani (PG)–Moga 400kV D/c line. 400 kV Moga and Bhiwani circuit via Fatehabad and Bhiwani(BBMB) are on the same diameter, shall be bypassed at Hissar S/s by opening both the main breakers and closing tie breaker. Other circuit of 400 kV Bhiwani-Moga line at Hissar substations are not on same diameter and hence bypass isolator for the same shall be supplied under present scope. We understand that, By-pass Isolator for other circuit of Bhiwani & Moga lines at Hissar SS shall be supplied loose. Please confirm. | Bidder to quote as per provision of bidding documents. |
|  | Common Points |  |  |  |
|  | Section project |  | Structure of Series Reactor and TRV Capacitor for Kanpur and Bhiwani S/s We do not find any line item for structure of Series Reactor and TRV capacitor. Kindly confirm the line item where it shall be paid or include the new line item in BPS. | Please refer Technical Specification Section-Project, 3.2.1.1.I & 3.2.2.1.I, wherein TRV Capacitors (if applicable), structure, support insulator, terminal connector etc. are part of Series Reactor. No additional payment shall be made in this account |
|  | C/ENGG-SS/NR/KANPUR-EXTN/LAYOUT/201822/00, REV.00, Sheet 1 of 2 |  | General Arrangement of Series line reactor at 400KV Kanpur SS and Bhiwani SS We request PGCIL to kindly provide the minimum area/dimension requirement for the 400KV series line reactor, since same is not marked in the GA drawing enclosed with the tender document. | Based on site conditions and provision of bidding documents, Layout shall be finalized during detail engineering. |
|  | C/ENGG-SS/NR/KANPUR-EXTN/LAYOUT/201822/00, REV.00, Sheet 1 of 2 |  | General Arrangement of Series line reactor at 400KV Kanpur SS and Bhiwani S/s Kindly clarify whether LCC required for 400KV GIS shall be provided in outdoor near GIS Modules or it shall be housed inside existing the nearest AC Kiosk or in Control Room building. | LCC shall be suitable for outdoor mounting. |
|  | C/ENGG-SS/NR/KANPUR-EXTN/LAYOUT/201822/00, REV.00, Sheet 1 of 2 |  | General Arrangement of Series line reactor at 400KV Kanpur SS and Bhiwani S/s If LCC required for GIS modules shall be housed inside the existing control room building or in AC Kiosk, then kindly confirm that there is sufficient space is available inside the existing control room building/ AC Kisok Room. | Please refer reply for similar query. |
|  | General |  | General Arrangement of Series line reactor at 400KV Kanpur SS and Bhiwani S/s We understand that there is sufficient space available inside the existing control room building for housing control & relay protection panels under present scope of works. Kindly confirm. | 765/400kV Bhiwani S/s is AC Kisok based S/s , hence panels shall be placed in AC Kisok. At Kanpur space is available in control room. |
|  | C/ENGG-SS/NR/KANPUR-EXTN/LAYOUT/201822/00, REV.00, Sheet 1 of 2 |  | Bus post insulators for Kanpur and Bhiwani Ss We understand that 400KV BPI alongwith its structure (if applicable) required for present scope of works at 400KV Line Series reactor shall also be included under erection hardware item. Kindly confirm. | These item shall be included in Miscellaneous item. |
|  | General |  | Existing 415V AC system & 220V DC system We understand that existing 415V AC system & 220V DC system is sufficient to cater the load requirements of the equipment's under present scope of works. Hence, same is not envisaged in the present scope of work of bidder. Kindly confirm. | Please refer reply for similar query. |
|  | General |  | Spare feeders available in existing ACDB & DCDB We understand that there are sufficient spare feeders available in existing ACDB/DCDB for the present scope of works. Kindly confirm. | Please refer reply for similar query. |
|  | General |  | Spare feeders available in existing MLDB/ELDB We understand that there is sufficient spare feeders are available in existing MLDB/ELDB for the illumination under present scope of works. Kindly confirm. | Please refer reply for similar query. |
|  | General |  | We understand that any modification/Refurbishment work towards any existing civil foundations is not in the bidder's scope. Please confirm. | Modification/Refurbishment work, if any towards any existing civil foundations for present scope of work in under subject contract. |
|  | General |  | Re use of existing control & power cables We understand that, bidder can make use of existing power & control cables where ever possible while replacing & shifting of existing equipment. Please confirm. | Please refer reply for similar query. |
|  | General |  | Kindly provide the series reactor CT parameters like, accuracy class, burden, Knee point voltage, Rct, etc… which is not available in specification. | Please refer reply for similar query. |
|  | Sec: Series reactor 4.2 |  | For Line Series reactor application type, Simulation Study shall also be carried out for efficacy of the Line protection system for the line with series reactor. Details of existing line distance protection relays, setting data and associated power system network data shall be provided by the employer during detail engineering. Kindly confirm the existing line protection relays are suitable for Line with series compensation. | Please refer reply for similar query. |
|  | General |  | Reactor REF protection. REF protection is not applicable for series reactors & hence not envisaged. Please confirm. | Please refer reply for similar query. |
|  | 400/220 KV HISAR SUBSTATION |  |  |  |
|  | DRAWING C/ENGG-SS/NR/HISSAR-EXTN/LAYOUT/201822 REV-0 | Volume-II | WE UNDERSTAND THAT SHIELD WIRE IS ALREADY EXISTING IN PRESENT SCOPE OF WORK. | Bidder is to quote as per provision of bidding documents. |
|  | DRAWING C/ENGG-SS/NR/HISSAR-EXTN/LAYOUT/201822 REV-0 | Volume-II | WE UNDERSTAND THAT 2 NOS. OF BMK ALREADY EXIST IN DIA. BHIWANI(PG)- MOGA LINE WHICH HAVE SPARE TERMINALS TO CATER PRESENT SCOPE OF WORK | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. |
|  | DRAWING C/ENGG-SS/NR/HISSAR-EXTN/LAYOUT/201822 REV-0 | Volume-II | WE UNDERSTAND THAT THE LINE IS EXTENDED UPTO BHIWANI(PG) LINE FROM EXISTING BHIWANI(PG) BAY AND CONTRACTOR ONLY NEED TO DO JUMPERING ARRANGEMENT AS HIGHLIGHTED IN RED IN TENDER LAYOUT | Bidder’s understanding is generally in order. |
|  | General | Volume-II | EXISTING CABLE TRENCH DRAWING TO BE PROVIDED TO CHECK INTEGRATION SCOPE. | Please refer reply against similar query. |
|  | DRAWING C/ENGG-SS/NR/HISSAR-EXTN/LAYOUT/201822 REV-0 | Volume-II | WE UNDERSTAND THAT THERE IS NO SPR ROOM IN HISAR SUBSTATION AND ALL THE PANELS ARE IN CONTROL ROOM. PLEASE CONFIRM. | Bidder’s understanding is generally in order. |
|  | CLAUSE 3.2.3.1 © | Volume-II | EXISTING CONTROL AND PROTECTION PANELS TO BE PROVIDED . | Available details/drawings details shall be provided to successful bidder by POWERGRID. However, Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. |
|  | 400/220 KV KANPUR SUBSTATION |  |  |  |
|  | CLAUSE 3.2.1.1 (VII) | Volume-II | EXISTING CONTROL AND PROTECTION PANELS TO BE PROVIDED . | Please refer reply against similar query above. |
|  | DRAWING C/ENGG-SS/NR/KANPUR-EXTN/LAYOUT/201822 REV-0 | Volume-II | WE UNDERSTAND THAT THERE IS NO SPR ROOM IN HISAR SUBSTATION AND ALL THE PANELS ARE IN CONTROL ROOM. PLEASE CONFIRM. | Bidder’s understanding is generally in order. |
|  | DRAWING C/ENGG-SS/NR/KANPUR-EXTN/LAYOUT/201822 REV-0 | Volume-II | WE UNDERSTAND THAT THE MAIN MAT IS EXISTING AT PRESENT SCOPE OF WORK. PLEASE CONFIRM. | Please refer reply against similar query. |
|  | DRAWING C/ENGG-SS/NR/KANPUR-EXTN/LAYOUT/201822 REV-0 | Volume-II | WE UNDERSTAND THAT CONTRACTOR DON’T NEED TO CONSIDER CABLE SEALING SYSTEM AS THERE IS NO SCOPE OF ANY NEW SPR ROOM OR CONTROL ROOM. PLEASE CONFIRM. | Please refer reply against similar query. |
|  | CLAUSE 3.2.1.1 (IX) | Volume-II | LOCATION OF EXISTING HYDRANT POINT TO BE PROVIDED ALONG WITH DIA. OF PIPE. | Please refer reply against similar query. |
|  | 400/220 KV BHIWANI SUBSTATION |  |  |  |
|  | DRAWING C/ENGG-SS/NR/BHIWANI-EXTN/LAYOUT/201822 REV-0 | Volume-II | WE UNDERSTAND THAT THERE IS NO SPR ROOM IN HISAR SUBSTATION AND ALL THE PANELS ARE IN CONTROL ROOM. PLEASE CONFIRM. | SPR ROOM at Bhiwani are available and CRP are to be installed in the same. |
|  | DRAWING C/ENGG-SS/NR/BHIWANI-EXTN/LAYOUT/201822 REV-0 | Volume-II | WE UNDERSTAND THAT 2 NOS. OF BMK ALREADY EXIST IN EACH DIA. HAVING SPARE TERMINALS FOR PRESENT SCOPE HAVING SERIES REACTOR. | Please refer reply against similar query |
|  | CLAUSE 3.2.2.1 (XV) | Volume-II | EXISTING BUS BAR PROTECTION SCHEMES TO BE PROVIDED . | Bidder is advised to visit site as per Cl. 3.5 of section project to get required inputs. Available details/drawings shall be provided to successful Bidder during detailed engineering activities. |
|  | CLAUSE 3.2.2.1 (XXI) | Volume-II | LOCATION OF EXISTING HYDRANT POINT TO BE PROVIDED ALONG WITH DIA. OF PIPE. | Please refer reply against similar query |
|  | 400/220 KV KANPUR SUBSTATION |  |  |  |
|  | Project Scope , Clause No. 3.2.1.1-IX - Piping for fire protection system shall be extended from nearest hydrant point. | Volume-II | Please provide the Existing Fire Hydrant layout drg showing Existing Fire Pipe header and tapping point which can be extended for Hydrant system. | Please refer reply against similar query |
|  | Project Scope , Clause No. 3.2.1.1-IX - Piping for fire protection system shall be extended from nearest hydrant point. | Volume-II | We assume that Existing Pumping Capacity, Pump head and water tank capacity is sufficient to take care Hydrant Fire fighting system. Hence Fire Pumping system is totally excluded from Bidder scope of work. Please confirm. | Bidder’s understanding is generally in order. |
|  | Project Scope , Clause No. 3.2.1.1-IX - Piping for fire protection system shall be extended from nearest hydrant point. | Volume-II | We assume that sufficient Fire water pressure & Fire water qty is available at the TOP (take over point)/ Tapping point of Existing Fire Pipe Header which to be extended for Firefighting system. Hence Booster Pump is not envisaged at Tapping point. Please confirm . | Bidder’s understanding is generally in order. |
|  | Project Scope , Clause No. 3.2.1.1-IX - Piping for fire protection system shall be extended from nearest hydrant point. | Volume-II | We are considering tapping distance from existing header as 50 metres. Please provide the exact length of tapping to be considered for the extension of Hydrant/ HVWS system. | Please refer reply against similar query |
|  | 400/220 KV BHIWANI SUBSTATION |  |  |  |
|  | Project Scope, Clause No. 3.2.2.1-XXI - Piping for fire protection system shall be extended from nearest hydrant point. | Volume-II | Please provide the Existing Fire Hydrant layout drg showing Existing Fire Pipe header and tapping point which can be extended for Hydrant system. | Please refer reply against similar query |
|  | Project Scope, Clause No. 3.2.2.1-XXI - Piping for fire protection system shall be extended from nearest hydrant point. | Volume-II | We assume that Existing Pumping Capacity, Pump head and water tank capacity is sufficient to take care Hydrant Fire fighting system. Hence Fire Pumping system is totally excluded from Bidder scope of work. Please confirm. | Please refer reply against similar query |
|  | Project Scope , Clause No. 3.2.2.1-XXI - Piping for fire protection system shall be extended from nearest hydrant point. | Volume-II | We assume that sufficient Fire water pressure & Fire water qty is available at the TOP (take over point)/ Tapping point of Existing Fire Pipe Header which to be extended for Fire fighting system. Hence Booster Pump is not envisaged at Tapping point. Please confirm . | Please refer reply against similar query |
|  | Project Scope , Clause No. 3.2.2.1-XXI - Piping for fire protection system shall be extended from nearest hydrant point. | Volume-II | We are considering tapping distance from existing header as 50 metres. Please provide the exact length of tapping to be considered for the extension of Hydrant/ HVWS system. | Please refer reply against similar query |
|  | Section project : clause 3.2.1.4, 3.2.2.4 and 3.2.7.3 |  | Please confirm the scope of Geotechnical investigation. | Geotechnical Investigation is not in the scope of the bidder. |
|  | Section project : clause 3.2.1.4, 3.2.2.4 and 3.2.7.3 |  | Please confirm the scope of Site Grading. | Site is fairly graded. Site gradation is not in the scope of the bidder. |
|  | Section Project Cl 3.2.2.1.XI.a Isolator Refurbishment | Volume-II | Upgradation of existing 420kV, 2000A, 40kA DB Isolators (M/s GE (previously Alstom) make) to 3000A Current Rating by replacing the current carrying parts, etc., as per requirements. Kindly provide us the GA drawing, details of current carrying parts for the GE make isolators which need to be refurbished. | Please refer reply against similar query in earlier issued clarifications. |
|  | Section Project PLCC Reconfiguration | Volume-II | Modification of Existing CRP and PLCC Panels for lines under the present supply scope. With regards to the requirement you are kindly requested to provide us the make and model of existing PLCC for all the lines at: a) Kanpur (Fatehpur & Panki Lines), b) Bhiwani (Mohindergarh-Bhiwani & Bhiwani-Hissar), c) Hissar (Bhiwani PG-Hissar & Moga-Hissar PG) and their corresponding remote substations for which re-wiring is required. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. |
|  | Section Project Protection coupler | Volume-II | Spare Output code in protection coupler shall be wired to send signal “Bay in bypass mode” to remote end. Kindly provide us the make and model of the protection coupler for the Kanpur, Bhiwani and Hissar Substation. | Bidders are advised to visit site as per Cl. 3.5 of section project to get required inputs. |
|  | Section Project 3.2.3.1.c PLCC Reconfiguration | Volume-II | As existing Hissar End PLCC is of BPL make, and the manufacturing of the same is obsoleted, also services are not available from BPL. Hence please suggest about the requirements of new supply of PLCC panel in absence of presence of BPL make PLCC in market. | Bidder to comply the provision of Bidding Document. |
|  | Commercial |  |  |  |
|  | GCC Clause22.2(iii) in SCC, | Section-V, Volume-I | As per this clause we presume the defect liability period for TRV capacitor is 12 months. Please confirm. | Defect Liability period of TRV capacitor shall be same as of Series reactor i.e. 60 months. |