| Sr. No. | Clause No. & Reference | Tender Description | Bidders Query | Employer’s Reply |
| --- | --- | --- | --- | --- |
|  | Price Sch-1 Sr.No. 145,481&665 | 11KV, 1CX50 SQMM XLPE INSULTED COVERED CONDUCTOR - 213KM | The Total supply Qty of MVCC is (213+815)KM = 1028 KM Whereas ETC Qty is (70+269)KM = 339KM Please confirm the ETC Qty is in CKM or KM. The clarity in this regard will us to consider the prices accordingly and can avoid potential price implications. | It is clarified that the installation of the referred BPS items are in Circuit-KM (CKM) as per the description of the items (3-Ph, 3-wire). Bidder shall quote as per the provisions of the bidding documents. |
|  | Price Sch-1 Sr.No. 460,507, | 33KV, 1CX70 SQMM XLPE INSULATED COVERED CONDUCTOR - 815KM |  |  |
|  | Price Sch-2 Sr.No. 175 286 & 341 | 11KV, 1CX50 SQMM XLPE INSULTED COVERED CONDUCTOR - 70KM |  |  |
|  | Price Sch-2 Sr.No. 460,507, | 33KV, 1CX70 SQMM XLPE INSULATED COVERED CONDUCTOR - 269KM |  |  |
|  | Sch-1, I-29 | 62.5 KVA DIESEL GENERATOR SET WITH CONTROL PANEL | Please clarify all the required equipment to be considered with this item. | For 62.5kVA DG Set, the general Technical Specifications of 100kVA rating DG set as per “Technical Specification, Section: D.G. SET, C/ENGG/SPEC/DG Rev. No: 5” shall be followed (except the kVA rating). Bidder shall quote as per the provisions of the bidding documents. |
|  | General | Fault level capacity | As per TS for 33KV & 11KV Switchgear equipment (VCB type) Fault level is given as 25KA/1sec, however as per "major scope of works" in section project (pg-26) fault level is given as 25KA/3sec. Kindly clarify which fault level to be considered as final. | In line with cl. no. 1.6 of Section-Project of Tech. Spec., in case of any conflict/ contradiction in provisions of other sections and Section-Project of the Technical Specifications, the provision given in Section-Project shall prevail. |
|  | Sch-1, "I" | Dairy Farm New SS under LR works | 1. Please confirm the number of 33KV incoming and 33KV Outgoing Feeders for this Substation. 2. Please confirm whether Switchyard lighting shall be mounted on Poles or Lighting mast (Please provide size and height of Lighting mast if required) | 1. Kindly refer Major Scope of Works at Annexure-I and Reference SLD at sl. no. 1 of Annexure-A of Section-Project of Tech. Spec. for number of 33kV feeders at Dairy Farm New substation. 2. Kindly refer to cl. no. 2.3.14.p) of Section-Project of Tech. Spec. for details regarding switchyard lighting at Dairy Farm substation. |
|  | Sch-1, I-21 | 12 kV (3-phase) Indoor Switch gear Panel for Transformer Module | In case of 11KV Indoor Switchgear CT's, "Burden-VA" and "Accuracy class" details mentioned in Section project document and Indoor Switchgear Technical specification are not matching with each other. Kinly clarify which will prevail. | In line with cl. no. 1.6 of Section-Project of Tech. Spec., in case of any conflict/ contradiction in provisions of other sections and Section-Project of the Technical Specifications, the provision given in Section-Project shall prevail. |
|  | Sch-1, I-23 | 11 KV,25 KA (3-PHASE) INDOOR SWITCH GEAR PANEL FOR LT TRANSFORMERMODULE |  |  |
|  | Sch-1, I-24 | 12 kV (3-phase) Indoor Switch gear Panel for Line Module |  |  |
|  | Sch-1, II-64 | Switchyard Lighting | Please conform whether Poles should be considered in supply for mounting of Lighting bulbs for switchyard mounting. | Kindly refer to cl. no. 2.3.14.p), cl. no. 2.3.15.d), 2.3.16.c) and 2.3.18.g) of Section-Project of Tech. Spec. for details regarding switchyard lighting at substations. |
|  | Sch-1, V-29 | SYNCHRONIZING PANEL WITH FEATURE TO SYNCHRONIZE THE DG INCOMERS WITHRESPECT TO BUS WITH AUTO, MANUAL AND CHECK SYNCHRONIZER | Provided Sl.No.15 of Annex-A in section project document does not contain any attached pdf document as mentioned. Kindly provide Technical specification to give detailed break-up for this item. | The referred document has been provided with Clarification-I/Amendment-II dtd-11.07.2025. |
|  | Sch-1,VI-136 | 20 MM DIA 2500 MM LONG GI ROD TOGETHER WITH FIXING ARRANGEMENT (EXCLUDING GI WIRE REQUIRED FOR EARTHING) AS PER APPROVEDDRAWING. | Please confirm whether treated or Untreated Earthing. | Earthing shall generally be as per the provisions of "RDSS Infra SBD-Tender drawings (Version-2) and Technical Specifications (Version-2)". Bidder shall quote as per the provisions of bidding documents. |
|  | Sch-1,VI-143 | DISC INSULATOR HARDWARE & ACCESSORIES SUITABLE TO 11 KV B&S TYPE, 45KN POLYMER INSULATORS AS PER TS | As per our present projects work knowledge, T&C type Disc insulator hardware is well suited for holding of MVCC using Wedge type Tension clamp at disc insulator. Kindly clarify or change Disc insulator hardware type. | Bidder shall quote as per the provisions of bidding documents. |
|  | Sch-1,VI-145 | 11KV, 1Cx50 Sqmm XLPE Insulted Covered conductor | Covered conductor accessories are not provided by customer in price schedule. kindly clarify whether to consider or not. | Supply and installation of mid-span joints, repair sleeves etc. for covered conductor are envisaged under the installation of covered conductor. Bidder shall quote as per the provisions of bidding documents. |
|  | Sch-1,VI-229 | 3-PHASE LT AERIAL BUNCHED CABLE (3CX25+1CX35+1CX16 SQ.MM) AS PER TS | Bare messenger size mentioned at Tension clamp is different form AB cable description in this LT AB cable work schedule. Please clarify. | Tension clamp shall be suitable for LT AB Cable 3CX25+1CX35+1CX16 SQ.MM. Kindly refer Amendment-III. |
|  | Sch-1,VI-231 | TENSION CLAMP SUITABLE FOR 3CX25+1CX25+1Cx16 Sqmm LT AB Cable AS TS |  |  |
|  | Sch-1,VI-313 | PIPE EARTHING OF 40 MM DIA, 2.5M LONG GI PIPE (MEDIUM GRADE) FORTREATED EARTHING AT DT LOCATION. | 8 SWG GI wire not given in schedule, Qty taken as per Previous PGCIL pkg DTR dwg-please confirm whether consider or not. | In line with cl. no. 2.8.4.5) of Section-Project of Tech. Spec., 25x3 mm flat shall be used for earthing of the pole. Bidder shall quote as per the provisions of bidding documents. |
|  | Sch-1,VI-317 | PG Clamp for ACSR Conductor | Please confirm the Conductor Size for PG clamps. | The conductor size for PG clamps shall be finalized during detailed engineering based on the survey. Bidder shall quote as per the provisions of bidding documents. |
|  | Sch-1,VI-377 | 250KVA, 11/0.433kV, 3PH LT Transformer complete with all accessories | Please confirm type and material of windings and also core material CRGO/Amorphous for transformer. | Kindly refer cl. no. 2.8.1.17) and 2.8.1.18) of Section-Project of Tech. Spec. for material of winding and core of distribution Transformers. Bidder shall quote as per the provisions of bidding documents. |
|  | Sch-1,VI-395 | 315kVA, 11/0.433kV, 3ph LT Transformer |  |  |
|  | Sch-1,VI-412 | 400KVA, 11/0.433KV, 3PH LT Transformer complete with all accessories |  |  |
|  | Sch-1,VI-437 | 500KVA, 11/0.433KV, 3PH LT TRANSFORMER COMPLETE WITH ALL ACCESSORIES |  |  |
|  | Sch-1,VI-438 | Supply of 30 kV, 1 phase, 10 KA polymer housing ZnO LA with all accessories as per TS | Please confirm the type of Conductor for using of LA jumpering. | The type of conductor for LA jumpering shall be finalized during detailed engineering based on the survey. Bidder shall quote as per the provisions of bidding documents. |
|  | Sch-1,VI-441 | 25KVA, 33/.433KV, 3PH TRANSFORMER WITH CRGO CORE AL WINDING | In case of 33/0.433KV Transformers, Winding Material is given Aluminium / Copper for different transformer ratings. Kindly confirm in this matter. | "Kindly refer cl. no. 2.8.1.17) of Section-Project of Tech. Spec. for material of winding of distribution Transformers. Bidder shall quote as per the provisions of bidding documents." |
|  | Sch-1,VI-442 | 50KVA, 33/.433KV, 3PH TRANSFORMER WITH CRGO CORE CU WINDING |  |  |
|  | Sch-1,VI-443 | 63KVA, 33/.433KV, 3PH STATION TRANSFORMER WITH CRGO CORE AL WINDING |  |  |
|  | Sch-1,VI-444 | 100KVA, 33/0.433KV, 3PH TRANSFORMER WITH CRGO CORE AL WINDING |  |  |
|  | Sch-1,VI-445 | 160KVA, 33/.433KV, 3PH TRANSFORMER WITH CRGO CORE CU WINDING |  |  |
|  | Sch-1,VI-446 | 200KVA, 33/0.433KV, 3PH TRANSFORMER WITH CRGO CORE AL WINDING |  |  |
|  | Sch-1,VI-447 | 250KVA, 33/0.433KV, 3PH TRANSFORMER WITH CRGO CORE CU WINDING |  |  |
|  | Sch-1, I-25 | 415V AC Distribution Board (ACDB) as per Technical Specification | Please provide Technical Specification. | Kindly refer to cl. no. 8.00 of RDSS Infra SBD Part-2_Scope of Works (Version-2) (at Page 68 of 250) for Technical Specification of ACDB. Also, refer Amendment no. II dtd-11.07.2025 for ACDB. |
|  | Sch-1, I-26 | 110 V DC Distribution Board(DCDB) | Please provide Technical Specification. | Kindly refer to cl. no. 9.00 of RDSS Infra SBD Part-2_Scope of Works (Version-2) (at Page 68 of 250) for Technical Specification of DCDB. |
|  | Sch-1, I-29 | 62.5 KVA DIESEL GENERATOR SET WITH CONTROL PANEL | Please provide Technical Specification. | Kindly, refer Amendment no. II dtd-11.07.2025. For 62.5kVA DG Set, the general Technical Specifications of 100kVA rating DG set as per the attached “Technical Specification, Section: D.G. SET, C/ENGG/SPEC/DG Rev. No: 5” shall be followed (except the kVA rating). |
|  | Sch-1, I-30 | 4.5 kg CO2 type Portable Fire extinguisher | Please provide Technical Specification. | Kindly refer to cl. no. 30.00 of RDSS Infra SBD Part-2_Scope of Works (Version-2) (at Page 80 of 250) for details of fire extinguishers. |
|  | Sch-1, I-31 | 6Kg dry chemical powered type Portable Fire extinguisher | Please provide Technical Specification. | Kindly refer to cl. no. 30.00 of RDSS Infra SBD Part-2_Scope of Works (Version-2) (at Page 80 of 250) for details of fire extinguishers. |
|  | Sch-1, V-119 | 12 KV (3-PHASE) INDOOR SWITCH GEAR PANEL FOR INCOMER DG MODULE | Please provide Technical Specification. | In line with cl. no. 2.8.1.11) of Section-Project of Tech. Spec., for 11kV Indoor switchgear panels, the min. rated current for the Bus bar and Circuit Breakers shall be 1250A and 630A respectively. The panels shall be complete with the Protection relays, Isolators, Earth Switches, Current Transformers, etc. as per the requirements of SBD Technical Specifications. |
|  | Sch-1,VI-129 | HDPE PIPE 160MM | Please provide Technical Specification. | In line with cl. no. 3.3 of Section-Project of Tech. Spec., in case the specification of any equipment /material is not included in the provided Technical Specifications, the same shall be supplied as per relevant standards. |
|  | Sch-1,VI-130 | GI Pipe 150mm dia | Please provide Technical Specification. | In line with cl. no. 3.3 of Section-Project of Tech. Spec., in case the specification of any equipment /material is not included in the provided Technical Specifications, the same shall be supplied as per relevant standards. |
|  | Sch-1,VI-135 | PG Clamp suitable for 50 Sqmm Covered Conductor | Please provide Technical Specification. | In line with cl. no. 3.3 of Section-Project of Tech. Spec., in case the specification of any equipment /material is not included in the provided Technical Specifications, the same shall be supplied as per relevant standards. |
|  | Sch-1,VI-169 | Suspension Clamp suitable for 3Cx95 + 1Cx50 sqmm 11KV AB Cable | Please provide Technical Specification. | In line with cl. no. 3.3 of Section-Project of Tech. Spec., in case the specification of any equipment /material is not included in the provided Technical Specifications, the same shall be supplied as per relevant standards. |
|  | Sch-1,VI-170 | Tension Clamp suitable for 3Cx95 + 1Cx50 sqmm 11KV AB Cable | Please provide Technical Specification. | In line with cl. no. 3.3 of Section-Project of Tech. Spec., in case the specification of any equipment /material is not included in the provided Technical Specifications, the same shall be supplied as per relevant standards. |
|  | Sch-1,VI-158 | PG CLAMP FOR AAAC RABBIT CONDUCTOR | Please provide Technical Specification. | In line with cl. no. 3.3 of Section-Project of Tech. Spec., in case the specification of any equipment /material is not included in the provided Technical Specifications, the same shall be supplied as per relevant standards. |
|  | Sch-1,VI-160 | PG CLAMP SUITABLE FOR 50SQMM AS PER TS |  |  |
|  | Sch-1,VI-173 | PG CLAMP SUITABLE FOR 70SQMM AS PER TS |  |  |
|  | Sch-1,VI-171 | MS Galvenised Forged Eye Hook suitable for 3Cx95 + 1Cx50 sqmm 11KV AB Cable | Please provide Technical Specification. | In line with cl. no. 3.3 of Section-Project of Tech. Spec., in case the specification of any equipment /material is not included in the provided Technical Specifications, the same shall be supplied as per relevant standards. |
|  | Sch-1,VI-188 | 110MM, PE80, PN-4 HDPE PIPE FOR CABLE LAYING | Please provide Technical Specification. | In line with cl. no. 3.3 of Section-Project of Tech. Spec., in case the specification of any equipment /material is not included in the provided Technical Specifications, the same shall be supplied as per relevant standards. |
|  | Sch-1,VI-463 | 160mm, PE80, PN-4 HDPE Pipe for cable laying |  |  |
|  | Sch-1,VI-384 | LT DISTRIBUTION BOX SUITABLE FOR 250 KVA DT AS PER TS | Please provide Technical Specification. | In line with cl. no. 3.3 of Section-Project of Tech. Spec., in case the specification of any equipment /material is not included in the provided Technical Specifications, the same shall be supplied as per relevant standards. |
|  | Sch-1,VI-402 | LT DISTRIBUTION BOX SUITABLE FOR 400 KVA DT AS PER TS | Please provide Technical Specification. | In line with cl. no. 3.3 of Section-Project of Tech. Spec., in case the specification of any equipment /material is not included in the provided Technical Specifications, the same shall be supplied as per relevant standards. |
|  | Sch-1,VI-435 | LT DISTRIBUTION BOX SUITABLE FOR 500 KVA DT AS PER TS | Please provide Technical Specification. | In line with cl. no. 3.3 of Section-Project of Tech. Spec., in case the specification of any equipment /material is not included in the provided Technical Specifications, the same shall be supplied as per relevant standards. |
|  | Sch-1,VI-460 | 33KV, 1Cx70 Sqmm XLPE Insulated Covered conductor | Please provide Technical Specification for MVCC Accessories | Covered conductor shall be as per the requirements of "Technical Specifications for Covered Conductor" enclosed along with the bid documents as mentioned at cl. no. 1.6 of Section-Project of Tech. Spec. |