| Sr. No. | Clause No. & Reference | Tender Description | Bidders Query | POWERGRID Reply |
| --- | --- | --- | --- | --- |
|  | Cl.no-1.6 | Section Project | As mentioned in Section project , Cl.no-1.6 -III, " RDSS Infra SBD Part-2_Technical Specification (Version-2) " , We understand that for Equipmnets " TS-III-REC RDSSInfra-SBDPart-2TS Version-2 to be followed expect the equipments like Covered conductor, 33 & 11kV Switchgear, RMU, LT AB Cable etc.. Please confirm the same. | Bidder's unerstanding is in order. Bidder shall quote as per the provisions of bidding documents. |
|  | Cl.no-2.3.8 & BOQ Sl.no-57 civil work | Foundation of Indoor switchgear Panel, C&R Panel, ACDB | As per section project cl.no- 2.3.8 , it is mentioned that " The cost of foundation shall deem to be included in the erection items for Indoor switchgear Panel, C&R Panel, ACDB etc" . However as per the BOQ Sl.no-57, civil work of CR Building including all Cable trench and accessories provided. As per our understanding , Indoor switchgear Panel, C&R Panel, ACDB separte foundation not required and the same shall be placed on top of cable trench. Kindly clarify the foundation of the said items. | Bidder's unerstanding is in order. Kindly refer to Amendment no. 1 also. |
|  | Section Project & BOQ | Main Earth Mat & Riser ( New 2x10 MVA dairy Farm Substation) | As per section project and BOQ , Main Mat of 75x8 GS flat mentioned. However the following earthing items are not specified in BOQ. 1. Earth Riser below and above ground 2. Earth Electrode Kindly confirm the same. | In line with cl. no. 2.3.3 of Section-Project of Tech. Spec., the Insulator strings hardware, Disc Insulators/Long Rod Insulators (as applicable), conductor(s), Al tube, bus-bar materials, cable trays & covers, Cable Pull pit, Bay MB, spacers, clamps & connectors, Junction box, earthwire, earthing material risers, auxiliary earthmat, buried cable trenches/pipes for equipment & lighting, cable supporting angles/channels, Insulating mats, cable sealing arrangement, all accessories etc. as required, are included in the “Erection Hardware” item of BPS. Accordingly, the earth risers below & above the ground and Earth electrodes are covered under the "Erection Hardware" item of BPS. Bidder may quote as per the provisions of the bidding documents. |
|  | section 2.3.14 ,( C) in "TS-I-Section-Project" Page 3 of 62 | 10MVA, 33/11 KV, 3-Ph Power Transformer | As per TS-I-Section-Project, we understood that 33/11kV Transformer shall be provided with cable box on 11kV side. Kindly provide the Technical specification of cable box. | Kindly refer to cl. no. 7.9.1.xiii) of RDSS Infra SBD Part-2_Technical Specification (Version-2) (at Page 25 of 809) for Technical Specification of Cable Box of 33/11kV Power Transformer. |
|  | BOQ | Nitrogen injection type fire production for 33KV transformer complete all respect | Kindly provide the technical specification of Nitrogen injection type fire production for 33KV transformer complete all respect. | Kindly refer to Amendment no. 1. |
|  | BOQ | 36KV, 1250 A, 25KA, 3-phase circuit breaker with support structure | Kindly provide the technical specification of outdoor type 36KV, 1250 A, 25KA, 3-phase circuit breaker. | In line with cl. no. 2.8.1 of Section-Project of Tech. Spec., the 33kV Circuit Breakers shall be provided as per the latest REC specification & relevant Construction Standards, as applicable, meeting the requirements of bidding documents. |
|  | BOQ Sl No. 10. Page 508 of 809 of "TS-III-REC-RDSSInfra-SBDPart-2TSVersion-2" under section 28 sr no. 2 | 11KV, 400A, 3-Ph, vertical mounted AB switch | As per price schedule, required configuration of 11KV AB switch is 400A whereas in TS current rating of 11KV AB switch 200A. Kindly provide the detailed techinical specification of 11KV, 400A, 3-Ph, vertical mounted AB switch . | The current rating of 11kV AB Switch shall be as per the BPS. Other technical parameters shall be as per the provisions of Section-Project and RDSS Infra SBD Part-2_Technical Specification (Version-2). |
|  | BOQ | 9KV surge arrester (1-Phase) | Please confirm 9KV surge arrester class & KA rating. | The technical specifications 9kV Surge Arrester (Lightning Arrestor) shall be as per the provisions of Section-Project and RDSS Infra SBD Part-2_Technical Specification (Version-2). |
|  | BOQ schedule I, II, III & IV | Bus bar & Bay equipment conductor | Please note that, the item & Qty of ACSR Conductor not available in bOQ for substation schedules. Kindly confirm the scope of the same. | In line with cl. no. 2.3.3 of Section-Project of Tech. Spec., the Insulator strings hardware, Disc Insulators/Long Rod Insulators (as applicable), conductor(s), Al tube, bus-bar materials, cable trays & covers, Cable Pull pit, Bay MB, spacers, clamps & connectors, Junction box, earthwire, earthing material risers, auxiliary earthmat, buried cable trenches/pipes for equipment & lighting, cable supporting angles/channels, Insulating mats, cable sealing arrangement, all accessories etc. as required, are included in the “Erection Hardware” item of BPS. Accordingly, the ACSR conductor is covered under the "Erection Hardware" item of BPS. Bidder may quote as per the provisions of the bidding documents. |
|  | Page no 68 of 250 of TS-II REC RDSSInfra-SBDPart-2SoWVersion-2 under section 13.3 sl no 8 & 9 | ACDB & DCDB | We understand that the technical specification of ACDB & DCDB as per TS-II REC RDSSInfra-SBDPart-2SoWVersion-2 . Kindly confirm . | Kindly refer to cl. no. 8.00 and 9.00 of RDSS Infra SBD Part-2_Scope of Works (Version-2) (at Page 68 of 250) for Technical Specification of ACDB and DCDB respectively. |
|  | BOQ | 62.5KVA diesel generator set with control panel | Kindly provide the technical specification of 62.5KVA diesel generator set with control panel. | Kindly refer to Amendment no. 1. |
|  | Page 66 of 250 of "TS-II REC RDSSInfra-SBDPart-2SoWVersion-2" | Distribution Box for Aux. tranformer | As per part 2 of "EMPLOYER’S REQUIREMENTS", we understood that there is requirement of Distribution Box for Aux. tranformer. However the same is not available in the BOQ line items. Kindly confirm the requirement. | Separate distribution box for station auxiliary transformer is not envisaged at the substation. However, the ACDB shall have the provisions of feeders (with MCB/ MCCB, timer etc.) for lighting system, as per the requirements. Kindly refer Amendment no. 1 also. |
|  | under section 14 sl no C of Page 56 of 250 of TS-II REC RDSSInfra-SBDPart-2SoWVersion-2. | GI Pipe 150mm dia | We understand that 150mm dia GI pipe shall be used for cable support at DP structure. Kindly confirm . | Referred clause is applicable for 33 kV line for underground railway crossing. Bidder shall quote as per the provisions of the bidding docuements. |
|  | Erection BOQ Sh-2 sl.no-109 | Cover conductor accessories for HT & LT | Along with Stringing of Cover conductor , This shall also include supply and installation of mid span joints, repair sleeves, danger plate, anti-climbing device. Please provide the Technical Specification of accessories mentioned above. | The accessories for covered conductor shall be provided complying to relevant standards meeting the requirements of Tech. Spec. |
|  | Page 349 of 809 of "TS-III REC RDSSInfra-SBDPart-2TSVersion-2" | 3-Ph 11KV, XLPE insulated, Bare messanger Aerial Bunched Cable (3Cx95+1Cx50 Sqmm),(3Cx120+1Cx70 Sqmm) & (3Cx50+1Cx35 Sqmm) | Technical specification of 35 & 70 sqmm 3-Ph 11KV, XLPE insulated cable provided in TS. Kindly provide the technical specification of Bare messanger Aerial Bunched Cable (3Cx95+1Cx50 Sqmm), (3Cx120+1Cx70 Sqmm) & (3Cx50+1Cx35 Sqmm) | Kindly refer cl. no. 16.B of RDSS Infra SBD Part-2_Technical Specification (Version-2) (Page 347 of 809) for Technical Specifications of 11kV AB Cables. |
|  | BOQ | Technical specification of HT AB cable accessories | Kindly provide the technical specification of HT AB cable accessories. | The accessories for HT AB Cable shall be provided complying to relevant standards meeting the requirements of Tech. Spec. |
|  | Page 361 of 809 of "TS-III REC RDSSInfra-SBDPart-2TSVersion-2" | Technical specification of 11kV grade 3Cx95 sqmm (XLPE) Power Cable | As per TS 3Core 120, 150, 185, 240, 300 sq mm XLPE power cable's specification provided. Kindly provide the technical specification of 11kV grade 3Cx95 sqmm (XLPE) Power Cable | Kindly refer cl. no. 17 of RDSS Infra SBD Part-2_Technical Specification (Version-2) (Page 355 of 809) for Technical Specifications of 11kV XLPE cables. |
|  | BOQ | 1.1KV 4CX35SQMM XLPE POWER CABLE | Kindly provide the technical specification of 1.1KV 4CX35SQMM XLPE Power cable. | Kindly refer cl. no. 15 of RDSS Infra SBD Part-2_Technical Specification (Version-2) (Page 323 of 809) for Technical Specifications of LT XLPE cables upto 1100 V. |
|  | BOQ | 1.1 KV, 1 CORE 25 MM2, UNARMOURED XLPE CABLE | Kindly provide the technical specification of 1.1 KV, 1 CORE 25 MM2 XLPE cable. | Kindly refer cl. no. 15 of RDSS Infra SBD Part-2_Technical Specification (Version-2) (Page 323 of 809) for Technical Specifications of LT XLPE cables upto 1100 V. |
|  | BOQ | 1.1 KV, 1 CORE 70 MM2 & 240 MM2 FRLS, PVC CABLE | Kindly provide the technical specification of 1.1 KV, 1 CORE 70 MM2, FRLS, PVC CABLE | 1.1kV, PVC cables shall generally conform to IS 1554. |
|  | BOQ | 1.1 KV, 1 CORE 240 MM2 FRLS, PVC CABLE | Kindly provide the technical specification of 1.1 KV, 1 CORE 240 MM2 FRLS, PVC CABLE | 1.1kV, PVC cables shall generally conform to IS 1554. |
|  | BOQ | 1.1 KV, 1 CORE 630 MM2 FRLS, PVC CABLE | Kindly provide the technical specification of 1.1 KV, 1 CORE 630 MM2 FRLS, PVC CABLE | 1.1kV, PVC cables shall generally conform to IS 1554. |
|  | BOQ | 11KV HG FUSE INCLUDING ALL ACCESSORIES | Kindly provide the technical specification of 11KV HG fuse including all accessories. | 11kV HG Fuse shall generally conform to IS 9385. |
|  |  | Cable box at LV side for above 200KVA distribution transformer. | Kindly provide the technical specification of Cable box at LV side for above 200KVA distribution transformer. | Cable Box shall be provided as per the provisions of RDSS Infra SBD Part-2_Technical Specification (Version-2) |
|  | BOQ | 33KV, 3 PHASE HG FUSE | Kindly provide the technical specification of 33KV HG fuse including all accessories. | 11kV HG Fuse shall generally conform to IS 9385. |
|  | BOQ | 20 MM DIA 2500 MM LONG GI ROD | Kindly provide Technical Specification of 20 MM DIA 2500 MM LONG GI ROD. | Kindly refer cl. no. 37 of RDSS Infra SBD Part-2_Technical Specification (Version-2) (Page 559 of 809) for Technical Specifications of GI Rod for earthing. However, the diameter and length of the GI rod shall be as per BPS. |
|  | South Andaman |  |  |  |
|  | Sch-1, IV.3- Extn of Panighat S/s | BOQ | In Extn. of 33kV Panighat SS for 33 kV 3Cx300 sq.mm aluminium, armoured XLPE cable only 33 kV Outdoor Termination Kit suitable for 33 kV, 3Cx300 sq.mm is in scope of Bidder. Please confirm the same | Bidder shall quote as per the provisions of bidding documents. |
|  | Sch-1, VII, 128, Line Works South Andaman | BOQ | Nuts & Bolts quantity in supply BOQ is 248 MT against 4.96 MT of fabrication. Please check and verify the required quantity of Nuts & Bolts as it is on higher side w.r.t fabrication. | Refer revised BOQ at Amendment - I |
|  | Sch-1, VII, 146, Line Works South Andaman | BOQ | Nuts & Bolts quantity in supply BOQ is 80 MT against 1.6 MT of fabrication. Please check and verify the required quantity of Nuts & Bolts as it is on higher side w.r.t fabrication. | Refer revised BOQ at Amendment - I |
|  | North & Middle Andaman |  |  |  |
|  | Sch-1, VIII, 3, Line Works North & Middle Andaman | BOQ | Nuts & Bolts quantity in supply BOQ is 400 MT against 6.4 MT of fabrication. Please check and verify the required quantity of Nuts & Bolts as it is on higher side w.r.t fabrication. | Refer revised BOQ at Amendment - I |
|  | Sch-1, VIII, 88, Line Works North & Middle Andaman | BOQ | Nuts & Bolts quantity in supply BOQ is 176 MT against 3.52 MT of fabrication. Please check and verify the required quantity of Nuts & Bolts as it is on higher side w.r.t fabrication. | Refer revised BOQ at Amendment - I |
|  | Sch-2, VIII, 9, Line Works North & Middle Andaman | BOQ | In erection BOQ 11 mtr pole quantity is 320 nos while in supply BOQ of the same it is 200 nos. Please clarify the quantity for supply and erection. | Refer revised BOQ at Amendment - I |
|  | Sch-2, VIII, 12, Line Works North & Middle Andaman | BOQ | In erection BOQ 33 KV 70 sqmm ceovered conductor quantity is 960 km, while in supply BOQ of the same it is 152 km. Please clarify the quantity for supply and erection. | Refer revised BOQ at Amendment - I |
|  | Nicobar Island |  |  |  |
|  | Sch-1, IX, 3, Line Works Nicobar Island | BOQ | Nuts & Bolts quantity in supply BOQ is 400 MT against 6.4 MT of fabrication. Please check and verify the required quantity of Nuts & Bolts as it is on higher side w.r.t fabrication. | Refer revised BOQ at Amendment - I |
|  | Sch-1, VIII, 47,Line Works Nicobar Island | BOQ | Nuts & Bolts quantity in supply BOQ is 450 MT against 1.5 MT of fabrication. Please check and verify the required quantity of Nuts & Bolts as it is on higher side w.r.t fabrication. | Refer revised BOQ at Amendment - I |
|  | Sch-1, VIII, 88, Line Works Nicobar Island | BOQ | Nuts & Bolts quantity in supply BOQ is 80 MT against 1.6 MT of fabrication. Please check and verify the required quantity of Nuts & Bolts as it is on higher side w.r.t fabrication. | Refer revised BOQ at Amendment - I |
|  | Sch-1, VIII, 106, Line Works Nicobar Island | BOQ | Nuts & Bolts quantity in supply BOQ is 40 MT against 0.8 MT of fabrication. Please check and verify the required quantity of Nuts & Bolts as it is on higher side w.r.t fabrication. | Refer revised BOQ at Amendment - I |
|  | CIVIL |  |  |  |
|  | - | General (Garacharma, Phoenix, Panighat, Sitanagar) | Kindly provide existing FGL, foundation plinth levels to be considered in substation. | The existing drawings have been provided with the biding documents. Further, in line with cl. no. 1.5 of Section-Project of Tech. Spec., the bidder are advised to visit the substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy. Bidder shall quote as per the provisions of bidding documents. |
|  | - | General (Garacharma, Phoenix, Panighat, Sitanagar) | Kindly provide the existing soil investigation report. | In line with cl. No. 2.3.15.f), 2.3.16.d) & 2.3.18.c) of Section-Project of Tech. Spec., soil investigation at Garacharma, Phoenix Bay and Sitanagar subsations are to be carried out under present scope of works by the contractor. Further, in line with cl. no. 1.5 of Section-Project of Tech. Spec., the bidder are advised to visit the substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy. |
|  | - | General (Dairy farm, Garacharma, Phoenix, Panighat, Sitanagar) | Open Raft type foundation have been considered for all civil works within switchyard. No Pile type foundation are envisaged. | Bidder's understanding is in order for substation works. Bidder shall quote as per the provisions of bidding documents. |
|  | 4. Reference Layout drawing for 33/11kV Dairy Farm New substation (pg no.-33) & Standard civil drawings (Annexure-B) (pg no.- 40) | TS-I-Section-project | We understand that the Dairy Farm New substation building will have overall dimensions of 20000 mm x 12000 mm. As per the proposed layout, the CRB shall consist of the following rooms and facilities: Control room, I/C room, Battery room, store room, Toilet and dedicated area within the CRB for DG set foundation and Auxiliary Traformer foundation. Kindly confirm the above details. | In line with cl. no. 11.00.a) of RDSS Infra SBD Part-2_Scope of Works (Version-2) (at Page 151 of 250), the layout of the control room building shall be finalized during detailed engineering. |
|  | Sl.no.- (I)- Dairy farm New SS under LR works, (70)- Civil works | Price_schedule | Control room building for the Dairy Farm New substation, we understand that the RCC Roof slab is not required. Instead, a structural steel truss with a four-sided sloping roof shall be provided. Kindly confirm the above requirement so that we may proceed accordingly with the structural planning. | Structural steel truss shall be proviided on Control Room Building over the RCC roof slab. Bidder shall quote as per the provisions of bidding documents. |
|  | 13.9. Civil works and soil investigation (11). Buildings - General Requirements (pg no.-151) & Sl.no.- (I)- Dairy farm New SS under LR works, (70)- Civil works | TS-II-REC RDSSInfra-SBDPart-2SoWVersion-2 & Price_schedule | As per the technical specification & Price schedule, the Control Room Building for the Dairy Farm New Substation is proposed to be constructed as an RCC frame structure using M20 grade concrete for reinforced components and PCC M10 grade concrete for plain cement concrete works. Kindly confirm. | The RCC shall be of M30 grade and PCC shall be 1:2:4 & 1:4:8, for substation works as per the provisions of bidding documents. |
|  | 2.3.15 Salient Points for Extension of existing 33kV Garacharma substation (pg no.-05) 2.3.17 Salient Points for Extension of 33kV Panighat substation (pg no.-06) 2.3.18 Salient Points for Extension of 33/11kV Sitanagar substation (pg no.- 06) | TS-I-Section-project | a). We understand that the existing structures and switchyard equipment at Garacharma, Sitanagar, and Panighat substations are scheduled to be dismantled. In this regard, we kindly request Please provide details regarding the designated area/location for the disposal or storage of dismantled materials and equipment from the substations. b). For foundation dismantling works at the substation. Kindly provide the approximate distance of the disposal site from the substation. | In line with cl. no. 2.7 of Section-Project of Tech. Spec., the dismantled material shall be stored at the designated site office under the concerned division/ sub-division of EDANA with proper handing over. |
|  | 7. Reference Existing Earthmat layout for 33/11kV Garacharma substation (pg no.- 35), 14. Reference Existing Layout for 33/11kV Sitanagar substation (pg no.-39) | TS-I-Section-project | We understand that a road already exists at the substation site; therefore, construction of a new road is not included in the bidder's scope. Kindly confirm. | Construction of new road at existing substations (Phoenix Bay, Garacharma, Panighat and Sitanagar) are not envisaged under subject package. |
|  | - | General (Garacharma, Phoenix, Panighat, Sitanagar) | We understand that outdoor cable trench is already available in bay extension side with adequate size. Kindly confirm the same. | Construction of new cable trench at Sitanagar and Panighat substations are not envisaged. Bidder may quote as per the provisions of the bidding documents. |
|  | Sl.no.- II: Ext. of 33kV Garacharma SS, (18): Dismantling and Re-erection | Price_schedule | Kindly provide the Height of Lighting mast (LM) or the structure drawing. | In line with cl. no. 1.5 of Section-Project of Tech. Spec., the bidder are advised to visit the substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy. |
|  | Sl.no.- V: Ext. of 33kV Sitanagar SS (30): Dismantling | Price_schedule | Dismantling of the existing transformer along with its associated accessories shall be in the bidder's scope. However, dismantling or demolition of the existing transformer foundation shall not be in the bidder's scope. Kindly confirm. | Demolishing of foundation of existing 33/11kV Power Transformer at Sitanagar substtaion is deemed included under the relevant BPS item for dismantling. |
|  | General |  |  |  |
|  | - | General | We undersatnd that for completion of project if any material other than available in BOQ will be required, the payment of the extra materials will be paid by Employer. Please clarify our under standing. | Bidder may quote as per the provisions of the bidding documents. |
|  | - | General | Kindly clarify the designated CIP site for material transportation, considering there are four distinct locations: South Andaman, North Andaman, Middle Andaman, and Nicobar. | Bidder may quote as per the provisions of the bidding documents. |
|  | - | General | Replacement of underground cable is a challenging and sensitive task, there is a possibility of accidental damage to existing underground cables (which need to replaced) during the replacement work. Kindly confirm that any such damage, if it occurs unintentionally during the execution of the work, will not be considered under the bidder’s responsibility. | In line with sl. no. 4 of cl. no. 2.4.2 of Section-Project of Tech. Spec., removal of existing buried cables is not envisaged considering practical difficulties. However, in line with the above said clause, Public (Road, Footpath, boundary, etc.) or personnel property damaged during UG cabling work shall be repaired by the contractor without anny cost implication to the Employer and the dismantled material (If any) shall be transported to the designated store of the DISCOM. |
|  | Technical Specification | LT Control Cable | Kindly provide the Technical Specification (TS) of the synchronising panel with the capability to synchronise the DG Incomer with respect to the bus including Auto, Manual and check synchroniser mode | Kindly refer to sl. no. 15 of Annexure-A of Section-Project wherein existing C&R scheme and Panel drawings for 33/11kV Sitanagar substation are provided for reference. Synchronising panel, at least with the scheme & functions of existing synchronizing panel, shall be provided as per the provisions of biding documents to meet the project requirement. |
|  | Technical Specification | Synchronising Panel | Kindly confirm the designated store | In line with cl. no. 2.7 of Section-Project of Tech. Spec., the dismantled material shall be stored at the designated site office under the concerned division/ sub-division of EDANA with proper handing over. |
|  | Scope of work | Dismantling of existing overhead conductor, associated structures, insulated hardware, etc. (wherever required) and transporting the material to the designated store of the DISCOM | Kindly provide the typical sectional drawing of the HT buried cable trench | Contractor has to develop the drawing in line with the relevant standard and meeting the provisions of bidding documents. |
|  | 33KV/11KV UG Cable | Typical section Drawing | Kindly provide the Technical Specification (TS) of the synchronising panel with the capability to synchronise the DG Incomer with respect to the bus including Auto, Manual and check synchroniser mode | Kindly refer to sl. no. 15 of Annexure-A of Section-Project wherein existing C&R scheme and Panel drawings for 33/11kV Sitanagar substation are provided for reference. Synchronising panel, at least with the scheme & functions of existing synchronizing panel, shall be provided as per the provisions of biding documents to meet the project requirement. |
|  | Section Project (Page No. 28 of 62) | 33/0.4 KV DT for New Load, replacement & augmentation - 107 Nos. | Kindly provide the bifurcation of the quantity of the category wise, i.e new Installation, Augmentation and replacement | Bidder may quote as per the provisions of the bidding documents. |
|  | SLD-Annexure-A of Section Project | SLD, Layout and Earthmat Drawing | Kindly provide the readable copies of the followings for better understanding: 1. 2x10 MVA Dairy Farm New SS 2. Extension of 33KV Garacharma SS 3. Phonix SS 4. Sita Nagar SS | Existing drawings for the mentioned substations have already been provided with the bidding documents. Further, in line with cl. no. 1.5 of Section-Project of Tech. Spec., the bidder are advised to visit the substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy. |