| POWER GRID CORPORATION OF INDIA LTD. (A Government of India Enterprise) |  |  |
| --- | --- | --- |
| STANDARD TECHNICAL SPECIFICATION FOR tower package TW27 …………………………………………………………….. Transmission Line associated with …………………………………………………………….. Comprehensive scheme for strengthEning of tranmission and distribution system in arunachal pradesh |  |  |
|  | March-2018, Rev-06 |  |

| SECTION-I | GENERAL INFORMATION & SCOPE | REVISION –6 (dtd 07/09/2017) |
| --- | --- | --- |
| SECTION-II | GENERAL TECHNICAL CONDITIONS | REVISION – 4 (dtd 23/12/2016) |
| SECTION-III | SURVEY AND SOIL INVESTIGATION | REVISION – 5 (dtd 07/09/2017) |
| SECTION-IV | TOWER, FOUNDATION, ERECTION, STRINGING AND COMMISSIONING OF LINE | REVISION – 6 (dtd 07/09/2017) |
|  | SFQP | Rev-05, dtd 29/01/2016 |
|  | MQP | Rev-03, dtd |
| SECTION-V | GALVANISED STEEL EARTHWIRE | REVISION – 1 (dtd 07/09/2017) |
| SECTION-VII | ACSR CONDUCTOR | REVISION – 1 (dtd 24/09/2015) |
| SECTION-VIII | COMPOSITE INSULATOR | REVISION – 1 (dtd 27/12/2017) |
| SECTION-X | OPGW (SUPPLY & ERECTION BY CONTRACTOR) |  |
| SECTION-XA | OPGW (ONLY ERECTION BY CONTRACTOR) |  |

| POWER GRID CORPORATION OF INDIA LTD. (A Government of India Enterprise) |  |  |  |
| --- | --- | --- | --- |
| TECHNICAL SPECIFICATION FOR …………………………………………………………….. Tower package TW27 for M/C portion of following transmission line. (i) 132kV S/C on D/C Naharlagun – Sagali T/L (ii) 132kV S/C on D/C Naharlagun – Banderdewa T/L and (iii) 132kV S/C on D/C Naharlagun – Gerukamukh T/L …………………………………………………………….. |  |  |  |
|  | VOLUME-II March-2018, Rev-06 (With modifications upto OCT-2019) |  |  |
| Specification No.: Document Code No. |  | ---------------------------(To be inserted by CS Dept.) ---------------------------(To be inserted by CS Dept.) |  |
| (This document is meant for the exclusive purpose of bidding against this specification and shall not be transferred, reproduced or otherwise used for purposes other than that for which it is specifically issued). |  |  |  |

Brief Summary of Major changes in the Standard Technical Specification Rev-6-March-2018

| S.No | Description of Changes | Clause no. | Sec |
| --- | --- | --- | --- |
| SECTION-I |  |  |  |
| 1. | Minimum quantity of sagging bridges and minimum six number of power operated hydraulic/ motorized winch machines and use of Helicopters/ Drones in stringing process | 1.1.8 | SECTION-I |
| SECTION-III |  |  |  |
| 1. | Provision for Detailed soil investigation for at least 1 location for every 5 kms. | 4.2.1 | SECTION-III |
| 2. | Hammer weight for SPT test and depths of test specified as per IS | 4.5.2.2, 4.5.2.3, 4.5.2.4, 4.5.3.2, 4.5.3.3 & 4.5.5 | SECTION-III |
| SECTION-IV |  |  |  |
| 1. | Min. cement content of 330kg/m3 specified for RMC | 2.6.2.5 | SECTION-IV |
|  | SFQP:Rev-06 | - | SECTION-IV |
|  | MQP:Rev-04 | - | SECTION-IV |
|  | MQP:Rev-05 | - | SECTION-IV |
| 2. | Measurement of dimensions of compression type joints before and after compression & maintenance of record by the Contractor. | 3.8.3 | SECTION-IV |
| 3. | Thermo-vision scanning of compression type joints of the complete line by the Contractor | 3.14.3 | SECTION-IV |
| 4. | Earthing for River Crossing Towers/Pile foundation | 1.7.6 | SECTION-IV |
| 5. | Use of helicopter for faster erection of transmission line | 3.1.1 | SECTION-IV |
| 6. | Mandatory use of Gin pole / Centre mast for tower erection | 3.3 | SECTION-IV |
| 7. | T&P and PPEs clauses in addition to Safety Plan & GCC provisions. | 3.3.2 | SECTION-IV |
| 8. | Provision for using safety net during tower erection. | 3.3.3 | SECTION-IV |
| 9. | Broad list & basic parameters of major T & P to be used for tower erection & stringing included | 3.3.2 | SECTION-IV |
| SECTION-VIII |  |  |  |
| 1. | Use of fully threaded Bolts as an alternative for grading rings. Standards specified | 1.4.5 | SECTION-VIII |
| 2. | Use of suitable anti-fungal and Avian repellent admixtures/additives. | 1.4.2 | SECTION-VIII |
| 3. | Removable covers for 10% insulators of each rating. | 4.12.6 | SECTION-VIII |

Brief Summary of Major changes in the Technical Specification from Rev-5 to Rev-6

Page- 1 of 2

| S.No | Description of Changes | Clause no. |  | Sec |
| --- | --- | --- | --- | --- |
| SECTION-I |  |  |  |  |
| 1 | Provision of Insulated Conductor sleeve (if required & covered under BPS) | 1.1.2(viii) |  | Sec-I |
| 2 | Installation of OPGW under live line Condition (where ever applicable & covered under BPS) | 1.1.2(xv) |  | Sec-I |
| 3 | Use of ladder on Insulator strings | 1.1.8 |  | Sec-I |
| 4 | Use of drones for stringing of pilot wires/ropes for pilot wire | 1.1.8 |  | Sec-I |
| 5 | For finalization of sub-vendor by Contractor & QR for Contractor’s supplied line material | 2.0 |  | Sec-I |
| 6 | Submission of CPG to POWERGRID regional HQ with intimation to Engg. | 2.0 |  | Sec-I |
| SECTION-II |  |  |  |  |
| 1 | Modification in clauses of Quality Assurance Programme | 1.7 |  | Sec-II |
| SECTION-III |  |  |  |  |
| 1 | Provision of collection of data/details of ownership of land within the line corridor & tower base. | 1.1 e. |  | Sec-III |
| 2 | Provision of Oil/gas pipeline crossing | 3.5.4(i) |  | Sec-III |
| 3 | Provision of Collection of data/details of ownership of land within the line corridor and tower base. | 3.6.3.1 |  | Sec-III |
| 4 | Indian Standards and codes | 4.4.2 |  | Sec-III |
| 5 | Format for data/details of ownership of land | Annex-E |  | Sec-III |
| SECTION-IV |  |  |  |  |
| 1 | Measurement of Tower Footing Impedance | 1.7.3 |  | Sec-IV |
| 2 | New clause added in regard of Chemical earthing | 1.7.5 |  | Sec-IV |
| 3 | Inclusion of Hard rock earthing with reduced depth. | 1.7.7 |  | Sec-IV |
| 4 | For alternative use of ready-mix concrete, minimum grade of M25 is specified | 2.6.2.2 & 2.10.1 |  | Sec-IV |
| 5 | Concrete of M25 grade design mix as per IS:456, Ready-mix concrete for foundations of railway crossing locations. | 2.6.2.3 |  | Sec-IV |
| 6 | Use of small batching machines/self-loading mixers for concrete mixing. | 2.6.2.4 |  | Sec-IV |
| 7 | Use of crushed stone in place of natural sand, in case of non-avaiability or restriction by local authority. | 2.6.7 |  | Sec-IV |
| 8 | New clause added regarding foundations in creek or aggressive soil areas. | 2.6.8 |  | Sec-IV |
| 9 | Provision for Individual leg stub Setting template added | 2.9.3 | Sec-IV |  |
| 10 | Measurement of stub level, back to back dimensions, diagonal dimensions etc. after completion of foundation. | 2.15 | Sec-IV |  |
| 11 | Plugging of open holes | 3.3.1 (f) | Sec-IV |  |
| 12 | Meggering of only Porcelain Disc Insulators | 3.5 | Sec-IV |  |
| 13 | New clause added regarding jumper drop | 3.10.3 | Sec-IV |  |
| 14 | New clause regarding Insulated conductor sleeve on bare conductor of Power line, National Highway and expressway crossing and jumper of transposition tower | 3.11.1 | Sec-IV |  |

Brief Summary of Major changes in the Technical Specification from Rev-5 to Rev-6

Page- 2 of 2

| 15 | Provision of minimum 4 nos. of high resolution geo tagged photographs of each tower after completion of stringing |  | 3.14.1 |  | Sec-IV |
| --- | --- | --- | --- | --- | --- |
| SECTION-V |  |  |  |  |  |
| 1 | Standard specification of GS Earthwire |  | - |  | Sec-V |
| SECTION-VII |  |  |  |  |  |
| 1 | Standard specification of ACSR Conductor |  | - |  | Sec-VII |
| SECTION-VIII |  |  |  |  |  |
| 1 | Standard specification of Composite Insulator |  | - |  | Sec-VIII |
| SECTION-XI |  |  |  |  |  |
| 1 |  | Drawing of Quad tension string modified to change the orientation of strap. |  | Drawing enclosed. | Sec-IX |
| 2 |  | Standard Drum drawing for GS earthwire enclosed in specification. |  | Drawing enclosed. | Sec-IX |
| 3 |  | Standard Drum drawing for ACSR Conductor enclosed in specification. |  | Drawing enclosed. | Sec-IX |
| 4 |  | Standard drawing for Chemical Pipe type earthing enclosed in specification. |  | Drawing enclosed. | Sec-IX |
| 5 |  | Standard drawing for Chemical Counterpoise type earthing enclosed in specification. |  | Drawing enclosed. | Sec-IX |
| 6 |  | Drawing of Stub setting Template (individual leg) enclosed in specification. |  | Drawing enclosed. | Sec-IX |
| SECTION-X* |  |  |  |  |  |
| 1 |  | Technical specification of OPGW, wherein supply & erection of OPGW is in the scope of Contractor |  | - | Sec-X |
| SECTION-XA* |  |  |  |  |  |
| 1 |  | Technical specification of OPGW, wherein only erection of OPGW is in the scope of Contractor |  | - | Sec-XA |

Brief Summary of Major changes in the Technical Specification from Rev-4 to Rev-5

Page- 1 of 3

| S.No | Description of Changes |  | Clause no. |  | Sec |
| --- | --- | --- | --- | --- | --- |
| SECTION-I |  |  |  |  |  |
| 1 | To promote mechanization and safe working conditions, use of crane is being promoted for tower erection. (a) Use of tractor not permitted for tower erection. (b) Use power operated winch machines proposed for tower erection. |  | 1.1.2(viii) |  | Sec-I |
| 2 | Provision for Power line crossing section under Live Line Condition (where ever applicable & covered under BPS) |  | 1.1.2(x) |  | Sec-I |
| 3 | Panel wise dispatch. |  | 1.1.2.3 |  | Sec-I |
| 4 | In case part quantity of tower/tower part supplied by Employer or other supplier. Erection contractor shall take delivery of material (tower/towers parts) at their store. |  | 1.1.5 |  | Sec-I |
| 5 | The scope of installation/stringing shall include splicing, termination, testing, demonstration for acceptance & commissioning as well as documentation. |  | 1.1.6 |  | Sec-I |
| 6 | Modifications regarding use of TSE |  | 1.1.8 |  | Sec-I |
| 7 | Use of Sagging bridges/working platform. |  | 1.1.8 |  | Sec-I |
| 8 | Use of power operated winch machine for carrying out final sagging |  | 1.1.8 |  | Sec-I |
| 9 | Use of tractor not permitted for final sagging. |  | 1.1.8 |  | Sec-I |
| 10 | The Contractor shall use power operated winch machines for final sagging. |  | 1.1.8 |  | Sec-I |
| 11 | Use of tractor not permitted for entire stringing of OPGW |  | 1.1.8 |  | Sec-I |
| 12 | Stringing of OPGW shall be carried out by using power operated winch machine. |  | 1.1.8 |  | Sec-I |
| 13 | Contractor Execution plan |  | 1.5 |  | Sec-I |
| 14 | QR for pile foundation, whenever Pile foundation is in the scope of tower Package |  | 2.1 |  | Sec-I |
| SECTION-II |  |  |  |  |  |
| 1 | Modification in clauses of Inspection & Testing. |  | 1.8 |  | Sec-II |
| 2 | Guidelines for storages of different type of material used for transmission line package. |  | 1.11 |  | Sec-II |
| SECTION-III |  |  |  |  |  |
| 1 | Change in provision of railway crossing clearance. |  | 3.5.4(e)vi |  | Sec-III |
| 2. | Change in provision of Power line Crossing |  | 3.5.4(g) |  | Sec-III |
| SECTION-IV |  |  |  |  |  |
| 1 | Clarification w.r.t Proto assembly of towers clauses | 1.1.2 |  | Sec-IV |  |
| 1a | For snow zone Grade of MS & HT steel section E250 Grade C & E350 Grade C has been specified as per IS:2062:2011 | 1.2.1 |  | Sec-IV |  |
| 2 | Provision of Step bolts on diagonally opposite legs in case of single circuit towers. | 1.3.1 |  | Sec-IV |  |

Brief Summary of Major changes in the Technical Specification from Rev-4 to Rev-5

Page- 2 of 3

| 3 | Provision for suitable cleat /plate for installation of Bird Guard for I type/ V type string on all suspensionTowers after stringing. | 1.3.5.1 |  | Sec-IV |  |
| --- | --- | --- | --- | --- | --- |
| 4 | The punching may be adopted for thickness upto 12 mm instead of 16 mm. | 1.4.7.2 |  | Sec-IV |  |
| 5 | Panel wise dispatch. | 1.5.1 |  | Sec-IV |  |
| 6 | Provision for spare tower quantity. | 1.5.2 |  | Sec-IV |  |
| 7 | Weight of D-shackle/hangers & Pack washer | 1.5.3 |  | Sec-IV |  |
| 8 | New clause added in regard of pipe type earthing | 1.7.2 |  | Sec-IV |  |
| 9 | Inclusion of additional Earthing requirement. | 1.7.6 |  | Sec-IV |  |
| 10 | Additional Rod type earthing shall be provided in one of the foundation pit | 1.7.7 |  | Sec-IV |  |
| 11 | Addition of new type of foundation i.e. “Wet Cultivated”. | 2.3.4 |  | Sec-IV |  |
| 12 | New clause added in respect of sub-soil water table. | 2.3.10 |  | Sec-IV |  |
| 13 | For clarity, Nominal Mix for concreting has been designated as nominal volumetric mix in line with the provision stipulated in technical specification of Substation civil package | 2.6.1 |  | Sec-IV |  |
| 14 | To avoid any mishap during exaction of soil, provision for slopped / step excavation added. | 2.7.1.3 | Sec-IV |  |  |
| 15 | Clarity in clause of Excavation for Blasting for Fissured rock made more clear. | 2.7.1.5 | Sec-IV |  |  |
| 16 | Provision for Prop Setting template for Multi circuit towers, for tower with +18/25/30 m extension and Anchor tower have also been included in the specification. | 2.9.3 | Sec-IV |  |  |
| 17 | Provision for application of anti-corrosive paint in case wet/PS/FS&WBC foundation in the 50 mm coping portion as well as 350 mm above CL. | 2.10.6 | Sec-IV |  |  |
| 18 | All the excavated earth shall be placed over the filled in pit to allow further settlement by gravity and Proctor test for Compaction of Backfill of foundation has been deleted. | 2.12.2 | Sec-IV |  |  |
| 19 | Use of Tractor for tower erection & final sagging shall not be permitted. | 3.0 | Sec-IV |  |
| 20 | For erection of towers using crane (wherever feasible) Cranes of suitable capacity along with other necessary T&P, power operated winches, Gin pole etc. shall be deployed by the Contractor accordingly. | 3.3 | Sec-IV |  |
| 21 | Verticality requirement for erection of Tower has been added. | 3.3.1(g) | Sec-IV |  |
| 22 | All nuts shall be tightened properly using torque wrench, applying the torque recommended by manufacturer of bolts & nuts | 3.4.1 | Sec-IV |  |
| 23 | Extra consumption of OPGW indicated | 3.13.2 | Sec-IV |  |
| 24 | Provision for use of returnable steel/hybrid drum as an alternative has been included. | 3.13.4 | Sec-IV |  |

Brief Summary of Major changes in the Technical Specification from Rev-4 to Rev-5

Page- 3 of 3

| SECTION-XI |  |  |  |
| --- | --- | --- | --- |
| 1 | Jumper pad bolting arrangement has been standardized and drawing enclosed in specification. | Drawing enclosed. | Sec-XI |
| 2 | Drawing of Pipe type earthing has been modified wherein it has been indicated that length of flat is indicative only and actual length shall vary depending on site requirement (to avoid fouling of pipe type earthing with the foundation base slab | Drawing enclosed. | Sec-XI |
| 3 | Aluminium Bond drawing enclosed in specification | Drawing enclosed. | Sec-XI |
| 4 | Typical Layout of Store enclosed in specification | Drawing enclosed. | Sec-XI |
| 5 | Rod type Earthing arrangement has been standardized and drawing enclosed in specification. | Drawing enclosed. | Sec-XI |
| 6 | Weight of Step Bolt revised and drawing enclosed in specification. | Drawing enclosed. | Sec-XI |
| 7 | Bird Guard for I string revised and drawing enclosed in specification. | Drawing enclosed. | Sec-XI |

|  | TECHNICAL SPECIFICATION (VOLUME-II) |  |
| --- | --- | --- |
|  | CONTENTS |  |
| SECTION-I | GENERAL INFORMATION & SCOPE |  |
| SECTION-II | GENERAL TECHNICAL CONDITIONS |  |
| SECTION-III | SURVEY AND SOIL INVESTIGATION |  |
| SECTION-IV | TOWER, FOUNDATION, ERECTION, STRINGING AND COMMISSIONING OF LINE |  |
| SECTION-V | GALVANISED STEEL EARTHWIRE |  |
| SECTION-VI | HARDWARE FITTINGS & ACCESSORIES |  |
| SECTION-VII* | CONDUCTOR |  |
| SECTION-VIII* | INSULATOR |  |
| SECTION-IX* | PILE FOUNDATION |  |
| SECTION-X* SECTION-X-A* | OPGW OPGW GUIDELINES FOR OFFLINE INSTALLATION & SPLICING |  |
| SECTION-XI* | DRAWINGS |  |

SECTION-I

|  | SECTION-I |  |
| --- | --- | --- |
|  | CONTENTS |  |
| Clause | Description | Page No. |
| 1.0 | General Information and Scope | 1 |
| 2.0 | Qualification Requirement for Contractor's Supplied Line Materials | 7 |
| 3.0 | Transmission towers & line data | 18 |
| 4.0 | Details of line materials | 24 |
| 5.0 | Service Conditions | 29 |

SECTION-I

TECHNICAL SPECIFICATIONS

- General Information and Scope

  - Scope

    - The following transmission lines are included in the scope of the contractor under various packages:

Tower package TW27

Line name M/C portion of following transmission line 6 Kms (approx.).

(i) 132kV S/C on D/C Naharlagun – Sagali T/L.

(ii) 132kV S/C on D/C Naharlagun – Banderdewa T/L.  and

(iii) 132kV S/C on D/C Naharlagun – Gerukamukh T/L–

    - This  Specification covers the following scope of works:

          - Detailed survey including route alignment, profiling, tower spotting, optimization of tower locations, soil resistivity measurement & geotechnical investigation (including special foundation locations viz. pile/well foundation locations, whenever applicable & covered under BPS);

          - Check survey;

          - Fabrication and supply of all type of transmission line towers, including River crossing towers (wherever applicable) as per Employer’s design/drawings including fasteners, step bolts, hangers, D-shackles etc. ;

          - Supply of all types of tower accessories like phase plate, circuit plate (where ever applicable), number plate, danger plate, anti-climbing device, Bird guard(where ever applicable);

          - Supply of

- Earth wire, Hardware Fittings and Conductor. & Earth wire Accessories

- Conductor, Insulators

- OPGW & associated fittings & accessories.

          - Classification of foundations for different type of tower and casting of foundations for tower footings as per Employer’s foundations drawing;

          - Supply & Installation of Tower Earthing.

          - Supply & installation of Insulated Conductor sleeve, (if required & covered under BPS);

          - For transmission lines, to promote mechanization and safe working conditions, use of crane is being promoted.  Erection of towers, tack welding of bolts and nuts including supply and application of zinc rich paint, fixing of insulator strings, stringing of conductors and earth wires/OPGW/ADSS along with all necessary line accessories by using crane(wherever feasible). However, where usage of crane is not possible, erection of towers has to be carried out   by conventional method i.e using Gin pole, Derrick, Centre mast etc. through usage of Power Operated Winch Machines. No tractor shall be allowed for tower erection.;

          - De-stringing & dismantling of existing 765/400/220/132/66kV Transmission line. (whenever applicable & covered under BPS)

          - Stringing of Power line crossing section under Live Line Condition (where ever applicable & covered under BPS);

          - Painting of towers &supply and erection of span markers, obstruction lights (wherever applicable) for aviation requirements (as required)

          - Testing and commissioning of the erected transmission lines and

          - Other items not specifically mentioned in this Specification and/or BPS but are required for the successful commissioning of the transmission line, unless specifically excluded in the Specification.

          - Stringing of spans from common M/C tower to D/C towers of the lines mentioned at Cl.1.1.1 and from M/C towers to Naharlagun SS gantries/DE tower.

          - OPGW on existing …………………………. line shall be installed under live line conditions, i.e. with all the circuits of the transmission line charged to their rated voltage. The tentative bill of quantities for live-line OPGW cable system installations have been specified.

The OPGW cable shall be installed at the top of the tower by replacing the existing ground wire. The Contractor shall carry out re-tensioning of the existing earth wire wherever required to maintain the adequate clearances for live line stringing of fibre optic cables.

(This clause will be inserted if OPGW installation on existing line is covered under the scope of work)

      - Employer shall provide structural drawings, shop drawings & Bill of Materials of all type of standard transmission line towers and their extensions, river crossing towers/ special towers as required to the Contractor after placement of award, in sequence, suiting the project requirement. The drawings for all type of foundations for the towers shall also be provided by Employer to the Contractor.

However, if the contractor has already executed/is executing any other POWERGRID project involving same type & design of towers as required under the present package, POWERGRID shall not provide the drawings, BOM and Shop sketches again and confirmation regarding the applicability of the same for present package shall be given.

During execution of the project, if any specific designs viz. +18/+25/+30M extensions, other equal/unequal leg extensions, cross-arm strengthening, auxiliary cross-arms, raised chimney foundations etc. are required as per site conditions, Single Line Diagram/Design Drawing shall be provided by the Employer. The contractor shall be required to develop the corresponding structural drgs, BOM & Shop drawings etc. without any financial implication to Employer.

1.1.2.2	(a) 	The provisional quantities of fabricated &galvanized steel  parts required for towers, concrete, excavation volume & reinforcement steel for foundation and other items are given in appropriate Schedule of Bid Proposal Sheet (BPS) for respective packages.  However, the 	work shall be executed as per approved construction drawings.

- The various items of work are described very briefly in the appropriate Schedule of BPS.  The various items of the BPS shall be read in conjunction with the corresponding sections in the Technical Specifications including amendments and, additions, if any. The Bidder’s quoted rates shall be based on the description of activities in the BPS as well as other necessary operations required to complete the works detailed in these Technical Specifications.

(c) 	The Unit rates quoted shall include minor details which are obviously and fairly intended, and which may not have been included in these documents but are essential for the satisfactory completion of the various works.

(d) 	The unit rate quoted shall be inclusive of all plant equipment, men, material skilled and unskilled labour etc. essential for satisfactory completion of various works.

(e)	All measurements for payment shall be in S.I. units, lengths shall be measured in meters corrected to two decimal places.  Areas shall be computed in square meters & volume in cubic meters, rounded off to two decimals.

1.1.2.3	The Bidder shall submit his offer taking into consideration that the tower and foundation designs/drawings shall be developed/provided by Employer and design rights will be strictly reserved with Employer.  Bidder shall quote the unit rates for various items of towers and foundations as per units mentioned in appropriate schedule of (BPS). However, payment of these items identified in the schedule of prices shall be made as follows:

# TOWER

Supply items              : On supply of respective complete tower

### Erection items            : On erection of respective complete tower

Foundation items : On completion of respective foundation in all respect

Towers to be supplied by the contractors/Tower Manufacturers shall be dispatched Panel wise as per mutually agreed procedure with Employer Quality Assurance & Inspection Department.

The payment to be made for towers/foundations shall be worked out based on the unit rates and approved Bill of Materials (BOM) for towers and quantities/volumes as per approved tower foundation drawings.

    - This specification also includes the supply of the following items, as detailed in the specification.

        - Earth wire & hardware fittings and all type of accessories for conductor and earth wire.

        - Insulator & Conductor

        - OPGW & associated fittings and accessories

Contractor shall clearly indicate in their offer, the sources from where they propose to procure these materials in appropriate Schedule of BPS. The technical descriptions of these items are given in relevant sections of this Volume

    - The Contractor shall take delivery of the Employer’s supplied materials at the stores established by the contractor in consultation with the Employer and ensure their safe custody and shall install the same in the transmission lines as stipulated in this specification.

    - In case, part quantity of Tower/Tower Parts are supplied by the Employer or other Supplier, the contractor shall take delivery, carry out (unloading & stacking), ensure safe custody of materials at their stores including insurance cover as required &install the same in the transmission lines as stipulated in this specification.

    - The installation/stringing of OPGW cable & ADSS Cable along with associated fittings & accessories shall be carried out by the contractor. The scope of installation/stringing of OPGW & ADSS shall include splicing, termination, testing, demonstration for acceptance & commissioning as well as documentation. Splicing is preferred to be carried out at Tension tower locations. However, it shall be permitted at Suspension Tower locations also as required due to site conditions. The installation/stringing and splicing shall be carried out as per owner guidelines (provided as part of TS). The FODP & Approach cable shall also be installed by the Contractor.

(Clause no. 1.1.6 to be inserted whenever OPGW, ADSS, Approach Cable & FODP etc. is to be used in the project whether supplied by owner or contractor.)

    - All the raw materials such as steel, zinc for galvanizing, reinforcement steel and cement for tower foundation, coke and salt for tower earthing etc. bolts, nuts, washers, step bolts, D-shackles, hangers, links, danger plates, phase plates , number plates, Circuit Plates, aviation signals etc., required for tower manufacture and erection shall be included in the Contractor’s scope of supply. Bidder shall indicate in the offer, the sources from where they propose to procure the raw materials and the components.

    - Stringing

a) 	For Earthwire:

The entire stringing work of earth wire shall be carried out by standard stringing practice

b) 	For OPGW:

The entire stringing work of OPGW shall be carried out by power operated winch machines. No tractor shall be allowed for stringing of OPGW.

b-1)     For ADSS :

The stringing of ADSS Cable alongwith associated accessories and joint box shall be as per field proven practices, and relevant standards of ADSS Cable. The maximum allowable stringing tension, maximum allowable torsional shear stress, crush strength and other physical parameters of cable shall not be exceeded during installation.

*c) 	For transmission line with Single Conductor per phase:

The entire stringing work of conductor shall be carried out by standard stringing practice.  No tractor shall be allowed for final sagging. The Contractor shall use power operated winch machines only

*d)	For transmission line with Bundle Conductor per phase:

The entire stringing work of conductor shall be carried out by tension stringing technique.  The bidder shall indicate in their offer, the sets of tension stringing equipment in their possession and the sets of stringing equipment he would deploy exclusively for each package. However, it should not be less than the number and capacity requirement indicated in Qualifying Requirements for Bidder.  The period of deployment of tension stringing equipment shall be as per actual site requirement. No tractor shall be allowed for final sagging.

To promote mechanization, for better safe working condition at site the contractor shall mandatorily provide at site for each package (i) requisite numbers (minimum 2 nos per TSE as specified in qualification requirement) of sagging bridges/working platform with pull lifts for facilitating sagging & dead end jointing (ii) requisite numbers (minimum six nos for each package) of power operated hydraulic/motorized winch machines for tower erection & carrying out final sagging (iii) requisite numbers (minimum four) ladders with suitable hooks and attachment arrangement to facilitate worker movement on insulators strings and (iv) adequate number of walkie- talkies. In case more number of sagging bridges/working platform, power operated winch machines etc. are required for stringing of transmission line in accordance with time schedule, the same shall be provided by the Contractor. Further, use of tractor for   final sagging shall not be permitted. The Contractor shall use power operated hydraulic/motorized winch machines only.

Power line crossing, river crossings, railway crossings, other single span sections where deployment of tension stringing machine is not warranted and in hilly terrain, thick forest or areas with site constraints, where deployment of tension stringing machine is not feasible , manual stringing may be adopted after getting approval of EMPLOYER’s site Engineer. The contractor shall deploy appropriate tools / equipments / machinery to ensure that the stringing operation is carried out without causing damage to conductor/earth wire/OPGW which are installed at the prescribed sag-tension as per the approved stringing charts.

However, the Bidder having requisite experience may use helicopter for stringing. The Bidder intending to use helicopter shall furnish detailed description of the procedure, type & number of helicopter & accessories etc., to be deployed for stringing operation.

The contractor may also deploy drones for stringing of pilot wires/ropes for pilot wire, keeping in view site condition & feasibility.

Helicopters/Drones may be used in stringing process, particularly in difficult and inaccessible terrain, subject to the required clearance from Director General of Civil Aviation (DGCA) / any other competent authority.

The payment for stringing shall be done as per the unit rates of stringing under the contract irrespective of the methodology adopted for stringing.

    - *The casting of special pile/well foundations, wherever required shall be in the scope of the Bidder. The design shall be provided by POWERGRID. If the bidder does not have necessary experience and is not meeting the qualifying requirements, some other agencies meeting the qualifying requirements may be engaged by the bidder for the casting of pile/well foundations.

or

*In case of special type pile or well foundations, some other contractor may be engaged by the Employer for casting of foundations. However, the Bidder shall be responsible for all the necessary co-ordination with the special foundation Contractor including stub-setting/fixing of base plate with anchor bolt.

  - Details of Transmission Line Routes and Terrain

The detailed survey shall be carried out using Total stations along the approved route alignment. As an alternative, the contractor may also use ALTM (Airborne Laser Terrain Modeling) techniques of equal or better accuracy for the detailed survey.

Quantity of detailed survey including route alignment, profiling, tower spotting, optimization of tower locations, soil resistivity measurement & geotechnical investigation etc. of lines have been indicated in the BPS.

    - Bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines. For this purpose they are requested to contact the following address:

POWERGRID CORPORATION OF INDIA LTD.

CPIU OFFICE – GUWAHATI

6TH FLOOR, MONAL TOWER, OPP. ASSAM SECRETERIATE,

NERA SBI BRANCH, GUWAHATI 781006

  - Location Details and Terminal Points –

    - The transmission line shall emanate from common point of  transmission lines mentioned at 1.1.1 at Naharlagun in the State of Arunachal Pradesh and terminate at gantries of Naharlagun substation in the State of Arunachal Pradesh

The transmission line are passing through Plain*/Hilly*/Snow Zone* area.

    - The Contractor shall have to construct these transmission lines completely from M/C common towers to dead end tower at Naharlagun end. Stringing shall also be carried out from D/C towers of the lines mentioned at Cl.1.1.1 up to DE towers/Gantries of Naharlagun substation.

  - Access to the Line and Right of Way

Right of way and way leave clearance shall be arranged by the Employer in accordance with work schedules. Employer will secure way leave and Right of way in the Forest area.

  - Contractor Execution Plan

After award of the contract, the contractor shall submit a detailed plan for resources mobilization & execution of various activities under the project scope along with the L2 network (L2 network to be approved by CMG) to Site, CMG & Engg .The detail should also cover the locations and size of stores to be established by the contractor.

- Qualification Requirement for Contractor’s Supplied Line Materials.

The Bidder should have assured access to supply the Conductor, Insulator, Earth wire*, Hardware fittings and Conductor & Earth wire accessories and OPGW from Qualified Manufacturers meeting the following minimum requirements and must demonstrate that based on known commitments they will be available for use in the proposed contract.

All materials shall be procured from the POWERGRID approved firms which meet the respective qualifying requirements stipulated below. The contractor shall finalize their sub-vendors/manufacturers for supply of various line materials from amongst qualified firms within one month from date of NOA and submit the details in support of their meeting the stipulated qualification requirements.

In case Contractor proposes to supply the line material(s) from a sub-vendor/manufacturer which is not already approved by POWERGRID, the same may be considered subject to following :-

- The proposal shall be given by Contractor along with complete details in support of suppliers’ meeting the stipulated qualification requirements including details of past supplies, test certificates, performance certificates etc.

- POWERGRID may carryout assessment of the works of the proposed suppliers, if required.

- The final approval of the supplier shall be subject to verification of QR data and assessment of the supplier to the satisfaction of POWERGRID.

The review/verification of QR data by POWERGRID/assessment of supplier’s works/approval of the proposed supplier shall not in any way limit Contractor’s responsibility or dilute their obligation of timely completion of supplies/works. Any delays, what-so-ever, shall be entirely to contractor’s account.

- Wherever the qualification requirement mentioned below stipulate requirement of providing additional warranty, the requisite CPG shall be submitted to POWERGRID regional HQ with intimation to Engg department for subsequent review & approval of sub vendor drawings/documents

  - Earthwire*(applicable in case supply of Earthwire is included in the scope)

The qualified manufacturer should have manufactured, tested and supplied at least three hundred (300) kms. Of galvanized steel ground wire/ ACSR core wire of size 7/3.15mm or above.

  - OPGW*(applicable in case supply of OPGW is included in the scope)

    - For Manufacturer of OPGW

(a)     The OPGW manufacturer should be a manufacturer who has been manufacturing OPGW for the last   three (03) years and at least 100 Kms of OPGW manufactured by such manufacturer should have been in satisfactory operation# on 66 KV or above transmission line(s) for at least two (02) years as on the date of award of Contract (NOA).

In addition to this, if OPGW manufacturer is foreign entity then he should have manufactured & supplied at least 100Kms of OPGW to any country other than the home country and same should be in satisfactory operation# on 66kV or above transmission lines as on date of award of Contract (NOA)

- In case of Foreign OPGW manufacturer, its Subsidiary or Group Company or a JVC shall have manufacturing facilities of OPGW cable in India or Foreign OPGW manufacturer shall incorporate within six months of NOA a Subsidiary or Group Company or a JVC as per companies Act of India to manufacture OPGW cable in India

ii) 	Foreign OPGW manufacturer would supply at least 25% of OPGW cable manufactured in said facilities in India for which bidders should furnish an undertaking (as per enclosed format in……. of bidding documents) during detailed engineering.

iii) 	The Foreign OPGW manufacturer can supply more than 25% quantity of OPGW cable from Indian works provided he should have manufactured and supplied OPGW cable  for 66kV or above voltage line from said Indian works.

OR

(b)  The OPGW manufacturer should be a manufacturer who must have established manufacturing and routine test facility for OPGW in India and at least 100 Km of OPGW manufactured by such manufacturer  should have been installed on 66 kV or above Transmission line(s) as on the date of bid opening mentioned above. Further, the bidder shall submit, along with its bid, a legally enforceable undertaking for extended warranty of two (2) years over and above the warranty period specified for OPGW Cable during detailed engineering.

OR

(c) 	The OPGW manufacturer should be a manufacturer who must have established manufacturing and routine test facility for OPGW in India based on technological support of a parent company (principal) or collaborator and has commenced manufacturing. The parent company (principal) or collaborator should meet the criteria of  clause 2.2.1 (a) above and bidder furnishes along with its bid  a legally enforceable joint deed of undertaking   along with the collaborator / principal for  extended warranty obligations of additional two (2) years over and above the warranty period specified for the OPGW and a confirmation letter from the parent company or the collaborator  furnish performance guarantee for an amount of 10% of the cost of OPGW cable during detailed engineering.

In case OPGW manufacturer is a holding company, the technical experience referred to in clause 2.2.1 above shall be of that holding company only (i.e. excluding its subsidiary / group companies). In case OPGW manufacturer is a subsidiary of a holding company, the technical experience referred to in clause 2.2.1 above shall be of that subsidiary company only (i.e. excluding its holding company).

Note#   :  Satisfactory operation means certificate issued by the employer certifying the operation without any adverse remarks.

    - For Live Line Installation (if applicable)

The agency must have installed at least 50 Kms of OPGW cable in live-line condition on 66 kV or higher voltage transmission line(s) as on date of award of contract (NOA).

(This clause will be inserted if OPGW installation on existing line is covered under the scope of work)

  - Composite Insulators*(for 132/220/400/765kV transmission line) (applicable in case supply of Composite Insulators is included in the scope)

The Qualified Manufacturer shall be a manufacturer of Composite Insulators. The Qualified Manufacturer’s experience should include the following:

2.3.1   	The Qualified Manufacturer should have designed, manufactured, tested and supplied minimum 2000 nos. of 90KN or above rating Composite long rod insulators for 110kV or above transmission lines and the same should have been in satisfactory operation$ for a minimum period of two years as on date of NOA.

2.3.2  The Qualified manufacturer should also have successfully completed at least the following tests on insulator units and insulator strings (of Composite long rod insulators) as on date of NOA.

- Tests on individual units of 90 KN or above rating as per IEC 61109-1995 or IEC 61109-2008.

- Following Type tests on insulator strings assembly for 110kV or above transmission lines with 90KN or above electromechanical strength insulators:

- Power Frequency Voltage withstand test (Wet).

- Switching Surge Voltage Withstand test (Wet).

- Lightning Impulse Voltage Withstand test (Dry).

- Radio Interference Voltage Test (Dry).

- Accelerated ageing test of 5000hrs as described in  appendix-C of IEC 61109 or Test at Multiple stresses of 5000 hrs as described in Annex-B of  IEC- 62217

2.3.3    In case of foreign manufacturer, he should have manufactured and supplied at least 1000 nos of *120/160/210kN (*:as per higher kN rating of insulators covered under the package. For 400kV, 160kN to be stipulated for 210kN insulator {to be deleted}) or above electromechanical strength of composite long rod insulators for 345 kV or above voltage in not more than two contracts to any other country other than the home country of the manufacturer and the same should have been in operation as on date of NOA. (Applicable for 400kV & above voltage level only, to be deleted for other voltage levels)

2.3.4  In case of indigenous manufacturer not meeting the requirement stipulated in cl. 2.3.1 above, can also participate provided he meets the following requirements:-

          - The Qualified Indigenous Manufacturer should have designed, manufactured, tested and supplied minimum 150 nos. of 90KN  or above rating Composite long rod insulator for 110kV or above transmission lines / sub-stations and the same should have been in satisfactory operation$ for a minimum period of two years as on date of NOA.

          - The Qualified manufacturer shall meet the testing requirements as stipulated at Clause 2.3.2 above.

          - If the Qualified manufacturer is not meeting the stipulated two years operational experience requirements specified at 2.3.4.(i) above, the manufacturer shall furnish extended warranty^^ of additional two years over and above the warranty period specified under the package. (This Clause (iii) to be inserted for composite longrod insulator upto 400kV voltage level.)

$ Satisfactory operation under above clauses means certificate issued by the Employer certifying the operation without adverse remark.

2.3.5	The proposed manufacturer can also be a qualified licensee of a qualified manufacturer meeting the above specified requirements at 2.3.1 & 2.3.2 and also meeting the conditions stipulated at 2.7.

  - Conductor (applicable in case supply of Conductor is included in the scope)

The Qualified Manufacturer shall be a manufacturer of Conductor. The qualified manufacturer experience should include the following:

The qualified manufacturer should have manufactured, tested and supplied at least One Thousand (1000)km thirty seven (37) or above strand ACSR/AAAC conductor during last seven (7) years as on date of NOA.

2.4.1	The proposed manufacturer can also be a qualified licensee of a qualified manufacturer meeting the above specified requirements at 2.4 and also meeting the conditions stipulated at 2.7.

  - Hardware Fittings

The qualified manufacturer shall be a manufacturer of hardware fittings of similar nature. The qualified manufacturer’s experience should include the following:

Applicable for 220kV/400kV/765kV Lines**

(i)	The qualified manufacturer should have designed, manufactured, tested and supplied hardware fittings for at least 600 sets of tension strings and 1200 sets of suspension strings for @220kV/345kV/765kV (@ as per applicable voltage{to be deleted}) or above voltage transmission line and the same should have been in satisfactory operation$ for a minimum period of two (2) years as on date of NOA ;

OR

(ii)	(a) Alternatively, the qualified manufacturer should have designed, manufactured, tested and supplied hardware fittings for at least 600 sets of tension strings and 1200 sets of suspension strings for #110kV/220kV/345kV (# one voltage level below the applicable voltage level{to be deleted}) or above voltage transmission line and the same should have been in satisfactory operation$ for a minimum period of two (2) years as on as on date of NOA; and

(b)  The qualified manufacturer should also have successfully completed at least the following type tests on tension & suspension strings for @220kV/345kV/765kV (@ as per applicable voltage{to be deleted}) or above application as on date of NOA:

Power Frequency Voltage withstand test   (Wet)

Switching Surge Voltage Withstand test    (Wet)***

Lightning Impulse Voltage Withstand test (Dry)

Corona & Radio Interference Voltage Test (Dry)***

(iii)	In case of indigenous manufacturers, if the Qualified manufacturer is not meeting the stipulated two years operational experience requirements specified at (i) & (ii) (a) above, the contractor shall furnish extended warranty^^ of additional two years over and above the warranty period specified under the package.

(*** Not applicable for220kV, strike out if not applicable)

Applicable for 132kV Lines**

(i)	The qualified manufacturer should have designed, manufactured, tested and supplied hardware fittings for at least 600 sets of tension strings and 1200 sets of suspension strings for 110kV or above voltage transmission line and the same should have been in satisfactory operation$ for a minimum period of two (2) years as on date of NOA ;

(ii)	In case of indigenous manufacturers, if the Qualified manufacturer is not meeting the stipulated two years operational experience requirements specified at (i) above, the contractor shall furnish extended warranty^^ of additional two years over and above the warranty period specified under the package.

Note: ^^ Additional  extended warranty in terms of 10% CPG corresponding to cost of the item(s).

2.5.1	The proposed manufacturer can also be a qualified licensee of a qualified manufacturer meeting the above specified requirements at 2.5 (i) or (ii) and also meeting the conditions stipulated at 2.7.

  - Accessories for Conductor and Earth wire

2.6 (i). The qualified manufacturer shall be a manufacturer of accessories for conductor & earthwire of similar nature. The qualified manufacturer experience should include the following:

Applicable for 132kV Lines**

The qualified manufacturer should have designed, manufactured, tested and supplied the item(s) of accessories for conductor & earth wire covered under the package or item(s) of similar/comparable nature. For Vibration dampers, the experience should include at least the supply of 5,850 nos. of vibration dampers for conductor and 1,950 nos. of vibration dampers for earthwire for 132kV or above voltage transmission line and the same should have been in satisfactory operation$ for a minimum period of two (2) years as on date of NOA. (For accessories for galvanized steel Earthwire, the requirement of voltage level shall not be applicable).

Applicable for 220kV Single/Twin bundle conductor  Lines**

The qualified manufacturer should have designed, manufactured, tested and supplied the item(s) of accessories for conductor & earth wire covered under the package or item(s) of similar/comparable nature. For Bundle Spacer and (@ In case of Single Conductor {to be deleted}) Vibration dampers, the experience should include at least the supply of 7,875 nos. of twin bundle spacers and(@ In case of Single Conductor {to be deleted}) 5,850 nos. of vibration dampers for conductor and 1,950 nos. of vibration dampers for earthwire for 220kV or above voltage transmission line and the same should have been in satisfactory operation$ for a minimum period of two (2) years as on date of NOA. (For accessories for galvanized steel Earthwire, the requirement of voltage level shall not be applicable).

Applicable for 400kV Twin bundle conductor  Lines**

The qualified manufacturer should have designed, manufactured, tested and supplied the item(s) of accessories for conductor & earth wire covered under the package or item(s) of similar/comparable nature. For Bundle Spacer and Vibration dampers, the experience should include at least the supply of 7,875 nos. of twin bundle spacers and 5,850 nos. of vibration dampers for conductor and 1,950 nos. of vibration dampers for earthwire for 220kV or above voltage transmission line and the same should have been in satisfactory operation$ for a minimum period of two (2) years as on date of NOA. (For accessories for galvanized steel Earthwire, the requirement of voltage level shall not be applicable).

Applicable for 400kV Quad/Triple bundle conductor  Lines **

The qualified manufacturer should have designed, manufactured, tested and supplied the item(s) of accessories for conductor & earth wire covered under the package or item(s) of similar/comparable nature. For spacer dampers for Quad/Triple bundle conductor and vibration dampers for earth wire, the experience should include at least the supply of 6900 nos. of quad spacer dampers and 1950 nos. of vibration dampers for earth wire for 345kV or above transmission line and the same should have been in satisfactory operation$ for a minimum period of two (2) years as on date of NOA. (For accessories for galvanized steel Earthwire, the requirement of voltage level shall not be applicable).

Applicable for 765kV Lines **

The qualified manufacturer should have designed, manufactured, tested and supplied the   item(s) of accessories for conductor & earth wire covered under the package or item(s) of similar/comparable nature.  For spacer dampers for Hexa/Quad bundle conductor and vibration dampers for earth wire, the experience should include at least the supply of 6900 nos. of quad spacer dampers and 2300 nos. of vibration dampers for earth wire for 345kV or above transmission line and the same should have been in satisfactory operation$ for a minimum period of two (2) years as on date of NOA. (For accessories for galvanized steel Earthwire, the requirement of voltage level shall not be applicable).

2.6 (ii). In case of indigenous manufacturers, if the Qualified manufacturer is not meeting the stipulated two years operational experience requirements specified at (i) above, the contractor shall furnish extended warranty# of additional two years over and above the warranty^^ period specified under the package.

Note: ^^ Additional  extended warranty in terms of 10% CPG corresponding to cost of the item(s).

    - The proposed manufacturer can also be a qualified licensee of a qualified manufacturer meeting the above specified requirements at 2.6 (i) and also meeting the conditions stipulated at 2.7.

    - The manufacturer(s) meeting the above requirement for any individual item or items shall be considered qualified for the respective item or items only.

  - Licensor-Licensee conditions:

(i)	Manufacturer/licensees shall have adequate design infrastructure and manufacturing facility and capacity and procedures including quality control.

(ii)  A qualified Licensee of a qualified manufacturer shall comply with all of the following requirements and furnish a joint undertaking by the licensor along with the bid.

- Any design undertaken by the licensee shall be approved by the licensor.

- Manufacture by the licensee shall be done with the approval of the licensor and Employer under a quality assurance programme approved and monitored by the licensor.

- Licensee must furnish back-up guarantee from the licensor for individual and overall performance of all   materials supplied under the contract.

- Licensor must guarantee sequential and timely supply of   materials and submission of technical information and data as desired by the Employer so as to meet the overall construction schedule and

- The agreement between licensee and licensor (copy to be submitted along with the undertaking as per, Proforma enclosed as Annexure –A to this section) shall be valid for a period of at least five (5) years after the guarantee period of equipment and materials under supply is over.

  - Qualification for Pile foundation*

    - Qualifying Requirements

The bidder shall have experience of its own or should engage the services of an agency (ies) meeting the following experience, for carrying out pile foundations covered under the scope of the work of the package. The details in support of the contractor/agencies meeting the stipulated requirement shall be submitted by the Contractor within one month of NOA, to Site-Incharge for approval:-

2.8.1.1	Technical   Experience

The bidder/agency shall have successfully completed@ execution of pile foundation project (s) within last seven years as on date of NOA. The bidder’s experience should include the following:

- The bidder/agency should have installed cast-in-situ vertical bored pile foundation having #750 mm/1000 mm/1200mm/1500 mm diameter and having minimum depth of 25 meters below ground level.

For Package-A :}#750 mm/1000 mm/1200mm/1500 mm

For Package-B :}#750 mm/1000 mm/1200mm/1500 mm

(# As per applicable diameter of pile covered in the package. In case different diameter piles are involved diameter of pile having maximum quantity in the package to be selected. Strike out other diameter.)

- The monthly average rate of pile boring for best three months achieved by the bidder/agency in any one contract executed during last 5 years as on date of NOA should be at least ##  ___ m for Package-A and ## ____m for Package-B.

- The monthly average rate of Concreting for pile cap, pedestal, tie beams etc. for best three months achieved by the bidder/agency in any one contract executed during last 5 years as on date of NOA should be at least ## _______ cum for Package-A and ## ______ cum for Package-B.

In case bidder is a holding company, the technical experience referred to in clause 2.8.1.1 above shall be of that holding company only (i.e. excluding its subsidiary/group companies). In case bidder is a subsidiary of a holding company, the technical experience referred to in clause 2.8.1.1 above shall be of that subsidiary company only (i.e. excluding its holding companies).

(Below table is for calculation purpose only to be deleted in the final specification)

| Calculation of monthly bore piling rate and concreting rate for pile foundation |  |  |
| --- | --- | --- |
| - Pile boring rate |  |  |
| Tower Pile boring involved in the package (as per NIT BOQ) | : | X M |
| Completion period (as per draft MNW) | : | Y months |
| Pile boring required per month: | : | X/(0.5* Y) m = Z M Rounded off to nearest ten) |
| Monthly average bore piling rate in any contract | : | Same as Pile boring required per month= Z M |
| * For working out pile boring rate per month, it has been assumed that 50 % of the total completion time shall be required for boring |  |  |
| - Concrete Rate |  |  |
| Total Concerting involved for pile cap Pedestal, tie beam etc. (as per NIT BOQ) |  | Q Cu. M |
| Completion period (as per draft MNW) |  | Y months |
| Monthly average concreting rate## |  | A/ (0.5Y-3) Rounded off to nearest ten) |
| ## for working out monthly average concerting rate, it has been assumed that 3 months will be required for mobilization and 50 % of the total completion time shall be required for boring. Thus time left for concrete shall be 0.5 Y-3 months |  |  |

2.8.1.2	Equipment capabilities

The bidder/agency should own or have access to at least 1 (one) no. Hydraulically operated drilling machine capable of boring #750 mm/1000 mm/1200mm/1500 mm diameter and upto 40 m depth below ground level with necessary tools/accessories for boring in all kinds of soil including bed rock.

(# As per applicable diameter of pile covered in the package. In case different diameter piles are involved diameter of pile having maximum quantity in the package to be selected. Strike out other diameter.)

In case bidder is proposing above facilities from other agencies, they shall furnish the details of such agencies along with their consent letters.

Clause No. 2.8 will be applicable whenever Pile Foundation is required in the scope.

$  Satisfactory operation under above clauses 2.2, 2.3, 2.5, 2.6 means certificate issued by the Employer certifying the operation without adverse remark.

@ Successfully completed under clause 2.8 means issue of provisional or final taking over certificate (TOC)by the Employer to the contractor for the referred contract.

- Transmission towers and Line data

  - General Description of the Tower

    - The transmission towers are of self-supporting hot dip galvanized lattice steel type, designed to carry the line conductors with necessary insulators, earth wire*, OPGW(If applicable) and all fittings under all loading conditions.  Outline diagram of towers are enclosed with the Specification.

    - The towers shall have mild steel or/and high tensile steel sections and shall be fully galvanized as specified in relevant clauses in section-IV. Bolts and nuts with spring washer are to be used for connections.

    - The towers are of the following types:

A)	Single Circuit

B) 	Double Circuit

C)	Multi Circuit

D)	Special towers.

  - Classification of Towers

    - The towers for **765/400/220/132 kV Double Circuit Lines are classified as given below:

| Type of Tower | Deviation Limit | Typical Use |
| --- | --- | --- |
| A/DA/QA* | 0 – 2 deg. | To be used as tangent tower. |
| B/DB/QB* | 0 deg. | To be used as Section Tower. |
| B/DB/QB* | 0 - 15 deg. | - Angle towers with tension Insulator string. |
|  |  | - Also to be used for uplift force resulting from an uplift span up to 200m under broken wire conditions. |
|  |  | - Also to be used for Anti Cascading Condition. |
| C/DC/QC* | 0 deg. | To be used as Section Tower. |
| C/DC/QC* | 15 - 30 deg. | - Angle tower with tension insulator string. |
|  |  | - Also to be used for uplift forces resulting from an uplift span up to 200m under broken wire condition. |
|  |  | - Also to be used for anti-cascading condition. |
| D/DD/QD* | 30 - 60 deg. | - Angle tower with tension insulator string. |
|  |  | - Also to be used for uplift forces resulting from an uplift span up to 300m under broken wire condition. |
|  |  | - Dead end with 0 deg to 15 deg deviation both on line side and sub-station side (slack span) |
| D/DD/QD* | 0 deg. | - Complete Dead end |
|  |  | - For river crossing anchoring with longer wind span & 0 deg. deviation on crossing span side and 0 deg to 30 deg. deviation on other side. |

Note:

1.	The above towers can also be used for longer span with smaller angle of 	deviations 	without infringement of ground clearance.

2.  	The above table provides indicative classification of Towers. Tower spotting 	data for various towers to be used in the transmission lines under the specific 	package shall be given to the contractor during execution stage.

    - Transposition tower for Lines

For transposition  of transmission line if required suitable tension type tower with modifications shall be used for transposition of the line maintaining all the required electrical clearances and shielding. Indicative sketches for single and double circuit transposition towers are enclosed in drawing section of this specification.

Two numbers of transposition towers shall be required in a double circuit transmission line and three number of transposition towers shall be required in a single circuit transmission line having horizontal configuration of towers. Location of transposition towers shall be selected by the contractor during detailed survey in consultation with site in charge.

In case of the 765 kV S/C transmission line having delta configuration of towers, no modification in the C type tower is required and transposition shall be carried by using three pairs of C type towers in the line as shown in the sketch enclosed in drawing section of this specification.

Single tension strings, Single suspension pilot strings and T-connectors/PG Clamp as indicated in the sketches shall be used for maintaining the requisite electrical clearances under normal and swing conditions.

    - Special Towers

The towers which will be specially designed for very long spans which cannot be crossed by normal tower with extensions as given in cl.no.3.2.4 like Major River crossings etc. shall be treated as special towers.

    - Extensions

      - The towers are generally designed so as to be suitable for-6.0/-4.5/-3.0/-1.5/±0.0/+1.5/+3.0/+6.0/+7.5/+9.0/+18/+25/+30Mbody truncations/extensions/leg extensions for maintaining adequate ground clearances without reducing the specified factor of safety in any manner.

      - The provision for addition of 18/25/30M body extension to tower types A/DA,B/DB and D/DD(as specified in tower spotting data given to the contractor during execution stage) is also kept. For Power Line Crossing or any other obstacle crossing, tower types A/DA, B/DB or D/DD can be used with 18/25 M extensions depending, upon the merit of the prevailing site condition.  The maximum reduced spans for A/DA,B/DB and D/DD type towers shall be mentioned in the tower spotting data.

      - The towers have been designed for providing unequal leg extensions. The details of unequal leg extensions provided in the design shall be furnished to the contractor during execution stage, so that proper optimization of benching / revetment requirement can be done accordingly by the contractor. The towers are designed for unequal leg extensions of -6.0/-4.5/-3.0/-1.5/±0.0/+1.5/+3.0/+6.0/+7.5/+9.0M generally with 3M maximum leg differential and in specific cases with 6m maximum leg differential. In situations where difference in leg differential does not suit the standard unequal leg extension provisions on the tower mentioned above, suitable chimney extensions can be provided to reduce benching/revetment requirement.

      - All above extension provisions to towers and foundations shall be treated as part of normal towers and foundations only.

      - The leg extensions, unequal leg extensions, chimney extensions and / or a combination of these suitable for a tower location shall be selected on the basis of techno-economic evaluation.

  - Span and clearances

Span and clearances given in following clauses are indicative. Span & Clearances to be adopted for the specific package shall be as per Tower Spotting Data to be given to the contractor during execution stage.

    - Normal Span

The normal ruling span of the line is *400m for 765/400KV/1200KV, *350m for 220KV and *320m for 132KV lines.

    - Wind Span

The wind span is the sum of the two half spans adjacent to the support under consideration. For normal horizontal spans this equals to normal ruling span.

    - Weight span

The weight span is the horizontal distance between the null points of the conductors on the two spans adjacent to the tower. For spotting of structures, the span limits are given in following table:

| (FOR 765 KV LINE)** |  |  |  |  |
| --- | --- | --- | --- | --- |
| TOWER TYPE | NORMAL CONDITION |  | BROKEN WIRE CONDITION |  |
|  | MAX. (m) | MIN. (m) | MAX. (m) | MIN. (m) |
| DA | 600 | 200 | 360 | 100 |
| DB | 600 | 0 | 360 | -200 |
| DC | 600 | 0 | 360 | -200 |
| DD | 600 | 0 | 360 | -300 |

| (FOR 400 KV LINE) |  |  |  |  |
| --- | --- | --- | --- | --- |
| TOWER TYPE | NORMAL CONDITION |  | BROKEN WIRE CONDITION |  |
|  | MAX. (m) | MIN. (m) | MAX. (m) | MIN. (m) |
| DA | 600 | 200 | 360 | 100 |
| DB | 600 | 0 | 360 | -200 |
| DC | 600 | 0 | 360 | -200 |
| DD | 600 | 0 | 360 | -300 |

| (FOR 220 KV LINE) |  |  |  |  |
| --- | --- | --- | --- | --- |
| TOWER TYPE | NORMAL CONDITION |  | BROKEN WIRE CONDITION |  |
|  | MAX. (m) | MIN. (m) | MAX. (m) | MIN. (m) |
| DA | 525 | 200 | 315 | 100 |
| DB | 525 | 0 | 315 | -200 |
| DC | 525 | 0 | 315 | -200 |
| DD | 525 | 0 | 315 | -200 |
| (FOR 132 KV LINE) |  |  |  |  |
| TOWER TYPE | NORMAL CONDITION |  | BROKEN WIRE CONDITION |  |
|  | MAX. (m) | MIN. (m) | MAX. (m) | MIN. (m) |
| DA | 500 | 270 | 300 | 100 |
| DB | 515 | 0 | 310 | -200 |
| DC | 515 | 0 | 310 | -200 |
| DD | 515 | 0 | 310 | -300 |

    - In case at certain locations, actual spans are found to be exceeding the design spans and cross-arms/other members of towers are required to be modified/reinforced, the tower shall be modified/reinforced by the contractor based on drawings supplied to the Contractor.

  - Electrical Clearances

    - Ground Clearance

The minimum ground clearance from the bottom conductor shall not be less than 6100 mm for 132KV lines at the maximum sag conditions i.e at max temperature as indicated in tower spotting data and still air.

a) 	An allowance of 150mm shall be provided to account for errors in stringing.

b) 	Conductor creep shall be compensated by over tensioning the conductor at a temperature as mentioned in cl 3.7 of section IV of this specification.

  - Electrical System Data**

    - 765 kV transmission line

| 1. | Nominal Voltage | kV | 765 |
| --- | --- | --- | --- |
| 2. | Maximum system voltage | kV | 800 |
| 3. | BIL (Impulse) | kV (Peak) | 2400 |
| 4. | Power frequency withstand voltage (Wet) | kV (rms) | 830 |
| 5. | Switching surge withstand voltage (Wet) | kV (peak) | 1550 |
| 6. | Minimum Corona extinction voltage at 50 Hz AC system under dry condition | kV (rms) phase to earth. | 510(Min) |
| 7. | Radio interference voltage at one MHz for phase to earth voltage of 510 kV under dry condition. | Micro Volts | 1000 (Max) |

400 kV transmission line

| 1. | Nominal Voltage | kV | 400 |
| --- | --- | --- | --- |
| 2. | Maximum system voltage | kV | 420 |
| 3. | BIL (Impulse) | kV (Peak) | 1550 |
| 4. | Power frequency withstand voltage (Wet) | kV (rms) | 680 |
| 5. | Switching surge withstand voltage (Wet) | kV (peak) | 1050 |
| 6. | Minimum Corona extinction voltage at 50 Hz AC system under dry condition | kV (rms) phase to earth. | 320 |
| 7. | Radio interference voltage at one MHz for phase to earth voltage of 305 kV under dry condition. | Micro Volts | 1000 (max) |

For 220 KV Transmission Line

| 1. | Nominal Voltage | kV | 220 |
| --- | --- | --- | --- |
| 2. | Maximum system voltage | kV | 245 |
| 3. | BIL (Impulse) | kV (Peak) | 1050 |
| 4. | Power frequency withstand voltage (Wet) | kV (rms) | 460 |
| 5. | Minimum Corona extinction voltage at 50 Hz AC system under dry condition | kV (rms) phase to earth. | 154(Min) |
| 6. | Radio interference voltage at one MHz for phase to earth voltage of 154 kV under dry condition. | Micro Volts | 1000 (Max) |

For 132 KV Transmission Line (for 1000m Alt.)

| 1. | Nominal Voltage | kV | 132 |
| --- | --- | --- | --- |
| 2. | Maximum system voltage | kV | 145 |
| 3. | BIL (Impulse) | kV (Peak) | 650 |
| 4. | Power frequency withstand voltage (Wet) | kV (rms) | 275 |

- Details of line Materials

  - Details of Conductor & Earthwire

For 765 kV Single/Double Circuit transmission line

| Sl. No. | Description | Conductor (Single Ckt.) | Conductor (Double Ckt.) | Earthwire* | OPGW* |
| --- | --- | --- | --- | --- | --- |
| 1. | Type | ACSR ‘BERSIMIS’ conductor | ACSR ‘ZEBRA’ conductor | 7/3.66mm GS Earthwire | Equivalent to 7/3.66mm GS Earthwire |
| 2. | Stranding and wire diameter |  |  |  |  |
|  | Aluminium / Al Alloy | 42/4.57 | 54/3.18 | - |  |
|  | Steel | 7/2.54 | 7/3.18 | 7/3.66 |  |
| 3. | Conductor per phase | 4 | 6 | NA |  |
| 4. | Spacing between conductor of same phase(sub conductor spacing)(mm) | 457 | 457 | NA |  |
| 5. | Overall Diameter (mm) | 35.05 | 28.62 | 10.98 |  |
| 6. | Unit mass (kg/km) | 2181 | 1621 | 583 |  |
| 7. | Min. UTS (kN) | 154 | 130 | 68.4 |  |
| 8. | Configuration | DELTA | Vertical | One/Two* continuously to run horizontally on top of the towers and conductors. | One/Two* continuously to run horizontally on top of the towers and conductors. |

For 400 kV Single/Double Circuit transmission line

| Sl. No. | Description | Conductor | Earthwire* | OPGW* |
| --- | --- | --- | --- | --- |
| 1. | Type | ACSR ‘MOOSE’ conductor | 7/3.66mm GS Earthwire | Equivalent to 7/3.66mm GS Earthwire |
| 2. | Stranding and wire diameter |  |  |  |
|  | Aluminium / Al Alloy | 54/3.53 | - |  |
|  | Steel | 7/3.53 | 7/3.66 |  |
| 3. | Conductor per phase | 4 | NA |  |
| 4. | Spacing between conductor of same phase(sub conductor spacing)(mm) | 457 | NA |  |
| 5. | Overall Diameter (mm) | 31.77 | 10.98 |  |
| 6. | Unit mass (kg/km) | 2004 | 583 |  |
| 7. | Min. UTS (kN) | 161.6 | 68.4 |  |
| 8. | Configuration | Vertical | One/Two* continuously to run horizontally on top of the towers and conductors. | One/Two* continuously to run horizontally on top of the towers and conductors. |

For 220kV Double Circuit transmission lines

| Sl. No. | Description | Conductor | Earth wire | OPGW |
| --- | --- | --- | --- | --- |
| 1. | Type | ACSR ‘ZEBRA’ conductor | 7/3.15 mm GS Earth wire | Equivalent to 7/3.15 mm GS Earth wire |
| 2. | Stranding and wire diameter |  |  |  |
|  | Aluminium / Al Alloy | 54/3.18 | - |  |
|  | Steel | 7/3.18 | 7/3.15 |  |
| 3. | Conductor per phase | 1 | NA |  |
| 4. | Spacing between conductor of same phase(sub conductor spacing)(mm) | NA | NA |  |
| 5. | Overall Diameter (mm) | 28.62 | 9.45 |  |
| 6. | Unit mass (kg/km) | 1621 | 428 |  |
| 7. | Min. UTS (kN) | 130 | 56 |  |
| 8. | Configuration | Vertical | One continuously to run horizontally on top of the towers and conductors. | One continuously to run horizontally on top of the towers and conductors. |

For 132 kV Double Circuit transmission lines

| Sl. No. | Description | Conductor | Earth wire | OPGW |
| --- | --- | --- | --- | --- |
| 1. | Type | ACSR PANTHER | 7/3.15 mm GS Earth wire | Equivalent to 7/3.15 mm GS Earth wire |
| 2. | Stranding and wire diameter |  |  |  |
|  | Aluminium / Al Alloy | 30/3 | - |  |
|  | Steel | 7/3 | 7/3.15 |  |
| 3. | Conductor per phase | 1 | NA |  |
| 4. | Spacing between conductor of same phase(sub conductor spacing)(mm) | NA | NA |  |
| 5. | Overall Diameter (mm) | 21 | 9.45 |  |
| 6. | Unit mass (kg/km) | 974 | 428 |  |
| 7. | Min. UTS (kN) | 89.67 | 56 |  |
| 8. | Configuration | Vertical | One continuously to run horizontally on top of the towers and conductors. | One continuously to run horizontally on top of the towers and conductors. |

Note :a)  Conductor*/OPGW to be supplied by the Employer b)*Steel Earthwire to be supplied by the Contractor.

  - Details of insulator strings with composite long rod insulators.

| S.No | Type of String | *Size of Composite Insulator (Core dia x Nominal length)(mm) |  | Minimum Creepage Distance (mm) per unit |  | No. of individual Units per String (Nos.) | Electro- Mechanical Strength of Insulator Unit (kN) | Mechanical Strength of Insulator String along with Hardware Fittings (kN) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 765kV S/C AC TRANSMISSION LINES WITH QUAD BERSIMIS CONDUCTOR |  |  |  |  |  |  |  |  |
| 1. | Single ‘I’ suspension Pilot | 20 x 2900 | 12400 |  | 1x2 |  | 120 | 120 |
| 2. | Double ‘I’ suspension | 20 x 2900 | 12400 |  | 2x2 |  | 120 | 240 |
| 3. | Single ‘V’ suspension Pilot | 20 x 2900 | 12400 |  | 2x2 |  | 120 | 120 |
| 4. | Single ‘V’ suspension | 24 x 2975 | 12400 |  | 2x2 |  | 210 | 210 |
| 5. | Double ‘V’ suspension | 24 x 2975 | 12400 |  | 2x 2 x 2 |  | 210 | 420 |
| 6. | Quadruple Tension | 24 x 2975 | 12400 |  | 4 x 2 |  | 210 | 840 |

| S.No |  | Type of String |  | *Size of Composite Insulator (Core dia x Nominal length) (mm) |  | Minimum Creepage Distance (mm) per unit |  |  | No. of individual Units per String (Nos.) | Electro- Mechanical Strength of Insulator Unit (kN) | Mechanical Strength of Insulator String along with Hardware Fittings (kN) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| FOR 765 kV D/C AC TRANSMISSION LINES WITH HEX ZEBRA CONDUCTOR |  |  |  |  |  |  |  |  |  |  |
| 1. |  | Double ‘I’ Suspension |  | 24x2975 |  | 12400 | 2x2 |  | 160 | 2x160 |
| 2. |  | Single Suspension ‘Pilot’ |  | 24x2975 |  | 12400 | 1x2 |  | 160 | 160 |
| 3. |  | Quadruple Tension |  | 24x2975 |  | 12400 | 4x2 |  | 210 | 4x210 |
| FOR ±800kV HVDC TRANSMISSION LINES WITH HEX LAPWING CONDUCTOR |  |  |  |  |  |  |  |  |  |  |
| 1. |  | Single ‘Y’ suspension |  | 40 x 4560 |  | 16800 | 2 x 2 (V-portion) & 1 x 2 (II-portion) |  | 420 | 420 along one limb of V-portion and along II portion) |
| 2. |  | Triple Tension String |  | 40 x 4560 |  | 16800 | 3 x 3 |  | 420 | 1260 |

| FOR 400kV AC TRANSMISSION LINES WITH QUAD MOOSE CONDUCTOR |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. |  | Double ‘I’ Suspension | 20x3335 |  |  | 13020 | 2x1 | 120 |  | 2x120 |
| 2. |  | Single Suspension ‘Pilot’ | 20x3335 |  |  | 13020 | 1x1 | 120 |  | 120 |
| 3. |  | Single Tension | 20x3335 |  |  | 13020 | 1x1 | 120 |  | 120 |
| 4. |  | Quadruple Tension | 24x3910 |  |  | 13020 | 4x1 | 160 |  | 4x160 |
| FOR 400kV AC TRANSMISSION LINES WITH TRIPLE SNOWBIRD CONDUCTOR |  |  |  |  |  |  |  |  |  |  |
| 1. |  | Double I suspension | 20x3335 |  | 13020 |  | 2x1 | 120 |  | 2x120 |
| 2. |  | Single I Suspension Pilot | 20x3335 |  | 13020 |  | 1x1 | 120 |  | 120 |
| 3. |  | Single Tension | 20x3335 |  | 13020 |  | 1x1 | 120 |  | 120 |
| 4. |  | Double Tension | 24x3910 |  | 13020 |  | 2 x1 | 210 |  | 2 x210 |
| FOR 400kV AC TRANSMISSION LINES WITH TWIN MOOSE CONDUCTOR |  |  |  |  |  |  |  |  |  |  |
| 1. |  | Single ‘I’ Suspension | 20x3335 |  | 13020 |  | 1x1 | 120 |  | 120 |
| 2. |  | Single Suspension ‘Pilot’ | 20x3335 |  | 13020 |  | 1x1 | 120 |  | 120 |
| 3. |  | Double Tension | 24x3910 |  | 13020 |  | 2x1 | 160 |  | 2x160 |
| FOR 220 kV AC TRANSMISSION LINES |  |  |  |  |  |  |  |  |  |  |  |
| 1. |  | Single I Suspension ‘Pilot’ |  | 20x2030 | 7595 |  |  | 1 x 1 | 70 | 70 |  |
| 2. |  | Single I Suspension |  | 20x2030 | 7595 |  |  | 1 x 1 | 70 | 70 |  |
| 3. |  | Single Tension |  | 20x2175 | 7595 |  |  | 1 x 1 | 120 | 120 |  |
| 4. |  | Double Tension |  | 20x2175 | 7595 |  |  | 2 x 1 | 120 | 2x 120 |  |
| FOR 132 kV AC TRANSMISSION LINES |  |  |  |  |  |  |  |  |  |  |  |
| 1. |  | Single I Suspension |  | 18X1450 | 4495 |  |  | 1 x 1 | 70 | 70 |  |
| 2. |  | Single Tension |  | 18X1595 | 4495 |  |  | 1 x 1 | 90 | 90 |  |
| 3. |  | Double Tension |  | 18X1595 | 4495 |  |  | 2 x 1 | 90 | 2x 90 |  |

Note:	* The core dia of composite insulators mentioned at column No.3 is for indicative purpose. The bidder shall offer composite long rod insulators of suitable core dia not less than the value specified above, to meet specified E&M and torsion strength requirements.

  - Details of insulator strings with standard disc insulators.

| S.No | Type of String | E& M Strength of each disc KN |  | No of Standard Insulator Disc |  | Size of Disc in mm |  | Size and Designation of pin ball shank (mm) | Creepage distance of each disc (mm) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 765kV S/C AC TRANSMISSION LINES WITH QUAD BERSIMIS CONDUCTOR |  |  |  |  |  |  |  |  |  |  |
| 1. | Single ‘I’ suspension Pilot | 120 | 1x40 |  | 255 x 145 |  |  | 20 | 370 |  |
| 2. | Double ‘I’ suspension | 120 | 2x40 |  | 255 x 145 |  |  | 20 | 370 |  |
| 3. | Single ‘V’ suspension Pilot | 120 | 2x40 |  | 255 x 145 |  |  | 20 | 370 |  |
| 4. | Single ‘V’ suspension | 210 | 2x35 |  | 280 x 170 |  |  | 24 | 370 |  |
| 5. | Double ‘V’ suspension | 210 | 2x2x35 |  | 280 x 170 |  |  | 24 | 370 |  |
| 6. | Quadruple Tension, | 210 | 4x35 |  | 280 x 170 |  |  | 24 | 370 |  |
| FOR 765 kV D/C AC TRANSMISSION LINES WITH HEX ZEBRA CONDUCTOR |  |  |  |  |  |  |  |  |  |  |
| 1. | Double ‘I’ Suspension | 160 |  | 2x35 |  | 280 x 170 |  | 20 | 370 |  |
| 2. | Single Suspension ‘Pilot’ | 160 |  | 1x35 |  | 280 x 170 |  | 20 | 370 |  |
| 3. | Quadruple Tension | 210 |  | 4x35 |  | 280 x 170 |  | 24 | 370 |  |
| 4. | Single Tension | 160 |  | 1x35 |  | 280 x 170 |  | 20 | 370 |  |
| FOR 400kV AC TRANSMISSION LINES WITH QUAD MOOSE CONDUCTOR |  |  |  |  |  |  |  |  |  |
| 1. | Double ‘I’ Suspension | 120 |  | 2x23 |  |  | 255-280 x 145 | 20 | 370 |
| 2. | Single Suspension ‘Pilot’ | 120 |  | 1x23 |  |  | 255-280 x 145 | 20 | 370 |
| 3. | Single Tension | 120 |  | 1x24 |  |  | 255-280 x 145 | 20 | 370 |
| 4. | Quadruple Tension | 160 |  | 4x23 |  |  | 280 x 170 | 20 | 370 |
| FOR 400kV AC TRANSMISSION LINES WITH TWIN MOOSE CONDUCTOR |  |  |  |  |  |  |  |  |  |
| 1. | Single ‘I’ Suspension | 120 | 1x23 |  |  |  | 255-280 x 145 | 20 | 370 |
| 2. | Single Suspension ‘Pilot’ | 120 | 1x23 |  |  |  | 255-280 x 145 | 20 | 370 |
| 3. | Single Tension | 120 | 1x23 |  |  |  | 255-280 x 145 | 20 | 370 |
| 4. | Double Tension | 160 | 2x23 |  |  |  | 280 x 170 | 20 | 370 |

Note : a)  Insulator* to be supplied by the Employer

- Service Conditions:

Equipment/material to be supplied against this specification shall be suitable for satisfactory continuous operation under tropical conditions as specified below:

## Maximum ambient temperature (Degree Celsius)	:	**50

## Minimum ambient temperature (Degree Celsius)	:	**0

## Relative humidity (% range)	:	10-100

Wind zone (as per IS: 875)	: 	   5

Maximum wind velocity (m/sec.)		: 	50

Maximum altitude above mean sea level (Meters)	: 	1000

Isoceraunic level (days/years)	: 	50

Moderately hot and humid tropical climate conducive to rust and fungus growth.

** If conditions are different for a project, project specific data is got to be added

ANNEXURE-A

Page 1 of 3

FORM OF JOINT UNDERTAKING BY THE LICENSOR

ALONGWITH THE LICENSEE

On Non-Judicial Stamp Paper of Appropriate Value

THIS DEED OF UNDERTAKING executed this ..................... day of ................ Two Thousand .................... by ................... a Company incorporated under the laws of ........................ and having its Registered Office at ................................ (hereinafter called the "Licensor" which expression shall include its successors, executors and permitted assigns) and .......................... a Company incorporated under the Companies Act, 1956 having its Registered Office at ......................... (hereinafter called the "Licensee" which expression shall include its successors, executors and permitted assigns) in favour of Power Grid Corporation of India Ltd., having its Registered Office at B-9, Qutab Institutional Area, Katwaria Sarai, New Delhi-110016 (hereinafter called the "Employer" which expression shall include its successors, executors and permitted assigns).

WHEREAS the Employer invited Bids as per its Specification No. ....................... for the construction of transmission line which inter alia include design, manufacture, testing, supply on Final Destination delivery at site basis for Composite Insulator*, Conductor*, Hardware Fittings* and Accessories for Conductor & Earthwire* for .................................... Transmission Lines.

AND WHEREAS Clause 2.0 (d) (ii) (e) of Section-I, Vol-II, forming part of the Bidding Document inter alia stipulates that the Licensee along with its Licensor must fulfill the Qualifying Requirements and be jointly and severally bound and responsible for the successful performance of the equipment and shall be fully responsible for the design, manufacture, testing, supply and final destination delivery at site basis in the event the Bid is accepted by the Employer resulting in a "Contract".

AND WHEREAS ................................ a company incorporated Companies Act 1956, having its Registered Office at ..................................... (hereinafter called the "Bidder"/"Contractor" which expression shall include its successors, executors and permitted assigns) the Bidder has submitted its Bid for the Employer for ..................................... Transmission Line having Specification No. ................................... vide Proposal No. ..................... dated ...................... based on the License of the Licensor.

ANNEXURE-A

Page 2 of 3

NOW THEREFORE THIS UNDERTAKING WITNESSETH AS UNDER :

1.0	In consideration of the award of Contract by the Employer to the Bidder (hereinafter referred to as the "Contract") we, the Licensor and the Licensee do hereby declare that we shall be jointly and severally bound unto the Power Grid Corporation of India Ltd. (Employer)/the Bidder for the successful performance of the equipment and shall be fully responsible for the design, manufacture, testing, supply and final destination delivery at site basis and successful performance of equipment in accordance with the Contract specifications.

2.0	Without in any way affecting the generality and total responsibility in terms of this Deed of Undertaking the Licensor in particular hereby agrees to depute their technical experts to the Licensee's works as considered necessary by the Employer, Bidder and the Licensor to ensure proper design, manufacture, Quality Management, testing, supply on final destination delivery at site basis and successful performance of the equipment in accordance with Contract Specifications and if necessary the Licensor shall advise the Licensee suitable modifications of the designs and implement necessary corrective measures to discharge the obligations under the Contract.

3.0	As a security, the Licensor shall apart from the Contractor's performance guarantee, furnish a Performance Security from its Bank in favour of the Employer in a form acceptable to Employer. The value of such guarantee shall be equal to 5% of the Contract Price of equipment/material proposed to be manufactured and supplied by the Licensee under the contract awarded by the Employer to the Contractor and it shall be part of guarantee towards the faithful performance/compliance of this Deed of Undertaking in terms of the Contract. The Guarantee shall be unconditional, irrevocable and valid for the entire period of the contract, namely till the end of the warranty period of ...................... package under the Contract. The Bank Guarantee amount shall be payable to the Employer on demand without any reservation or demur.

4.0	We, the Licensor undertakes to guarantee sequential and timely supply of equipments and materials and submission of technical information and data as designed of the Employer so as to meet the overall construction schedule.

ANNEXURE-A

Page 3 of 3

5.0	We, the Licensor and the Licensee confirm that the License agreement shall be valid for a period of at least five (5) years after the guarantee period of the equipment and materials to be supplied under the Contract is over.

6.0	This Deed of Undertaking shall be constructed and interpreted in accordance with the Laws of India and the courts in Delhi shall have exclusive jurisdiction in all matters arising under the undertaking.

7.0	We the Licensor and the Licensee agree that this undertaking shall be irrevocable and shall form an integral part of the Contract and further agree that this undertaking shall continue to be enforceable till the Employer and the Bidder discharge it. It shall become operative from the effective date of Contract.

IN WITNESS WHEREOF the Licensor and the Licensee have through their authorised Representative executed these presents and affixed Common Seals of their respective Companies, on the day, month and year first above mentioned.

WITNESS	FOR LICENSEE

1.	.................................................	................................................................

(Signatures)	(Signature of Authorised Representative)

................................................	................................................................

(Name in Block Letter)	(Name)

.................................................	Designation ...........................................

(Office Address)	Common Seal of Company

WITNESS	FOR LICENSOR

1.	.................................................	................................................................

(Signatures)	(Signature of Authorised Representative)

................................................	................................................................

(Name in Block Letter)	(Name)

.................................................	Designation ...........................................

(Office Address)	Common Seal of Company

Note :   (i)	This deed of joint undertaking should be attested by Notary Public of the place of the respective executants.

(ii)	To be filled separately for each package.

Annexure-B					OPGW FORMS

FORM OF DEED OF JOINT UNDERTAKING TO BE EXECUTED BY THE BIDDER AND THE PROMOTER OF THE GROUP COMPANY (WHEN THE GROUP COMPANY IS YET TO BE INCORPORATED UNDER INDIAN COMPANIES ACT) OF THE BIDDER FOR SUPPLY AT LEAST 25% OF OPGW MANUFACTURED IN THE SAID FACILITIES IN INDIA  [STIPULATED IN CLAUSE 1.1.1(a) (i) & (ii)  OF QUALIFICATION REQUIREMENT]

(ON NON-JUDICIAL STAMP PAPER OF APPROPRIATE VALUE)

This DEED OF UNDERTAKING executed this ............ day of ................. Two Thousand ............ by M/s................................................................, a Company incorporated under ......................... having its Registered Office at ...................................................... hereinafter called the “Bidder” which expression shall include its  successors, administrators, executors and permitted assigns and M/s. ……………………………………, a Company incorporated under …………………………………….. having its Registered Office at ................................................. hereinafter called the “Promoter” which expression shall include its  successors, administrators, executors and permitted assigns, in favour of …….. (insert names of the Purchaser) …………….., a Company incorporated under the Indian Companies Act of 1956 having its registered office at …………….(insert registered address of the Purchaser)…………… (hereinafter called the “Purchaser” which expression shall include its successors, executors and permitted assigns)

WHEREAS the “Purchaser” invited Bid as per its Specification No. ……………. for the execution of …. (insert name of the package alongwith project name) ………………

AND WHEREAS Clause No. ………….., Section …………, of ………………, Vol.–… forming part of the Bidding Documents inter-alia stipulates that the Bidder must fulfill the Qualifying Requirements for the *…………………………… and be jointly and severally bound and responsible along with the Group Company for the successful performance of the *……………………….. offered in the event the Bid submitted by the Bidder is accepated by the Purchaser resulting in a Contract.

AND WHEREAS the Bidder has submitted its Bid to the Purchaser vide Proposal No. ………..….……. dated ………. based on the association of the Promoter of the Group Company and confirmed that the Group Company shall be incorporated as per Indian Companies Act, within six (06) months from the date of award.

AND WHEREAS the Bidder and the Promoter are required to jointly execute and furnish an irrevocable Deed of Joint Undertaking and be jointly and severally liable to the Purchaser for ensuring manufacturing facilities of OPGW Cablein India (hereinafter called as the “Equipment”) such that the Equipment to be supplied by the Supplier can be repaired and maintained without necessitating it to be taken outside the country and for supply at least 25% of OPGW Cablefrom such works of Group Company to be set up in India.

AND WHEREAS the Bidder has submitted its Bid to the Purchaser based on above stipulation and has agreed to furnish this Deed of Undertaking to be enforceable in the event of the award of the Contract by the Purchaser.

1.0	In consideration of the award of Contract by the Purchaser to the Bidder/Supplier (hereinafter referred to as the “Contract”) we, the Bidder/Supplier and the Promoter do hereby agree and undertake to provide requisite Manufacturing and testing facilities for the Equipment, after sales service and supply of spare parts as per the terms of the Contract.

2.0	Without in any way affecting the generality and total responsibility in terms of this Deed of Undertaking, the Bidder/Supplier hereby agrees to depute their technical experts from time to time to the Group Company Works/ Purchaser’s Project site as mutually considered necessary by the Purchaser, Bidder/Supplier and the Group Company to ensure:

(i)	A valid technology transfer agreement, including license to manufacture and supply from India, between the Bidder / Supplier, the technology provider and the Group Company covering the type, size and rating of the OPGW Cablespecified, valid minimum up to the end of the defect liability period of the contract. The technology transfer agreement necessarily covers transfer of technological know-how for OPGW Cablein the form of complete transfer of design dossier, design software, drawings and documentation, quality system manuals and imparting relevant training by the Bidder / Supplier to the personnel of the Group Company.

(ii)	Design of the Equipments manufactured in India shall be identical to the design of equipments to be manufactured and supplied by the Bidder/Supplier

(iii)	Adequate up gradation of the testing facilities including quality systems at Indian works

(iv)	Training to staff of the Group Company and certification to its trained personnel for carry out each activity

(v)	Involvement and supervision during all phases of manufacturing by expert of Bidder/Supplier for the OPGW Cable

(vi)	MQP of Group Company shall be same as that of Bidder/Supplier

(vii)	Source of raw material / major bought out components shall be same as that of Bidder/Supplier

(viii)	Timely supply on FOR destination delivery at site basis.

(ix)	Supervision of unloading at site, storage, erection, testing & commissioning and successful performance of the equipment in accordance with contract specifications

(x)	If necessary the Bidder/Supplier shall advise the Group Company, suitable modifications of designs and implement necessary corrective measures to discharge the obligations under the Contract.

(xi)	Warranty obligations as per GCC clause 22.1 of the biding documents for the entire quantity to be supplied from the Group Company.

3.0     This Deed of Undertaking shall be construed and interpreted in accordance with the laws of India and the Courts in Delhi shall have exclusive jurisdiction in all matters arising under the Undertaking.

4.0	We, agree that this undertaking shall be irrevocable and shall form an integral part of the Contract.

5.0	We hereby confirm that the above undertaking has also been approved by our Board of Directors and the Resolution passed by our Board(s) is attached with this undertaking.

IN WITNESS WHEREOF the Bidder / Supplier and Promoter of the Group Company have through their Authorised Representatives executed these presents and affixed Common seals of their respective Companies on the day, month and year first above mentioned.

| WITNESS Signature ……………………. Name ……………………….. Office Address ………………. | [For Bidder] (Signature of the authorized representative) Name …………………….. Common Seal of Company …...……………. |
| --- | --- |
| WITNESS Signature ……………………. Name ……………………….. Office Address ………………. | [For Promoter of the Group Company] (Signature of the authorized representative) Name …………………….. Common Seal of Company …...……………. |

Note:

1.	For the purpose of executing the Deed of Undertaking, the non-judicial stamp papers of appropriate value shall be purchased in the name of executant.

2.	The Undertaking shall be signed on all the pages by the authorised representative(s) of the Bidder and Promoter of the Group Company and should invariably be witnessed.

3.	The Resolution of the Board of Directors of the Bidder and Promoter of the Group Company, as per the format, shall be attached with this Undertaking.

4.	This Deed of Undertaking duly attested by Notary Public of the place(s) of the respective executant, shall be submitted along with the bid.

FORM OF DEED OF UNDERTAKING BY THE CONTRACTOR

[STIPULATED IN CLAUSE ………………………………………………………]

(ON NON-JUDICIAL STAMP PAPER OF APPROPRIATE VALUE)

(Declaration by Contractor regarding ……………………. OF GTR/Qualifying Requirements for Indigenous manufacturer of OPGW)

THIS DEED OF UNDERTAKING executed this ……………. day of ………………….. Two Thousand and ………… by M/s. ……..……………., a Company incorporated under the laws of …………………. having its Registered Office at …………………. (hereinafter called the “Contractor” which expression shall include its successors, executors and permitted assigns) in favour of …….. (insert names of the Employer) …………….., a Company incorporated under the Companies Act of1956 having its registered office at …………….(insert registered address of the Employer)…………… (hereinafter called the “Employer” which expression shall include its successors, executors and permitted assigns)

WHEREAS the “Employer” invited Bid as per its Specification No. ……………….. for the execution of …………… (insert name of the package along with project name)…………………...

AND WHEREAS  Clause No. ………….., Section …………, of ………………, Vol.–… forming part of the Bid Documents inter-alia stipulates that the Contractor must fulfill the General Technical  Requirements/Qualifying Requirement for OPGW in the event of award/or post award stage and shall be bound and responsible for the successful performance of OPGW offered in the event the Bid submitted by the Contractor is accepted by the Employer resulting in a Contract.

AND WHEREAS the Bidder/Contractor has submitted its Bid to the Employer vide Proposal No. ………..….……. dated …………..

NOW THEREFORE THIS UNDERTAKING WITNESSETH as under:

- In consideration of the award of Contract by the Employer to the Contractor (hereinafter referred to as the “Contract”) we, the Contractor do hereby undertake that we shall be bound unto the …… (insert name of the Employer) …………, for the successful performance of OPGW and shall be fully responsible for the design, manufacture, testing, supply on FOR destination delivery at site basis and unloading at site, storage, erection, testing & commissioning and successful performance of  OPGW in accordance with the Contract Specifications.

- We confirm 3 (three) years Warranty obligations for the entire quantity to be supplied under this contract.

- We, the Contractor agree that this Undertaking shall be irrevocable and shall form an integral part of the Contract and further agree that this Undertaking shall continue to be enforceable till the Employer discharges it. It shall become operative from the effective date of Contract.

- This Deed of Undertaking shall be construed and interpreted in accordance with the laws of India and the Courts in Delhi shall have exclusive jurisdiction in all matters arising under the Undertaking.

IN WITNESS WHEREOF the Contractor have through their Authorised Representatives executed these presents and affixed Common seals of their respective Companies, on the day, month and year first above mentioned.

| WITNESS Signature ……………………. Name ……………………….. Office Address ………………. | (For Contractor) (Signature of the authorized representative) Name …………………….. Common Seal of Company …...……………. |
| --- | --- |
| WITNESS Signature ……………………. Name ………………………… Office Address ………………. | WITNESS Signature ……………………. Name ………………………… Office Address ………………. |

Note:

1.	For the purpose of executing the Deed of Undertaking, the non-judicial stamp papers of appropriate value shall be purchased in the name of executants parties.

2.	The Undertaking shall be signed on all the pages by the authorised representatives of Contractor should invariably be witnessed.

3.	This Deed of  Joint Undertaking attested by Notary Public of the place(s) of the respective executant(s) or registered with the Indian Embassy/High Commission in that country shall be submitted by the Contractor after finalization of vendor for OPGW as per TS in the event of award/ post award stage.

*  Strike-off whichever is not applicable.

FORM OF DEED OF UNDERTAKING TO BE EXECUTED BY THE BIDDER  [WHERE THE SUBSIDIARY COMPANY / JOINT VENTURE COMPANY IS TO BE INCORPORATED] FOR SUPPLY AT LEAST 25% OF OPGW CABLEMANUFACTURED IN THE SAID FACILITIES IN INDIA  [STIPULATED IN CLAUSE 1.1.1(a) (i) & (ii)  OF QUALIFICATION REQUIREMENT]

(ON NON-JUDICIAL STAMP PAPER OF APPROPRIATE VALUE)

This DEED OF UNDERTAKING executed this ............ day of ................. Two Thousand ............ by M/s................................................................, a Company incorporated under ......................... having its Registered Office at ...................................................... hereinafter called the “Bidder” which expression shall include its  successors, administrators, executors and permitted assigns, in favour of …….. (insert name of the Purchaser) …………….., a Company incorporated under the Indian Companies Act of 1956 having its registered office at …………….(insert registered address of the Purchaser)…………… (hereinafter called the “Purchaser” which expression shall include its successors, executors and permitted assigns)

WHEREAS the “Purchaser” invited Bid as per its Specification No. ……………. for the execution of …. (insert name of the package alongwith project name) ………………

AND WHEREAS Clause No. ………….., Section …………, of ………………, Vol.–… forming part of the Bidding Documents inter-alia stipulates that the Bidder must fulfill the Qualifying Requirements for the *…………………………… and be jointly and severally bound and responsible along with the Subsidiary Company / Joint Venture Company for the successful performance of the *……………………….. offered in the event the Bid submitted by the Bidder is accepated by the Purchaser resulting in a Contract.

AND WHEREAS the Bidder has submitted its Bid to the Purchaser vide Proposal No. ………..….……. dated ………. and confirmed that the Subsidiary Company / Joint Venture Company shall be incorporated as per Indian Companies Act, within six (06) months from the date of award.

AND WHEREAS the Bidder and the Subsidiary Company / Joint Venture Company are required to jointly execute and furnish an irrevocable Deed of Joint Undertaking and be jointly and severally liable to the Purchaser for ensuring supply at least 25% of OPGW Cablemanufactured in the said facilities in India  (hereinafter called as the “Equipment”) such that the Equipment to be supplied by the Supplier can be repaired and maintained without necessitating it to be taken outside the country and for supply at least 25% of OPGW Cablefrom such works of Subsidiary Company / Joint Venture Company to be set up in India.

AND WHEREAS the Bidder has submitted its Bid to the Purchaser based on above stipulation and has agreed to furnish this Deed of Undertaking to be enforceable in the event of the award of the Contract by the Purchaser.

1.0	In consideration of the award of Contract by the Purchaser to the Bidder/Supplier (hereinafter referred to as the “Contract”) we, the Bidder/Supplier do hereby agree and undertake to provide requisite Manufacturing and testing facilities for the Equipment, after sales service and supply of spare parts as per the terms of the Contract.

2.0	Without in any way affecting the generality and total responsibility in terms of this Deed of Undertaking, the Bidder/Supplier hereby agrees to depute their technical experts from time to time to the Subsidiary Company / Joint Venture Company Works/ Purchaser’s Project site as mutually considered necessary by the Purchaser, Bidder/Supplier and the Subsidiary Company / Joint Venture Company to ensure:

(i)	A valid technology transfer agreement, including license to manufacture and supply from India, between the Bidder / Supplier, the technology provider and the Subsidiary Company / Joint Venture Company covering the type, size and rating of the OPGW Cable specified, valid minimum up to the end of the defect liability period of the contract. The technology transfer agreement necessarily covers transfer of technological know-how for OPGW Cable in the form of complete transfer of design dossier, design software, drawings and documentation, quality system manuals and imparting relevant training by the Bidder / Supplier to the personnel of the Subsidiary Company / Joint Venture Company.

(ii)	Design of the Equipments manufactured in India shall be identical to the design of equipments to be manufactured and supplied by the Bidder/Supplier

(iii)	Adequate up gradation of the testing facilities including quality systems at Indian works

(iv)	Training to staff of the Group Company and certification to its trained personnel for carry out each activity

(v)	Involvement and supervision during all phases of manufacturing by expert of Bidder/Supplier for the OPGW Cable

(vi)	MQP of Group Company shall be same as that of Bidder/Supplier

(vii)	Source of raw material / major bought out components shall be same as that of Bidder/Supplier

(viii)	Timely supply on FOR destination delivery at site basis.

(ix)	Supervision of unloading at site, storage, erection, testing & commissioning and successful performance of the equipment in accordance with contract specifications

(x)	If necessary the Bidder/Supplier shall advise the Subsidiary Company / Joint Venture Company, suitable modifications of designs and implement necessary corrective measures to discharge the obligations under the Contract.

(xi)	Warranty obligations as per GCC clause 22.1 of the biding documents for the entire quantity to be supplied from the Subsidiary Company / Joint Venture Company.

3.0     This Deed of Undertaking shall be construed and interpreted in accordance with the laws of India and the Courts in Delhi shall have exclusive jurisdiction in all matters arising under the Undertaking.

4.0	We, agree that this undertaking shall be irrevocable and shall form an integral part of the Contract.

5.0	We hereby confirm that the above undertaking has also been approved by our Board of Directors and the Resolution passed by our Board(s) is attached with this undertaking.

IN WITNESS WHEREOF the Bidder / Supplier have through their Authorised Representatives executed these presents and affixed Common seals of their respective Companies on the day, month and year first above mentioned.

| WITNESS Signature ……………………. Name ……………………….. Office Address ………………. | [For Bidder] (Signature of the authorized representative) Name …………………….. Common Seal of Company …...……………. |
| --- | --- |
| WITNESS Signature ……………………. Name ……………………….. Office Address ………………. |  |

Note:

1.	For the purpose of executing the Deed of Undertaking, the non-judicial stamp papers of appropriate value shall be purchased in the name of executant.

2.	The Undertaking shall be signed on all the pages by the authorised representative(s) of the Bidder and should invariably be witnessed.

3.	The Resolution of the Board of Directors of the Bidder, as per the format, shall be attached with this Undertaking.

4.	This Deed of Undertaking duly attested by Notary Public of the place(s) of the respective executant, shall be submitted along with the bid.

FORM OF BANK GUARANTEE FOR CONTRACT PERFORMANCE

(TO BE SUBMITTED BY THE COLLABORATOR / PARENT COMPANY OF INDIGENOUS MANUFACTURER OF OPGW)

[STIPULATED IN CLAUSE …………………………………………………]

(ON NON-JUDICIAL STAMP PAPER OF APPROPRIATE VALUE)

Bank Guarantee No. ……………………          	Date...................

Contract No.....................................

…………..[Name of Contract]…………………….

To: [Name and address of the Employer]

Dear Ladies and/or Gentlemen,

We refer to the Contract ("the Contract") signed on ..............(insert date of the Contract)…..... between you and M/s…………………….............. (Name of Contractor) .................., having its Principal place of business at ………....(Address of Contractor) ............................... and Registered Office at ………....(Registered address of Contractor) ...................................................... ("the Contractor") concerning …….................….. (Indicate brief scope of work) ............................... for the complete execution of the …… (insert name of Package alongwith name of the Project)……..

Whereas, the Contractor has agreed to supply the OPGW Manufactured by M/s ....................................................(the Manufacturer), Having its Principal place of business  and Registered office at ………………………(Herein after Referred to as the ‘Manufacturer’ ) in collaboration with  (the manufactures) M/s. ................. (Name of Collaborator) .................., having its Principal place of business at ………....(Address of Collaborator) ............................... and Registered Office at ………....(Registered address of Collaborator) .................................... (hereinafter referred to as the “Collaborator”), as a pre-requisite for qualification of the Contractor/Manufacturer and have submitted a deed of joint undertaking declaring that they are jointly and severally bound and responsible for the successful performance of the said equipment in accordance with the Contract Specifications and that the Collaborator having agreed to furnish a Contract Performance Guarantee for the faithful performance/compliance of the Deed of Undertaking equivalent to (10%) ten per cent of the Ex-works  cost of OPGW to be supplied by the Manufacturer under the Contract during finalization of OPGW Vendor in the event of award/ post award stage, in addition to Contract Performance Guarantee equivalent to 10% (ten per cent) of the value of the Contract to be provided by the Contractor for the faithful performance of the  entire Contract.

By this letter we, the undersigned, ………(insert name & address of the issuing bank) ………, a Bank (or Company) organized under the laws of .................................... and having its Registered/Head Office at …..…….(insert address of registered office of the bank)……..... do hereby irrevocably guarantee payment to you up to ………………………….. i.e., ten percent (10%) of the  Ex-works cost of OPGW to be supplied by the Manufacturer under the Contract until ninety (90) days beyond the Defect Liability Period i.e., upto and inclusive of ……………. (dd/mm/yy).

We undertake to make payment under this Letter of Guarantee upon receipt by us of your first written demand signed by your duly authorized officer declaring the Contractor/Manufacturer/Collaborator to be in default under the Contract and without cavil or argument any sum or sums within the above named limits, without your need to prove or show grounds or reasons for your demand and without the right of the Contractor/Manufacturer/Collaborator to dispute or question such demand.

Our liability under this Letter of Guarantee shall be to pay to you whichever is the lesser of the sum so requested or the amount then guaranteed hereunder in respect of any demand duly made hereunder prior to expiry of the Letter of Guarantee, without being entitled to inquire whether or not this payment is lawfully demanded.

This letter of Guarantee shall remain in full force and shall be valid from the date of issue until ninety (90) days beyond the Defect Liability Period of the said equipment i.e. upto and inclusive of ……………. (dd/mm/yy) and shall be extended from time to time for such period (not exceeding one year), as may be desired by M/s. …………… on whose behalf this Letter of Guarantee has been given.

Except for the documents herein specified, no other documents or other action shall be required, notwithstanding any applicable law or regulation.

Our liability under this Letter of Guarantee shall become null and void immediately upon its expiry, whether it is returned or not, and no claim may be made hereunder after such expiry or after the aggregate of the sums paid by us to you up shall equal the sums guaranteed hereunder, whichever is the earlier.

All notices to be given under shall be given by registered (airmail) posts to the addressee at the address herein set out or as otherwise advised by and between the parties hereto.

We hereby agree that any part of the Contract may be amended, renewed, extended, modified, compromised, released or discharged by mutual agreement between you and the Collaborator, and this security may be exchanged or surrendered without in any way impairing or affecting our liabilities hereunder without notices to us and without the necessity for any additional endorsement, consent or guarantee by us, provided, however, that the sum guaranteed shall not be increased or decreased.

No action, event or condition which by any applicable law should operate to discharge us from liability hereunder shall have any effect and we hereby waive any right we may have to apply such law so that in all respects our liability hereunder shall be irrevocable and, except as stated herein, unconditional in all respects.

For and on behalf of the Bank

[Signature of the authorisedsignatory(ies)]

Signature_______________________

Name_______________________

Designation_______________________

POA Number_______________________

Contact Number(s): Tel.______________Mobile______________

Fax Number_______________________

email ____________________________

Common Seal of the Bank______________________

Witness:

Signature_______________________

Name_______________________

Address______________________________

Contact Number(s): Tel.______________Mobile______________

email ____________________________

Note :

1.	For the purpose of executing the Bank Guarantee, the non-judicial stamp papers of appropriate value shall be purchased in the name of Bank who issues the ‘Bank Guarantee’.

2.	The Bank Guarantee shall be signed on all the pages by the Bank Authorities indicating their POA nos. and should invariably be witnessed.

3.	In case the bid is submitted by a Collaborator/Parent Company, either individually or as a partner of Joint Venture, the additional performance guarantee of 10% shall not be applicable.

4.	The Bank Guarantee should be in accordance with the proforma as provided. However, in case the issuing bank insists for additional paragraph for limitation of liability, the following may be added at the end of the proforma of the Bank Guarantee [i.e., end paragraph of the Bank Guarantee preceding the signature(s) of the issuing authority(ies) of the Bank Guarantee]:

Quote

“Notwithstanding anything contained herein:

1. 	Our liability under this Bank Guarantee shall not exceed _________ (value in figures)____________ [_____________________ (value in words)____________].

2.  	This Bank Guarantee shall be valid upto________(validity date)__________.

3. 	We are liable to pay the guaranteed amount or any part thereof under this Bank Guarantee only & only if we receive a written claim or demand on or before ________ (validity date) __________.”

Unquote

FORM OF JOINT DEED OF UNDERTAKING BY THE COLLABORATOR/ PARENT COMPANY ALONGWITH THE BIDDER/MANUFACTURER

[In line with Clause ………………… : Qualifying Requirements for Indigenous manufacturer of OPGW of Section-I:  Technical Specifications, Volume-II (Applicable for OPGW to be supplied by Indigenous manufacturer )]

(ON NON-JUDICIAL STAMP PAPER OF APPROPRIATE VALUE)

THIS DEED OF UNDERTAKING executed this ……………. day of ………………….. Two Thousand and ………… by M/s. ……….…………….., a Company incorporated under the laws of …………………… and having its Registered Office at …………………………….. (hereinafter called the “Collaborator” which expression shall include its successors, executors and permitted assigns), and M/s. ……..……………., a Company incorporated under the laws of …………………. having its Registered Office at …………………. (hereinafter called the “Manufacturer” which expression shall include its successors, executors and permitted assigns ) and Ms/. ……………….., a Company incorporated under the laws of …………………. having its Registered Office at ………………….. (hereinafter called the “Bidder/Contractor” which expression shall include its successors, executors and permitted assigns) in favour of …….. (insert names of the Employer) …………….., a Company incorporated under the Companies Act of 1956 having its registered office at …………….(insert registered address of the Employer)…………… (hereinafter called the “Employer” which expression shall include its successors, executors and permitted assigns)

WHEREAS the “Employer” invited Bid as per its Specification No. .……………….. for the execution of ..…………… (insert name of the package along with project name)…………………....

AND WHEREAS  Clause No. ………….., Section …………, of ………………, Vol.–… forming part of the Bid Documents inter-alia stipulates that the Contractor and Manufacturer alongwith  its Collaborator must fulfill the Qualifying Requirements for OPGW and be jointly and severally bound and responsible for the successful performance of OPGW offered in the event the proposal for supply of OPGW from the Manufacturer submitted by the Contractor is accepted by the Employer.

AND WHEREAS the Contractor has submitted its proposal to the Employer vide Proposal No. ………..….……. dated ………. for supply of OPGW from the Manufacturer based on the collaboration/association of the Collaborator with the Bidder/Manufacturer.

NOW THEREFORE THIS UNDERTAKING WITNESSETH as under:

- In consideration of the award of Contract by the Employer to the Contractor (hereinafter referred to as the “Contract”) we, the Collaborator and the Contractor and the Manufacturer do hereby declare that we shall be jointly and severally bound unto the …… (insert name of the Employer) …………, for the successful performance of OPGW and shall be fully responsible for the design, manufacture, testing, supply on FOR destination delivery at site basis and supervision of unloading at site, storage, erection, testing & commissioning and successful performance of  OPGW in accordance with the Contract Specifications.

- Without in any way affecting the generality and total responsibility in terms of this Deed of Undertaking, the Collaborator in particular hereby agrees to depute their technical experts from time to time to the Contractor’s/Indian Manufacturer’s Works/Employer’s Project site as mutually considered necessary by the Employer, Contractor, Manufacturer and the Collaborator to ensure proper design, engineering, manufacture, testing, supply on FOR destination delivery at site basis and supervision of unloading at site,  storage,  erection,  testing  & commissioning and successful performance of the equipment in accordance with Contract Specifications and if necessary, the Collaborator shall advise the Indian Manufacturer /Contractor suitable modifications of designs, manufacturing process and implement necessary corrective measures to discharge the obligations under the contract.

  - Without in any way affecting the generality and total responsibility in terms of this Deed of Undertaking, the Collaborator/Parent Company in particular hereby agrees to depute their technical experts from time to time to the Contractor’s/Indian Manufacturer’s Works / Employer’s Project site as mutually considered necessary by the Employer, Contractor, Manufacturer and the Collaborator/Parent Company to ensure the warranty obligations for  Three (3) years for the entire quantity to be supplied from the Contractor/Manufacturer.

3.0 	As a security, Collaborator shall apart from the Bidder’s performance guarantee, furnish additional Contract Performance Guarantee from its Bank in favour of the Employer in a form acceptable to the Employer. The value of such guarantee shall be equivalent to 10% of the Ex works cost of OPGW as identified in the Contract awarded by the Employer to the Contractor. The guarantee shall be unconditional, irrevocable and valid for the entire period of the Contract, and till the end of the Defect Liability Period of ……………………………. under the Contract. The Bank Guarantee amount shall be payable to the Employer on demand without any reservation or demur.

4.0 	We, the Collaborator and Contractor and/or Manufacturer agree that this Undertaking shall be irrevocable and shall form an integral part of the Contract and further agree that this Undertaking shall continue to be enforceable till the Employer discharges it. It shall become operative from the effective date of Contract.

5.0    	This Deed of Undertaking shall be construed and interpreted in accordance with the laws of India and the Courts in Delhi shall have exclusive jurisdiction to adjudicate any dispute arising under or in connection with this agreement.

IN WITNESS WHEREOF the Collaborator, the Manufacturer and the Contractor have through their Authorised Representatives executed these presents and affixed Common seals of their respective Companies, on the day, month and year first above mentioned.

| WITNESS Signature ……………………. Name ……………………….. Office Address ………………. | (For Collaborator) (Signature of the authorized representative) Name …………………….. Common Seal of Company …...……………. |
| --- | --- |
| WITNESS Signature ……………………. Name ……………………….. Office Address ………………. | (For Contractor) (Signature of the authorized representative) Name …………………….. Common Seal of Company …...…………… |
| WITNESS Signature ……………………. Name ……………………….. Office Address ………………. | (For Manufacturer) (Signature of the authorized representative) Name …………………….. Common Seal of Company …...…………… |

Note:

1.	For the purpose of executing the Deed of Joint Undertaking, the non-judicial stamp papers of appropriate value shall be purchased in the name of executants parties.

2.	The Undertaking shall be signed on all the pages by the authorised representatives of each of the partners and should invariably be witnessed.

3.	This Deed of Joint Undertaking duly certified by the Company Secretary shall be submitted alongwith the bid.  Further, the Deed of Joint Undertaking attested by Notary Public of the place(s) of the respective executant(s) or registered with the Indian Embassy/High Commission in that country shall be submitted by the bidder within ten (10) days from the date of intimation of post-bid discussion.

FORM OF DEED OF JOINT UNDERTAKING TO BE EXECUTED BY THE BIDDER / SUPPLIER  AND THE SUBSIDIARY COMPANY/JOINT VENTURE COMPANY/GROUP COMPANY (ALREADY INCORPORATED / AFTER INCORPORATION) OF THE BIDDER / SUPPLIER  FOR SUPPLY AT LEAST 25% OF OPGW CABLE MANUFACTURINED IN THE SAID FACILITIES IN INDIA  [STIPULATED IN CLAUSE 1.1.1(a) (i) & (ii)  OF QUALIFICATION REQUIREMENT]

(ON NON-JUDICIAL STAMP PAPER OF APPROPRIATE VALUE)

This DEED OF UNDERTAKING executed this ............ day of ................. Two Thousand ............ by M/s................................................................, a Company incorporated under ......................... having its Registered Office at ...................................................... hereinafter called the “Bidder/Supplier” which expression shall include its  successors, administrators, executors and permitted assigns and M/s. ……………………………………, registered under the Indian Companies Act of 1956 or 2013, as the case may be, and having its Registered Office at ................................................. hereinafter called the “Subsidiary Company/Group Company /Joint Venture Company (JVC)” which expression shall include its  successors, administrators, executors and permitted assigns, in favour of …….. (insert names of the Purchaser) …………….., a Company incorporated under the Indian Companies Act of 1956 having its registered office at …………….(insert registered address of the Purchaser)…………… (hereinafter called the “Purchaser” which expression shall include its successors, executors and permitted assigns)

WHEREAS the “Purchaser” invited Bid as per its Specification No. ……………. for the execution of …. (insert name of the package alongwith project name) ………………

AND WHEREAS Clause No. ………….., Section …………, of ………………, Vol.–… forming part of the Bidding Documents inter-alia stipulates that the Bidder/Supplier along with the Subsidiary Company/Joint Venture Company/Group Company must fulfill the Qualifying Requirements for the *…………………………… and be jointly and severally bound and responsible for the successful performance of the *……………………….. offered in the event the Bid submitted by the Bidder is accepted by the Purchaser resulting in a Contract.

AND WHEREAS the Bidder has submitted its Bid to the Purchaser vide Proposal No. ………..….……. dated ………. based on the association of the Subsidiary Company / Group Company / Joint Venture Company and are required to jointly execute and furnish an irrevocable Deed of Joint Undertaking and be jointly and severally liable to the Purchaser for ensuring manufacturing facilities of OPGW Cable in India (hereinafter called as the “Equipment”) such that the Equipment to be supplied by the Supplier can be repaired and maintained without necessitating it to be taken outside the country and for supply at least 25% of OPGW Cable from such works of Subsidiary Company / Group Company / Joint Venture Company in India.

AND WHEREAS the Bidder has submitted its Bid to the Purchaser based on above stipulation and has agreed to furnish this Deed of Undertaking to be enforceable in the event of the award of the Contract by the Purchaser.

1.0	In consideration of the award of Contract by the Purchaser to the Bidder / Supplier (hereinafter referred to as the “Contract”) we, the Bidder/Supplier and the Subsidiary Company/Joint Venture Company/ Group Company do hereby agree and undertake to provide requisite Manufacturing and testing facilities for the Equipment, after sales service and supply of spare parts as per the terms of the Contract.

2.0	Without in any way affecting the generality and total responsibility in terms of this Deed of Undertaking, the Bidder/Supplier hereby agrees to depute their technical experts from time to time to the Subsidiary Company/Joint Venture Company/ Group Company Works/ Purchaser’s Project site as mutually considered necessary by the Purchaser, Bidder/Supplier and the Subsidiary Company/Joint Venture Company/ Group Company to ensure:

(i)	A valid technology transfer agreement, including license to manufacture and supply from India, between the Bidder / Supplier, the technology provider and the Subsidiary Company/Joint Venture Company/ Group Company covering the type, size and rating of the OPGW Cable specified, valid minimum up to the end of the defect liability period of the contract. The technology transfer agreement necessarily covers transfer of technological know-how for OPGW Cablein the form of complete transfer of design dossier, design softwares, drawings and documentation, quality system manuals and imparting relevant training by the Bidder / Supplier to the personnel of the Subsidiary Company / Group Company / Joint Venture Company.

(ii)	Design of the Equipments manufactured in India shall be identical to the design of equipments to be manufactured and supplied by the Bidder/Supplier

(iii)	Adequate up gradation of the testing facilities including quality systems at Indian works

(iv)	Training to staff of the Subsidiary Company/Joint Venture Company/ Group Company and certification to its trained personnel for carry out each activity

(v)	Involvement and supervision during all phases of manufacturing by expert of Bidder/Supplier for the OPGW Cable.

(vi)	MQP of Subsidiary Company/Joint Venture Company/ Group Company shall be same as that of Bidder/Supplier

(vii)	Source of raw material / major bought out components shall be same as that of Bidder/Supplier

(viii)	Timely supply on FOR destination delivery at site basis.

(ix)	Supervision of unloading at site, storage, erection, testing & commissioning and successful performance of the equipment in accordance with contract specifications

(x)	If necessary the Bidder/Supplier shall advise the Subsidiary Company/Joint Venture Company/ Group Company, suitable modifications of designs and implement necessary corrective measures to discharge the obligations under the Contract.

(xi)	Warranty obligations as per GCC clause 22.1of the biding documents for the entire quantity to be supplied from the Subsidiary Company/Joint Venture Company/ Group Company.

3.0     This Deed of Undertaking shall be construed and interpreted in accordance with the laws of India and the Courts in Delhi shall have exclusive jurisdiction in all matters arising under the Undertaking.

4.0	We, agree that this undertaking shall be irrevocable and shall form an integral part of the Contract.

5.0	We hereby confirm that the above undertaking has also been approved by our Board of Directors and the Resolution passed by our Board(s) is attached with this undertaking.

IN WITNESS WHEREOF the Supplier and Subsidiary Company/Group Company/Joint Venture Company have through their Authorised Representatives executed these presents and affixed Common seals of their respective Companies on the day, month and year first above mentioned.

| WITNESS Signature ……………………. Name ……………………….. Office Address ………………. | [For Bidder/Supplier] (Signature of the authorized representative) Name …………………….. Common Seal of Company …...……………. |
| --- | --- |
| WITNESS Signature ……………………. Name ……………………….. Office Address ………………. | [For Subsidiary Company/Group Company/Joint Venture Company] (Signature of the authorized representative) Name …………………….. Common Seal of Company …...……………. |

Note:

1.	For the purpose of executing the Deed of Undertaking, the non-judicial stamp papers of appropriate value shall be purchased in the name of executant.

2.	The Undertaking shall be signed on all the pages by the authorised representative(s) of the Bidder and the Subsidiary Company/Group Company/Joint Venture Company and should invariably be witnessed.

3.	The Resolution of the Board of Directors of the Bidder and the Subsidiary Company / Group Company / Joint Venture Company, as per the format, shall be attached with this Undertaking.

4.	This Deed of Undertaking duly attested by Notary Public of the place(s) of the respective executant, shall be submitted along with the bid, in case where the Subsidiary Company/Group Company/Joint Venture Company is already incorporated under the Indian Companies Act, and shall be submitted during execution of contract if the Subsidiary Company/Group Company/Joint Venture Company is incorporated under the Indian Companies Act subsequent to award of contract.