## Basic (hidden)
Package Name | Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II.
Package Code | Civil Works
Specification No. | SR-II/C&M/WC-4332/2025

## Cover
REV_01
Price Schedules | Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II. |  | Civil Works
SR-II/C&M/WC-4332/2025
| 1 | Fill up only green shaded cells in Sch-1, Sch-2, Sch-3 and Bid Form of price bid
| 2 | All the cells in Sch-2 & Sch-3 are auto filled, therefore no cell is required to be filled up there.
| 3 | Instructions / error messages, if any, will be displayed automatically after selecting the cell.
| 4 | After filling up all the schedues, save the file, take print out of all the schedules and Bid form and sign & stamp and submit them as hard copy of the 2nd envelope (Price part) of the bid. Also ensure to submit the soft copy of the the same file on CD/ DVD.
Click to skip Instructions & Proceed
Click for Detailed General Instructions
General guidelines for filling up the Price Schedules, Sch-1 to Sch-3

## Instructions
General Instruction to the Bidders for filling up this workbook of Price Schedules for Package SS01
I | While filling up the worksheets following may please be observed :
| (i) | Fill up only green shaded cells.
| (ii) | Certain data type entries have been restricted, such as Numeric values or limits of numeric values.
| (iii) | Select only the options provided in pull down menus.
| (iv) | Do not link any cell of this work book with any other work book.
| (v) | Do not use copy & paste or cut & paste options for filling up the data.
| (vi) | Do not reformat any of the cell of the work book.
II | This Workbook consists of following worksheets :
Cover :
Opening page of the workbook.
Names of Bidder :
| ● | Select Sole Bidder or JV (Joint Venture) from the pull down menu. Do not leave this cell blank.
| ● | Select nos. of the JV Partners other than the Lead Partner from drop down menu.
| ● | In case of JV partners more than 2, enter details of 3rd & more partners along with details of 2nd partner.
| ● | Fill up names and address of the Sole Bidder and /or Joint Venture.
| ● | Fill up date in dd-mmm-yyyy format from drop down menu.
| ● | Click for proceed given at the right top of the worksheet and go to Sch-3.
Sch-1 (Ex-works Prices) :
| ● | Fill up unit rates for all the items in numeric values greater than 0 (zero). If unit rate is left blank, the corresponding item shall be deemed to be included in the total price.
| ● | Corresponding cell for mode of transaction shall be come enable only after filling up the unit rate, therefore first fill up the unit rate and then mode of transaction for the corresponding item.
●
| ● | Total amount shall get calculated automatically.
| ● | Type Test charges shall appear automatically after filling up Sch-7 appropriately.
Sch-2 (Freight & Insurance Charges) :
| ● | Fill up unit rates for all the items in numeric values greater than 0 (zero). If unit rate is left blank, the corresponding item shall be deemed to be included in the total price.
| ● | Total amount shall get calculated automatically.
Sch-1 (Installation / Service Charges) :
| ● | Fill up unit rates for all the items in numeric values greater than 0 (zero). If unit rate is left blank, the corresponding item shall be deemed to be included in the total price.
| ● | Total amount shall get calculated automatically.
Sch-4 (Training Charges) :
| ● | Not applicable, hence no cell is required to be filled up.
Sch-2 (Summary of Taxes and Duties applicable on the Services) :
| ● | No cell is required to be filled in by the bidder in this worksheet.
Sch -3 (Grand-Total) :
| ● | Summary of all the Schedules without considering discount (mentioned in the work sheet discount) shall be displayed automatically.
| ● | No cell is required to be filled in by the bidder in this worksheet.
Sch-7 (Type Test Charges) :
| ● | Fill up the rates & location where type tests are proposed.
| ● | Total of this Sch-7 shall automatically appear in Sch-1.
Bid from of price bid :
| ● | Fill up ref. no. as bidder's ref no. of this letter.
| ● | This letter shall consider the net price as per Sch-3
| ● | Fill up names & Designation of the representatives of other JV partner(s) if the bidder is JV (Joint Venture) .
| ● | Fill up additional information as required.
* * *
Happy Bidding !
Click to Proceed

## Names of Bidder
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II.
SR-II/C&M/WC-4332/2025 |  |  |  | Sole Bidder | 1
|  |  |  | JV (Joint Venture) | 2 or More
Enter following details of the bidder
Specify type of Bidder [Select from drop down menu] | Sole Bidder |  |  | 0
2 or More
Name of Bidder
Address of Bidder
Name of other Partner - 1
Address of other Partner - 1
…….. …….. …….. …….. …….. ……..
…….. …….. …….. …….. …….. ……..
Name of other Partner - 2 (more, if any) | …….. …….. …….. …….. …….. ……..
Address of other Partner - 2 (more, if any) | …….. …….. …….. …….. …….. ……..
…….. …….. …….. …….. …….. ……..
…….. …….. …….. …….. …….. ……..
Printed Name
Designation
email ID of Bid Signatory
Mobile No. of Bid Signatory
Tel No. of Bid Signatory
Fax No. of Bid Signatory
Date |  | 2025 | 31
Place
Click for Sch-3

## Sch-1 (hidden)
SR-II/C&M/WC-4332/2025 | [12 empty] | Schedule - 1
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II.
(SCHEDULE OF RATES AND PRICES)
Bidder’s Name and Address (Bidder) : | [11 empty] | To:
Sr.GM , Contracts & Materials Department,
Name : | [11 empty] | Power Grid Corporation of India Ltd.,
Address : | [11 empty] | SRTS-II, RHQ
Singanayakanahalli
Bengaluru-560064
Construction of Storage platform for spares of ±320 kV HVDC Line Materials at Palakkad SS
All Prices are in Indian Rupees.
SI. No. | PR No | PR Line Item No | Activity Description | Material Code | HSN Code | Whether HSN in column ‘6’ is confirmed. If not indicate applicable the HSN code * | Rate of GST applicable ( in %) | Whether rate of GST in column ‘8’ is confirmed. If not indicate applicable rate of GST * | Item Description | Unit | Qty. | Unit Ex-works price (excluding GST) | Total Ex-works price (excluding GST) | GST
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 = 12x13 | 11
1 | 7000005840 | 20 | FABRICATION AND SUPPLY |  | 76169990 |  | 18% |  | Supply of Galvanised Steel PG Clamps for Sheild / Earth wire of dia 10.98 mm in line with the drawing enclosed | Nos | 1300 |  | Included | 0 | 0 | 0
2 |  |  |  |  | 76169990 |  | 18% |  | Supply of Galvanised Steel PG clamps suitable to accommodate Earthwire of 10.98 mm in one groove and 12 mm OPGW cable in the other groove, in line with the tentative drawing enclosed. | Nos | 1300 |  | Included | 0 | 0 | 0
3 |  |  |  |  | 76169990 |  | 18% |  | Supply of 1.5 mm thickness Galvanised steel 'C' / 'U' clamp suitable for 10.98 mm earthwire / shield wire,in line with the drawing enclosed. | Nos | 23400 |  | Included | 0 | 0 | 0
[9 empty] | Total Ex-Works Price |  |  |  | 0 | 0
[9 empty] | Total Type Test charges as per Schedule-7 |  |  |  | 0
[9 empty] | Total Ex-works Price including Type Test charges |  |  |  | 0 | 0 |  |  | Total GST
Note : |  | Specify amount of GST on the transaction between the Contractor and the Employer.
* |  | In case the bidder leaves the cell for confirmation of the HSN code and/or GST rate “blank”, the HSN code and corresponding GST rate indicated by the Employer shall be deemed to be the one confirmed by the Bidder.
Date : |  |  |  |  | --2025
Place : | [9 empty] | Printed Name :
Designation :
Click for Sch-2

## Sch-1 dis (hidden)
SR-II/C&M/WC-4332/2025 | [5 empty] | Schedule - 1 |  |  |  | Direct Total | 0 | Sole Bidder | `
[10 empty] | BO Total | #REF! | 0
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II.
(SCHEDULE OF RATES AND PRICES : EX-WORKS PRICES)
Bidder’s Name and Address (Bidder) : |  |  |  | To:
Contract Services
Name : |  |  |  | Power Grid Corporation of India Ltd., | [7 empty] | , & …….. …….. …….. …….. …….. ……..
Address : |  |  |  | "Saudamini", Plot No.-2
Sector-29,
Gurgaon (Haryana) - 122001
Plant and Equipment (including Mandatory Spares Parts) to be supplied, including Type Test Charges for Tests to be conducted. | [10 empty] | Direct
[6 empty] | All Prices are in Indian Rupees. |  |  |  |  | Bought-Out
SI. No. | Item Description | Unit | Qty. | Unit Ex-works price | Total Ex-works price | Mode of Transaction (Direct / Bought-out)
1 | 2 | 3 | 4 | 5 | 6 = 4 x 5 | 7
#REF! | #REF!
#REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF!
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total Ex-Works Price Direct |  |  |  | 0 | Direct
| Total Ex-Works Price Bought Out |  |  |  | 0
| Total Ex-Works Price |  |  |  | 0
| Total Type Test charges as per Schedule-7 |  |  |  | #REF! |  |  | #REF! |  | #REF!
| Total Ex-works Price including Type Test charges |  |  |  | #REF! |  |  | #REF! |  | #REF!
[7 empty] | Discount Sch-1 | #REF! | MPD Sch-1 | #REF!
[7 empty] | Dis Alert | #REF!
Note : | Specify amount of Excise Duty, Sales Tax/'VAT and other taxes payable on the transaction between the Contractor and the Employer and octroi/entry tax as applicable for destination site/state on all items of supply including bought-out finished items (to be identified in the Contract), which shall be dispatched directly from the sub-vendor’s works to the Employer’s site (sale-in-transit), separately in Schedule-5. Excise Duty, Sales tax and other levies for all the bought-out items are to be included in the EXW Price (Col. No. 5) only and not to be indicated in Schedule-5.
Date : | --2025
Place : |  |  | Printed Name :
Designation :
Click for Sch-2

## Sch-2 (hidden)
SR-II/C&M/WC-4332/2025 | [8 empty] | Schedule - 2
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II.
(SCHEDULE OF RATES AND PRICES :Transportation, In-transit insurance, loading and unloading.)
Bidder’s Name and Address (Bidder) : | [7 empty] | To:
Sr.GM , Contracts & Materials Department,
Name : | [7 empty] | Power Grid Corporation of India Ltd.,
Address : | [7 empty] | SRTS-II, RHQ
Singanayakanahalli
Bengaluru-560064
All Prices are in Indian Rupees.
SI. No. | PR No | PR Line Item No | Activity Description | Material Code | Description | Unit | Quantity | Unit Prices F&I including packing and forwading Including taxes | Total Prices
1 | 2 | 3 | 4 | 5 | 6 | 7 | 9 | 10 | 11= 9 x 10
1 | 7000005840 | 20 | FABRICATION AND SUPPLY | 1000015274 | Supply of Galvanised Steel PG Clamps for Sheild / Earth wire of dia 10.98 mm in line with the drawing enclosed | Nos | 1300 |  | Included
2 |  |  |  |  | Supply of Galvanised Steel PG clamps suitable to accommodate Earthwire of 10.98 mm in one groove and 12 mm OPGW cable in the other groove, in line with the tentative drawing enclosed. | Nos | 1300 |  | Included
3 |  |  |  |  | Supply of 1.5 mm thcikness Galvanised steel 'C' / 'U' clamp suitable for 10.98 mm earthwire / shield wire,in line with the drawing enclosed. | Nos | 23400 |  | Included
[5 empty] | Total F&I Price |  |  |  | 0
Date : |  |  |  |  | --2025
Place : | [6 empty] | Printed Name :
Designation :
Click for Sch-3

## Sch-2 Dis (hidden)
SR-II/C&M/WC-4332/2025 |  |  |  |  | Schedule - 2 Dis
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II. | [5 empty] | As per Lum-sum |  | 0
(SCHEDULE OF RATES AND PRICES : FREIGHT & INSURANCE CHARGES) | [5 empty] | AS per Percent |  | #REF!
[6 empty] | As per lum-sum on Sch-2 |  | 0%
Bidder’s Name and Address (Bidder) : |  |  |  | To: |  | As per Percent on Sch-2 |  | #REF!
|  |  |  | Sr.GM , Contracts & Materials Department, |  | Total Discount |  | #REF!
Name : |  |  |  | Power Grid Corporation of India Ltd.,
Address : |  |  |  | SRTS-II, RHQ
|  |  |  | Singanayakanahalli |  | Multipackage Discount |  | #REF!
Bengaluru-560064
[5 empty] | All Prices are in Indian Rupees. |  | Amount after Discount (Rs.) |  | Dis Alert | Amount after MPD (Rs.)
SI. No. | Description | Unit | Quantity | Unit Freight & Insurance Charges | Total Freight & Insurance Charges |  | Unit Freight & Insurance Charges | Total Freight & Insurance Charges |  | Unit Freight & Insurance Charges | Total Freight & Insurance Charges
1 | 2 | 3 | 4 | 5 | 6 = 4 x 5 |  | 5 | 6 = 4 x 5 |  | 5 | 6 = 4 x 5
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total F&I Price |  |  |  | #REF!
Date : | --2025
Place : |  |  | Printed Name :
Designation :
Click for Sch-3

## Sch-3 Dis (hidden)
SR-II/C&M/WC-4332/2025 |  |  |  |  | Schedule - 3
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II. | [7 empty] | As per Lum-sum |  | 0%
(SCHEDULE OF RATES AND PRICES : ERECTION CHARGES) | [7 empty] | AS per Percent |  | #REF!
[8 empty] | As per lum-sum on Sch-3 |  | 0%
Bidder’s Name and Address (Bidder) : |  |  |  | To: |  |  |  | As per Percent on Sch-3 |  | #REF!
|  |  |  | Sr.GM , Contracts & Materials Department, |  |  |  | Total Discount |  | #REF!
Name : |  |  |  | Power Grid Corporation of India Ltd.,
Address : |  |  |  | SRTS-II, RHQ
|  |  |  | Singanayakanahalli |  |  |  | Multipackage lum-sum |  | #REF!
Bengaluru-560064
[5 empty] | All Prices are in Indian Rupees. |  |  |  | Amount after Discount (Rs.) |  | Dis Alert | Amount after MPD (Rs.)
SI. No. | Description | Unit | Quantity | Unit Erection Charges | Total Erection Charges |  |  |  | Unit Erection Charges | Total Erection Charges |  | Unit Erection Charges | Total Erection Charges
1 | 2 | 3 | 4 | 5 | 6 = 4 x 5 |  |  |  | 5 | 6 = 4 x 5 |  | 5 | 6 = 4 x 5
#REF! | #REF!
#REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  |  |  |  | (a) | Detailed Soil Investigation
| #REF! | #REF! | #REF! | #REF! | #REF! | (b) | All kinds of soil except fissured rock & hard rock
| #REF! | #REF! | #REF! | #REF! | #REF! | (e) | River Crossing Location
| #REF! | #REF! | #REF! | #REF! | #REF! | (f)
#REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
#REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF!
| #REF! | #REF! | #REF! | #REF! | #REF!
| Total Erection Price (A+B) |  |  |  | #REF!
Date : | --2025
Place : |  |  | Printed Name :
Designation :
Click for Sch-4

## Sch-4 (hidden)
SR-II/C&M/WC-4332/2025 |  |  |  | Schedule - 4
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II.
(SCHEDULE OF RATES AND PRICES )
Bidder’s Name and Address (Bidder) : |  |  | To:
Sr.GM , Contracts & Materials Department,
Name : |  |  | Power Grid Corporation of India Ltd.,
Address : |  |  | SRTS-II, RHQ
Singanayakanahalli
Bengaluru-560064
AMC Charges
| TOTAL TRAINING CHARGES |  |  | 0
Date : | -- | Printed Name :
Place : |  | Designation :
Click for Sch-5

## Sch-1 (2) (hidden)
SR-II/C&M/WC-4332/2025 | [10 empty] | Schedule - 1
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II. | [15 empty] | As per Lum-sum |  | 0%
(SCHEDULE OF RATES AND PRICES ) | [15 empty] | AS per Percent |  | #REF!
[16 empty] | As per lum-sum on Sch-3 |  | 0%
Bidder’s Name and Address (Sole Bidder) : | [9 empty] | To: | [5 empty] | As per Percent on Sch-3 |  | #REF!
[10 empty] | C&M Department | [5 empty] | Total Discount |  | #REF!
Name : | [9 empty] | Power Grid Corporation of India Ltd.
Address : | [9 empty] | SR-II, RHQ
[10 empty] | Singanayakkanahalli, Yelahanka | [5 empty] | Multipackage lum-sum |  | #REF!
Bangalore
[17 empty] | Amount after Discount (Rs.) |  | Dis Alert | Amount after MPD (Rs.)
All Prices are in Indian Rupees.
SI. No. | DSR-2021 Ref | SAC (Service Accounting Codes) | Whether SAC in column '2’ is confirmed. If not indicate applicable the SAC * | Rate of GST applicable ( in %) | Whether rate of GST in column ‘ 4 ’ is confirmed. If not indicate applicable rate of GST * | DSR 2023 Ref | Description | Unit | Quantity | Unit Rate in Rs. | Total in Rs. | GST TAX as confirmed by Bidder |  |  |  |  | Unit Erection Charges | Total Erection Charges |  | Unit Erection Charges | Total Erection Charges
1 |  | 2 | 3 | 4 | 5 |  | 6 | 7 | 8 | 9 | 10 = 8 x 9 | 11 |  |  |  |  | 5 | 6 = 4 x 5 |  | 5 | 6 = 4 x 5
I |  |  |  |  | SCHEDULE 1 |  | Civil works -Proposal for Renovation of B type, B+ type, C type & D type quarters at Udumalpet SS
PART - A SCHEDULE ITEMS
1 | 13.91 mod | 995413 |  | 18% | confirmed |  | Removing dry or oil bound distemper, water proofing cement paint, other paint, by scrapping, hacking, sand papering and preparing the surface smooth including necessary repairs to scratches, sealing of cracks etc. complete. as per direction of Engineer-in-charge. (Item includes all tools and tackles including scaffolding wherever necessary upto 1st floor roof level.) | sqm | 14200 |  | Included | 0 | 0 | 0
2 | 14.83 mod | 995413 |  | 18% | confirmed |  | Hacking of CC flooring,wall including cleaning for surface etc. complete as per direction of the Engineer-in-Charge. | sqm | 1490 |  | Included | 0 | 0 | 0
3 | 15.56 mod | 995413 |  | 18% | confirmed |  | Dismantling old plaster or skirting raking out joints and cleaning the surface for plaster including disposal of rubbish to the dumping ground within 1 km lead.as per direction of the Engineer-in-Charge. | sqm | 160 |  | Included | 0 | 0 | 0
3a | 11.41A.1 | 995413 |  | 18% | confirmed |  | Providing and laying Vitrified tiles in floor in different sizes (thickness 8-10mm as directed by engineer in charge) with water absorption less than 0.08% and conforming to IS:15622, of approved brand & manufacturer, in all colours and shade, laid on 20 mm thick cement mortar 1:4 (1 cement: 4 coarse sand) jointing with grey cement slurry @3.3 kg/sqm including grouting the joints with white cement and matching pigments etc. The tiles must be cut with the zero chipping diamond cutter only . Laying of tiles will be done with the notch trowel, plier, wedge, clips of required thickness, leveling system and rubber mallet for placing the tiles gently and easily. Double charge vitrified tile polished finish of size. Size of Tile 600 x 600 mm as per direction of the Engineer-in-Charge. | sqm | 1500 |  | Included | 0 | 0 | 0
5 | 11.46.2 | 995413 |  | 18% | confirmed |  | Providing and laying Vitrified tiles in different sizes(thickness 8-10mm as directed by engineer in charge) , with water absorption less than 0.08 % and conforming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), jointing with grey cement slurry @ 3.3 kg/ sqm including grouting the joint with white cement & matching pigments etc. complete. Size of Tile 600x600 mm as per direction of the Engineer-in-Charge. In ground floor and first floor quarters. | sqm | 160 |  | Included | 0 | 0 | 0
6 | 8.31 | 995413 |  | 18% | confirmed |  | Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in toilet walls, kitchen walls, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete.as per direction of the Engineer-in-Charge.( Item includes hacking of wall wherever necessary.) | sqm | 760 |  | Included | 0 | 0 | 0
7 | 11.38 mod | 995413 |  | 18% | confirmed |  | Providing and laying antiskid Ceramic glazed floor tiles of size 300x300 mm (thickness to be specified by the manufacturer), of 1st quality conforming to IS : 15622, of approved make, in all colours, shades, except White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick bed of cement mortar 1:4 (1 Cement : 4 Coarse sand), jointing with grey cement slurry @ 3.3kg/ sq.m including pointing the joints with white cement and matching pigments etc., complete | sqm | 105 |  | Included | 0 | 0 | 0
8 | 14.75 mod | 995413 |  | 18% | confirmed |  | Repair to plaster of thickness 12mm to 20 mm in patches of area 2.5 sqm and under, including cutting the patch in proper shape, raking out joints and preparing plastering the wall surface with white cement based polymer modified self curing mortar, including disposal of rubbish upto a lead of 1km and lift of 1.5m, all complete as per the direction of Engineer-In-Charge.Item includes all tools and tackles including scaffolding wherever necessary upto 1st floor roof level. | sqm | 900 |  | Included | 0 | 0 | 0
9 | 15.12.1 mod | 995413 |  | 18% | confirmed |  | Dismantling doors, windows,Cupboard and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete as per direction of the Engineer-in-Charge. and stacking within 1km lead :Of area 3 sq. metres and below. (Item includes all tools and tackles including scaffolding wherever necessary upto 1st floor roof level.) | each | 500 |  | Included | 0 | 0 | 0
10 | 13.80 mod | 995413 |  | 18% | confirmed |  | Providing and applying white cement based putty of average thickness 1 mm-5mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete as per direction of the Engineer-in-Charge.(Item includes all tools and tackles including scaffolding wherever necessary upto 1st floor roof level.) | sqm | 8100 |  |  |  | 0 | 0
11 | 13.43.1 | 995413 |  | 18% | confirmed |  | Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface as per direction of the Engineer-in-Charge.: Water thinnable cement primer.(Item includes all tools and tackles including scaffolding wherever necessary upto 1st floor roof level.) | sqm | 15500 |  | Included | 0 | 0 | 0
12 | 13.83.2 | 995413 |  | 18% | confirmed |  | Wall painting with premium emulsion paint of interior grade of superior quality, of approved brand and manufacture, including applying additional coats wherever required to achieve even shade and colour as per direction of the Engineer-in-Charge.Two coats. (Item includes all tools and tackles including scaffolding wherever necessary upto 1st floor roof level.) | sqm | 9900 |  | Included | 0 | 0 | 0
13 | 13.112.1 | 995413 |  | 18% | confirmed |  | Finishing walls with Premium Acrylic Smooth exterior paint of superior quality of required shade: Old work (Two or more coats applied @ 1.43 ltr/ 10 sqm) over existing cement paint surface. as per direction of the Engineer-in-Charge. (Item includes all tools and tackles including scaffolding wherever necessary upto 1st floor roof level.) | sqm | 5600 |  | Included | 0 | 0 | 0
14 | 13.99.1 | 995413 |  | 18% | confirmed |  | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade :One or more coats on old work as per direction of the Engineer-in-Charge. (Item includes all tools and tackles including scaffolding wherever necessary upto 1st floor roof level.) | sqm | 630 |  | Included | 0 | 0 | 0
15 | 15.23.1 mod | 995413 |  | 18% | confirmed |  | Dismantling tile work in floors and walls laid in cement mortar including stacking material within 2 km metres lead.For thickness of tiles 10 mm to 25 mm. | sqm | 780 |  | Included | 0 | 0 | 0
16 | 9.147D.2 mod | 995413 |  | 18% | confirmed |  | Providing and fixing factory made uPVC white colour sliding glazed window upto 1.50 m in height dimension comprising of uPVC multi-chambered frame with in-built roller track and sash extruded profiles duly reinforced with 1.60 ± 0.2 mm thick galvanized mild steel section made from roll forming process of required length (shape & size according to uPVC profile), appropriate dimension of uPVC extruded glazing beads and uPVC extruded interlocks, EPDM gasket, wool pile, zinc alloy (white powder coated) touch locks with hook, zinc alloy body with double or more nylon rollers (weight bearing capacity to be 40 kg), G.I fasteners 100 x 8 mm size for fixing frame to finished wall and necessary stainless steel screws etc. Profile of frame & sash shall be mitred cut and fusion welded at all corners, including drilling of holes for fixing hardware's and drainage of water etc. After fixing frame the gap between frame and adjacent finished wall shall be filled with weather proof silicon sealent over backer rod of required size and of approved quality, all complete as per approved drawing & direction of Engineer-in-Charge. (Single / double glass panes, wire mesh and silicon sealent shall be paid separately). Variation in profile dimension in higher side shall be accepted but no extra payment on this account shall be made. Three track three panels sliding window with fly proof SS wire mesh (Two nos. glazed & one no. wire mesh panels) made of (small series) frame 92 x 44 mm & sash 32 x 60 mm both having wall thickness of 1.9 ± 0.2 mm and single glazing bead of appropriate dimension including approved star locks and fittings (Area of window upto 1.75 sqm). | sqm | 180 |  | Included | 0 | 0 | 0
17 | 9.7.7.1 | 995413 |  | 18% | confirmed |  | Providing and fixing panelling or panelling and glazing in panelled or panelled and glazed shutters for doors, windows and clerestory windows with EPDM rubber / neoprene gasket etc. (Area of opening for panel inserts excluding portion inside grooves or rebates to be measured). Panelling for panelled or panelled and glazed shutters 25 mm to 40 mm thick :Float glass panes of 4 mm thick glass pane (weight not less than 10kg/sqm). | sqm | 200 |  | Included | 0 | 0 | 0
18 | 9.12 | 995413 |  | 18% | confirmed |  | Extra for providing frosted glass panes 4 mm thick instead of ordinary float glass panes 4 mm thick in doors, windows and clerestory window shutters. (Area of opening for glass panes excluding portion inside rebate shall be measured). as per direction of the Engineer-in-Charge. | sqm | 200 |  | Included | 0 | 0 | 0
19 | 9.135.2 | 995413 |  | 18% | confirmed |  | Providing and fixing fly proof stainless steel grade 304 wire gauge, to windows and clerestory windows using wire gauge with average width of aperture 1.4 mm in both directions with wire of dia. 0.50 mm all complete.With 12 mm mild steel U beading as per direction of the Engineer-in-Charge. | sqm | 90 |  | Included | 0 | 0 | 0
20 | 21.8.1 | 995413 |  | 18% | confirmed |  | Filling the gap in between aluminium frame & adjacent RCC/ Brick/ Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Engineer-in-charge complete.Upto 5mm depth and 5 mm width. For ground floor and first floor quarters. | metre | 875 |  |  |  | 0 | 0
21 | 2.10.1.3 mod | 995413 |  | 18% | confirmed |  | Excavating trenches of required width for pipes, cables, etc including excavation for sockets, and dressing of sides, ramming of bottoms, depth upto 1.5 m, including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cm in depth, including consolidating each deposited layer by ramming, watering, etc. and disposing of surplus excavated soil as per direction of the Engineer-in-Charge., within a lead of 1 km :All kinds of soil. Pipes, cables etc. exceeding 80 mm dia. but not exceeding 300 mm dia | metre | 115 |  | Included | 0 | 0 | 0
22 | 2.6.1 mod | 995413 |  | 18% | confirmed |  | Earth work in excavation by mechanical means (Hydraulic excavator)/ manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 1 km and lift upto 1.5 m, as directed by Engineer-incharge. All kinds of soil. | cum | 40 |  | Included | 0 | 0 | 0
23 | 4.1.10 | 995413 |  | 18% | confirmed |  | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level & above plinth level : 1:5:10 (1 cement : 5 coarse sand (zone-III) derived from natural sources : 10 graded stone aggregate 40 mm nominal size derived from natural sources) as per direction of the Engineer-in-Charge. | cum | 18 |  | Included | 0 | 0 | 0
24 | 6.4.2 | 995413 |  | 18% | confirmed |  | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure upto plinth level & above plinth level up to floor V roof level in all shapes and sizes in :Cement mortar 1:6 (1 cement : 6 coarse sand) as per direction of the Engineer-in-Charge. | cum | 26 |  | Included | 0 | 0 | 0
25 | 8.2.2.2 mod | 995413 |  | 18% | confirmed |  | Providing and fixing 18 mm thick gang saw cut, mirror polished, premoulded and prepolished, machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size, approved shade, colour and texture laid over 20 mm thick base cement mortar 1:4 (1 cement : 4 coarse sand), joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing,nosing curing, moulding and machine polishing to edges to give high gloss finish etc. complete at all levels.Area of slab over 0.50 sqm.Granite of any colour and shade as directed by engineer in charge. | sqm | 420 |  | Included | 0 | 0 | 0
26 | 8.4 | 995413 |  | 18% | confirmed |  | Extra for fixing marble /granite stone, over and above corresponding basic item, in facia and drops of width upto 150 mm with epoxy resin based adhesive, including cleaning etc. complete. as per direction of the Engineer-in-Charge. | metre | 200 |  | Included | 0 | 0 | 0
27 | 8.5 | 995413 |  | 18% | confirmed |  | Extra for providing opening of required size & shape for wash basin/ kitchen sink in kitchen platform, vanity counter and similar location in marble/ Granite/ stone work, including necessary holes for pillar taps, gas connections,etc. including moulding, rubbing and polishing of cut edges etc. complete. as per direction of the Engineer-in-Charge. | each | 80 |  | Included | 0 | 0 | 0
28 | 9.48.2 | 995413 |  | 18% | confirmed |  | Providing and fixing M.S. grills of required pattern in frames of windows etc. with M.S. flats, square or round bars etc. including priming coat with approved steel primer all complete.Fixed to openings /wooden frames with rawl plugs screws etc. as per direction of the Engineer-in-Charge. (Item includes welding also wherever necessary for making strong connections.) | kg | 1250 |  | Included | 0 | 0 | 0
29 | 9.21.1 | 995413 |  | 18% | confirmed |  | Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters:35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws as per direction of the Engineer-in-Charge. | sqm | 170 |  | Included | 0 | 0 | 0
30 | 9.23 | 995413 |  | 18% | confirmed |  | Extra for providing lipping with 2nd class teak wood battens 25mm minimum depth on all edges of flush door shutters as per requirement. as per direction of the Engineer-in-Charge.For ground floor and first floor quarters. | sqm | 170 |  |  |  | 0 | 0
31 | 9.96.2 | 995413 |  | 18% | confirmed |  | Providing and fixing aluminium sliding door bolts, ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868), transparent or dyed to required colour or shade, with nuts and screws etc. complete :250x16 mm | each | 90 |  | Included | 0 | 0 | 0
32 | 9.100.1 | 995413 |  | 18% | confirmed |  | Providing and fixing aluminium handles, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade, with necessary screws etc. complete : 125 mm | each | 130 |  | Included | 0 | 0 | 0
33 | 9.101.2 | 995413 |  | 18% | confirmed |  | Providing and fixing aluminium hanging floor door stopper, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade, with necessary screws etc. complete as per direction of the Engineer-in-Charge. Twin rubber stopper | each | 90 |  | Included | 0 | 0 | 0
34 | 9.72.1 | 995413 |  | 18% | confirmed |  | Providing and fixing bright finished brass butt hinges with necessary screws etc. complete as per direction of the Engineer-in-Charge. :125x85x5.5 mm (heavy type) | each | 355 |  | Included | 0 | 0 | 0
35 | 9.97.2 | 995413 |  | 18% | confirmed |  | Providing and fixing aluminium tower bolts, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868 ) transparent or dyed to required colour or shade, with necessary screws etc. complete : 250x10mm | each | 90 |  | Included | 0 | 0 | 0
36 | 9.92.1 | 995413 |  | 18% | confirmed |  | Providing and fixing chromium plated brass handles with necessary screws etc. complete: 125 mm | each | 90 |  | Included | 0 | 0 | 0
37 | 9.127.2 | 995413 |  | 18% | confirmed |  | Providing & Fixing decorative high pressure laminated sheet of plain / wood grain in gloss / matt/ suede finish with high density protective surface layer and reverse side of adhesive bonding quality conforming to IS : 2046 Type S, including cost of adhesive of approved quality. 1mm thick, as per direction of the Engineer-in-Charge.For ground floor and first floor quarters. | sqm | 170 |  | Included | 0 | 0 | 0
38 | 9.117.1 | 995413 |  | 18% | confirmed |  | Providing and fixing factory made uPVC door frame made of uPVC extruded sections having an overall dimension as below (tolerance ±1mm), with wall thickness 2.0 mm (± 0.2 mm), corners of the door frame to be Jointed with galvanized brackets and stainless steel screws, joints mitred and Plastic welded. The hinge side vertical of the frames reinforced by galvanized M.S. tube of size 19 X 19 mm and 1mm (± 0.1 mm) wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturer’s specification and direction of Engineerin- charge. Extruded section profile size 48x40 mm. (Size of each door shall vary from quarters to quarters. Fabrication shall be done accordingly.) | metre | 260 |  | Included | 0 | 0 | 0
39 | 9.118.1 | 995413 |  | 18% | confirmed |  | Providing and fixing to existing door frames (UPVC or PVC), 24 mm thick factory made PVC door shutters made of styles and rails of a uPVC hollow section of size 59x24 mm and wall thickness 2 mm (± 0.2 mm) with inbuilt edging on both sides. The styles and rails mitred and joint at the corners by means of M.S. galvanised/ plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanised M.S. tube of size 20x20 mm and 1 mm (± 0.1 mm) wall thickness. The lock rail made up of 'H' section, a uPVC hollow section of size 100x24 mm and 2 mm (± 0.2 mm) wall thickness, fixed to the shutter styles by means of plastic/ galvanised M.S. 'U' cleats. The shutter frame filled with a uPVC multi-chambered single panel of size not less than 620 mm, having over all thickness of 20 mm and 1 mm (± 0.1 mm) wall thickness. The panels filled vertically and tie bar at two places by inserting horizontally 6 mm galvanised M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer-in-charge. (For W.C. and bathroom door shutter). | sqm | 90 |  | Included | 0 | 0 | 0
40 | 9.53 | 995413 |  | 18% | confirmed |  | Providing 40x5 mm flat iron hold fast 40 cm long including fixing to frame with 10 mm diameter bolts, nuts and wooden plugs and embedding in cement concrete block 30x10x15cm 1:3:6 mix (1 cement : 3 coarse sand : 6 graded stone aggregate 20mm nominal size). as per direction of the Engineer-in-Charge.( Item shall be welded to pressed steel door frames & upvc window frames.) | each | 715 |  |  |  | 0 | 0
41 | 9.46.2 | 995413 |  | 18% | confirmed |  | Providing and fixing chromium plated brass curtain rod having wall thickness of 1.25mm with two chromium plated brass brackets fixed with C.P. brass screws and PVC sleeves etc., wherever necessary complete : 20 mm dia | metre | 170 |  | Included | 0 | 0 | 0
42 | 9.61.1 | 995413 |  | 18% | confirmed |  | Providing M.S. Piano hinges ISI marked IS : 3818 finished with nickel plating and fixing with necessary screws etc., complete. Overall width 35 mm | metre | 150 |  | Included | 0 | 0 | 0
43 | 9.90.2 | 995413 |  | 18% | confirmed |  | Providing and fixing special quality chromium plated brass cupboard locks with six levers of approved quality including necessary screws etc. complete. Size 50 mm as per direction of the Engineer-in-Charge. | each | 70 |  | Included | 0 | 0 | 0
44 | 9.114.1 | 995413 |  | 18% | confirmed |  | Providing and fixing magnetic catcher of approved quality in cupboard / ward robe shutters, including fixing with necessary screws etc. complete. Triple strip vertical type . as per direction of the Engineer-in-Charge. | each | 140 |  | Included | 0 | 0 | 0
45 | 9.96.1 | 995413 |  | 18% | confirmed |  | Providing and fixing aluminium sliding door bolts, ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868), transparent or dyed to required colour or shade, with nuts and screws etc. complete : 300x16 mm as per direction of the Engineer-in-Charge. | each | 55 |  | Included | 0 | 0 | 0
46 | 9.97.4 | 995413 |  | 18% | confirmed |  | Providing and fixing aluminium tower bolts, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868 ) transparent or dyed to required colour or shade, with necessary screws etc. complete : 150x10 mm as per direction of the Engineer-in-Charge. | each | 55 |  | Included | 0 | 0 | 0
47 | 9.100.2 | 995413 |  | 18% | confirmed |  | Providing and fixing aluminium handles, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade, with necessary screws etc. complete : 100 mm as per direction of the Engineer-in-Charge. | each | 55 |  | Included | 0 | 0 | 0
48 | 9.103 | 995413 |  | 18% | confirmed |  | Providing and fixing bright finished brass 100 mm mortice latch and lock, ISI marked, with six levers and a pair of anodised (anodic coating not less than grade AC 10 as per IS : 1868) aluminium lever handles of approved quality with necessary screws etc. complete. as per direction of the Engineer-in-Charge. | each | 140 |  | Included | 0 | 0 | 0
49 | 10.14.1.1 | 995413 |  | 18% | confirmed |  | Providing and fixing pressed steel door frames conforming to IS: 4351, manufactured from commercial mild steel sheet of 1.60 mm thickness, including hinges, jamb, lock jamb, bead and if required angle threshold of mild steel angle of section 50x25 mm, or base ties of 1.60 mm, pressed mild steel welded or rigidly fixed together by mechanical means, including M.S. pressed butt hinges 2.5 mm thick with mortar guards, lock strike-plate and shock absorbers as specified and applying a coat of approved steel primer after pre-treatment of the surface as directed by Engineer-in-charge: Profile B Fixing with adjustable lugs with split end tail to each jamb. For ground floor and first floor quarters. | metre | 450 |  | Included | 0 | 0 | 0
50 | 10.1 | 995413 |  | 18% | confirmed |  | Structural steel work in single section, fixed with or without connecting plate, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. (For overhead cabinet supports- Bracket L angle 50x50x6 as per direction of the Engineer-in-Charge.) | kg | 900 |  |  |  | 0 | 0
51 | 12.41.2 | 995413 |  | 18% | confirmed |  | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion, (i) Single socketed pipes. 110 mm diameter | metre | 115 |  | Included | 0 | 0 | 0
52 | 12.42.6.2 | 995413 |  | 18% | confirmed |  | Providing and fixing on wall face unplasticised - PVC moulded fittings/ accessories for unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion. 110 mm Shoe | each | 15 |  | Included | 0 | 0 | 0
53 | 12.43.2 | 995413 |  | 18% | confirmed |  | Providing and fixing unplasticised -PVC pipe clips of approved design to unplasticised - PVC rain water pipes by means of 50x50x50 mm hard wood plugs, screwed with M.S. screws of required length, including cutting brick work and fixing in cement mortar 1:4 (1 cement : 4 coarse sand) and making good the wall etc. complete. 110 mm | each | 45 |  | Included | 0 | 0 | 0
54 | 13.1.2 | 995413 |  | 18% | confirmed |  | 12 mm cement plaster of mix :1:6 (1 cement: 6 fine sand) as per direction of the Engineer-in-Charge. | sqm | 250 |  | Included | 0 | 0 | 0
55 | 14.82 mod | 995413 |  | 18% | confirmed |  | Dismantling W.C. Pan,Wash basin,kitchen sink of all sizes including all fittings and disposal of dismantled materials i/c malba all complete as per directions of Engineer-in-Charge. Lead upto 1km. | each | 41 |  | Included | 0 | 0 | 0
56 | 14.84 mod | 995413 |  | 18% | confirmed |  | Dismantling 15 to 40 mm dia G.I. pipe including stacking of dismantled pipes (within 1 km lead) as per direction of Engineerin- Charge. Internal work | metre | 600 |  | Included | 0 | 0 | 0
57 | 14.79 | 995413 |  | 18% | confirmed |  | Disconnecting damaged overhead/terrace PVC water storage tank of any size from water supply line and removing from the terrace including shifting at ground level as per direction of Engineer-in-charge. | each | 19 |  | Included | 0 | 0 | 0
58 | 15.19 mod | 995413 |  | 18% | confirmed |  | Dismantling steel work manually/ by mechanical means in built up sections without dismembering and stacking within 1 km lead as per direction of Engineer-in-charge. | kg | 600 |  | Included | 0 | 0 | 0
59 | 15.2.1 mod | 995413 |  | 18% | confirmed |  | Demolishing cement concrete manually/ by mechanical means including disposal of material within 1 km lead as per direction of Engineer - in - charge.Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) | cum | 40 |  | Included | 0 | 0 | 0
60 | 15.52 mod | 995413 |  | 18% | confirmed |  | Dismantling of flushing cistern of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials within 1km lead. as per direction of the Engineer-in-Charge. | each | 40 |  |  |  | 0 | 0
61 | 15.25 mod | 995413 |  | 18% | confirmed |  | Dismantling stone slab flooring laid in cement mortar including stacking of serviceable material and disposal of unserviceable material within 1km lead. as per direction of the Engineer-in-Charge. | sqm | 70 |  | Included | 0 | 0 | 0
62 | 15.44.2 mod | 995413 |  | 18% | confirmed |  | Dismantling G.I. pipes (external work) including excavation and refilling trenches after taking out the pipes, manually/ by mechanical means including stacking of pipes within 1 km lead as per direction of Engineer-in-charge :Above 40 mm nominal bore | metre | 120 |  | Included | 0 | 0 | 0
63 | 15.60 mod | 995413 |  | 18% | confirmed |  | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means, including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 2 km initial lead, for all leads including all lifts involved. | cum | 100 |  | Included | 0 | 0 | 0
64 | 18.8.2 | 995413 |  | 18% | confirmed |  | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same using concrete/plaster, including testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making good the walls etc. 20 mm nominal dia Pipes | metre | 120 |  | Included | 0 | 0 | 0
65 | 18.8.3 | 995413 |  | 18% | confirmed |  | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same using concrete/plaster including testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making good the walls etc. 25 mm nominal dia Pipes | metre | 200 |  | Included | 0 | 0 | 0
66 | 18.8.4 | 995413 |  | 18% | confirmed |  | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same using concrete/plasterincluding testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making good the walls etc. 32 mm nominal dia Pipes | metre | 200 |  | Included | 0 | 0 | 0
67 | 18.9.4 | 995413 |  | 18% | confirmed |  | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. External work in trenches as well as exposed on wall with clamps: 32 mm nominal dia pipes. Depth of trench as directed by engineer-in-charge. | metre | 100 |  | Included | 0 | 0 | 0
68 | 18.9.5 | 995413 |  | 18% | confirmed |  | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. External work in trenches as well as exposed on wall with clamps: 40 mm nominal dia pipes. Depth of trench as directed by engineer-in-charge. | metre | 100 |  | Included | 0 | 0 | 0
69 | 18.9.6 | 995413 |  | 18% | confirmed |  | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. External work in trenches as well as exposed on wall with clamps: 50 mm nominal dia pipes. Depth of trench as directed by engineer-in-charge. | metre | 200 |  | Included | 0 | 0 | 0
70 | 18.21.2.1 | 995413 |  | 18% | confirmed |  | Providing and fixing uplasticised PVC connection pipe with brass unions : 45 cm /60cm length: 15 mm nominal bore as per direction of the Engineer-in-Charge. | each | 51 |  | Included | 0 | 0 | 0
71 | 18.48 | 995413 |  | 18% | confirmed |  | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, IS : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. as per direction of the Engineer-in-Charge. | per litre | 28500 |  | Included | 0 | 0 | 0
72 | 18.75.3 | 995413 |  | 18% | confirmed |  | Providing and fixing PTMT extension nipple for water tank pipe, fittings of approved quality and colour. 25mm nominal bore, weighing not less than 62 gms as per direction of the Engineer-in-Charge. | each | 19 |  | Included | 0 | 0 | 0
73 | 18.62.3 | 995413 |  | 18% | confirmed |  | Providing and fixing PTMT Ball cock of approved quality, colour and make complete with Epoxy coated aluminium rod with L.P./ H.P.H.D. plastic ball. 25 mm nominal bore, 152 mm long, weighing not less than 440 gms as per direction of the Engineer-in-Charge. | each | 19 |  | Included | 0 | 0 | 0
74 | 18.17.1 | 995413 |  | 18% | confirmed |  | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) : 25 mm nominal bore. as per direction of the Engineer-in-Charge. | each | 19 |  | Included | 0 | 0 | 0
75 | 18.17.2 | 995413 |  | 18% | confirmed |  | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) : 32 mm nominal bore. as per direction of the Engineer-in-Charge. | each | 19 |  |  |  | 0 | 0
76 | 18.17.3 | 995413 |  | 18% | confirmed |  | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) : 40 mm nominal bore. as per direction of the Engineer-in-Charge. | each | 19 |  | Included | 0 | 0 | 0
77 | 18.17.4 | 995413 |  | 18% | confirmed |  | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) : 50 mm nominal bore. as per direction of the Engineer-in-Charge. | each | 19 |  | Included | 0 | 0 | 0
78 | 19.4.1.1 | 995413 |  | 18% | confirmed |  | Providing and fixing square-mouth S.W. gully trap class SP-1 complete with C.I. grating brick masonry chamber with water tight C.I. cover with frame of 300 x300 mm size (inside) the weight of cover to be not less than 4.50 kg and frame to be not less than 2.70 kg as per standard design:100x100 mm size P type 19.4.1.1 With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 as per direction of the Engineer-in-Charge. | each | 21 |  | Included | 0 | 0 | 0
79 | 19.7.1.1 | 995413 |  | 18% | confirmed |  | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone-III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5. Shall be provided at suitable depth as directed by Engineer-in-charge | each | 21 |  | Included | 0 | 0 | 0
80 | 19.8.1.1 | 995413 |  | 18% | confirmed |  | Extra for depth for manholes :Size 90x80 cm With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | metre | 10 |  | Included | 0 | 0 | 0
81 | 21.1.1.2 mod | 995413 |  | 18% | confirmed |  | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge (Glazing & paneling to be paid for separately) : For fixed portion Powder coated aluminium (minimum thickness of powder coating 50 micron) . | kg | 200 |  | Included | 0 | 0 | 0
82 | 5.9.19 | 995413 |  | 18% | confirmed |  | Centering and shuttering including strutting, propping etc. and removal of form for Weather shade, Chajjas, corbels etc., including edges as per direction of the Engineer-in-Charge.To be provided in both ground floor & first floor quarters. | sqm | 20 |  | Included | 0 | 0 | 0
83 | 9.168 mod | 995413 |  | 18% | confirmed |  | Providing and fixing cupboard shutter with 19mm thick one side decorative and other side balancing lamination factory pressed BWP grade marine ply as per IS 710 of approved brand including 2mm thick PVC edge banding tape with hot glue by edge bending machine etc. with auto closing spring loaded hinges (hydraulic type) etc. for shutters, drawers, partitions, shelves etc. complete as per direction of Engineer-in-charge. The facial area of the shutter shall be measured for payment which includes shutter, drawers, partitions.(Payment of providing and fixing auto closing hinges shall be paid separately) | sqm | 350 |  | Included | 0 | 0 | 0
84 | 9.170.1 | 995413 |  | 18% | confirmed |  | Providing and fixing stainless steel fancy handle of approved make fixed with SS screws etc. complete as per direction of Engineer-in-charge. 200mm | each | 300 |  | Included | 0 | 0 | 0
85 | 9.171 | 995413 |  | 18% | confirmed |  | Providing and fixing stainless steel soft closing spring hinges at 0 degree hinges (hydraulic type) of approved make/brand to cupboard shutters with full threaded steel screws including making necessary recess in board and finished etc. complete as per direction of Engineer-in-charge. | each | 300 |  |  |  | 0 | 0
86 | 9.172 | 995413 |  | 18% | confirmed |  | Providing and fixing stainless steel soft closing heavy type telescopic drawer channels of approved make 500 mm long with screws etc. complete as per directions of Engineer- in-charge. | one set | 475 |  | Included | 0 | 0 | 0
87 | 9.173 mod | 995413 |  | 18% | confirmed |  | Providing and fixing ready made 304 grade stainless steel Modular kitchen basket and accessories such as right angle basket (Plain Cup & Saucer, plant, Partition, Bottle rack, Thali, Cutlery) kitchen utensil basket, Dinner set basket, kitchen grain basket, Multipurpose basket as per site requirement including finishing (wherever required) and fittings. The same shall be fixed with necessary stainless steel nuts & bolts, Stainless Steel screws & telescopic channel etc. as per direction of Engineer-incharge. (For payment purpose, weight of Stainless steel basket shall be considered including weight of all fixing accessories such as nuts, bolts, fasteners but excluding telescopic basket channels etc. Payment of providing and fixing telescopic channel shall be paid separately) | kg | 200 |  | Included | 0 | 0 | 0
88 | 22.22A | 995413 |  | 18% | confirmed |  | Providing and applying fibre reinforced elastomeric liquid water proofing membrane with resilient acrylic polymers having Sun Reflectivity Index (SRI) of 105 on top of concrete roof in three coats @10.76 litre/ 10 sqm. One coat of self-priming of elastomeric waterproofing liquid (dilution with water in the ratio of 3:1) and two coats of undiluted elastomeric waterproofing liquid (dry film thickness of complete application/system not less than 500 microns). The operation shall be carried out after scrapping and properly cleaning the surface to remove loose particles with wire brushes, complete in all respect as per the direction of Engineer-in-Charge. At roof level of ground floor & first floor. | sqm | 1370 |  | Included | 0 | 0 | 0
89 | 5.2.2 | 995413 |  | 18% | confirmed |  | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. above plinth level up to floor five level, excluding cost of centering, shuttering, finishing and reinforcement :1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources) as per direction of the Engineer-in-Charge. | cum | 10 |  | Included | 0 | 0 | 0
90 | 5.22A.6 | 995413 |  | 18% | confirmed |  | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level upto floor 1 level. Thermo-Mechanically Treated bars of grade Fe-500D or more. as per direction of the Engineer-in-Charge. | kg | 400 |  | Included | 0 | 0 | 0
91 | 2.25 mod | 995413 |  | 18% | confirmed |  | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 1km and lift upto 3 m. | cum | 60 |  | Included | 0 | 0 | 0
92 | 2.27 | 995413 |  | 18% | confirmed |  | Supplying and filling in plinth with sand under floors, including watering, ramming, consolidating and dressing complete. | cum | 20 |  | Included | 0 | 0 | 0
93 | 2.28.1 mod | 995413 |  | 18% | confirmed |  | Surface dressing of the ground including removing vegetation and inequalities not exceeding 15cm deep and disposal of rubbish, lead up to 1km and lift up to 1.5 m. All kinds of soil | sqm | 2000 |  | Included | 0 | 0 | 0
94 | 4.17 | 995413 |  | 18% | confirmed |  | Making plinth protection 50mm thick of cement concrete 1:3:6 (1 cement : 3 coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 20 mm nominal size derived from natural sources) over 75mm thick bed of dry brick ballast 40 mm nominal size, well rammed and consolidated and grouted with fine sand, including necessary excavation, levelling & dressing & finishing the top smooth. | sqm | 100 |  | Included | 0 | 0 | 0
95 | 6.12.2 | 995413 |  | 18% | confirmed |  | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundations and plinth in:cement mortar 1:4 (1 cement : 4 coarse sand) | sqm | 40 |  |  |  | 0 | 0
96 | 17.7.2 | 995413 |  | 18% | confirmed |  | Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste coupling of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require:White Vitreous China Wash basin size 630x450 mm with a single 15 mm C.P. brass pillar tap | each | 20 |  | Included | 0 | 0 | 0
97 | 17.22A | 995413 |  | 18% | confirmed |  | Providing and fixing CP Brass 32mm size Bottle Trap of approved quality & make and as per the direction of Engineer-in-charge. | each | 20 |  | Included | 0 | 0 | 0
98 | 17.2.1 | 995413 |  | 18% | confirmed |  | Providing and fixing white vitreous china pedestal type water closet(European type W.C. pan) with seat and lid, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever), conforming to IS : 7231, with all fittings and fixtures complete, including cutting and making good the walls and floors wherever required :W.C. pan with ISI marked white solid plastic seat and lid | each | 38 |  | Included | 0 | 0 | 0
99 | 17.10.1 | 995413 |  | 18% | confirmed |  | Providing and fixing Stainless Steel A ISI 304 (18/8) kitchen sink as per IS:13983 with C.I. brackets and stainless steel plug 40 mm, including painting of fittings and brackets, cutting and making good the walls wherever required :Kitchen sink with drain board 510x1040 mm bowl depth 250 mm | each | 19 |  | Included | 0 | 0 | 0
100 | 17.31 | 995413 |  | 18% | confirmed |  | Providing and fixing 600x450 mm beveled edge mirror of superior glass (of approved quality) complete with 6 mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | each | 20 |  | Included | 0 | 0 | 0
101 | 17.33 | 995413 |  | 18% | confirmed |  | Providing and fixing 600x120x5 mm glass shelf with edges round off, supported on anodised aluminium angle frame with C.P. brass brackets and guard rail complete fixed with 40 mm long screws, rawl plugs etc., complete | each | 51 |  | Included | 0 | 0 | 0
102 | 18.49.1 | 995413 |  | 18% | confirmed |  | Providing and fixing C.P. brass bib cock of approved quality conforming to IS:8931 :15 mm nominal bore | each | 15 |  | Included | 0 | 0 | 0
103 | 18.51.1 | 995413 |  | 18% | confirmed |  | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms.15 mm nominal bore | each | 19 |  | Included | 0 | 0 | 0
104 | 18.53.1 | 995413 |  | 18% | confirmed |  | Providing and fixing C.P. brass angle valve for basin mixer and geyser points etc of approved quality conforming to IS 8931:15mm nominal bore | each | 78 |  | Included | 0 | 0 | 0
105 | 26.35.1 | 995413 |  | 18% | confirmed |  | Providing and injecting approved grout in proportion recommended by the manufacturer into cracks/honey-comb area of concrete/ masonry by suitable gun/pump at required pressure including cutting of nipples after curing etc. complete as per directions of Engineer-inCharge.(The payment shall be made on the basis of actual weight of approved grout injected.)Stirrer mixed Acrylic Polymer of approved make @ 2% of weight of cement used) modified Cement slurry made with non shrink compound in concrete/RCC work | kg | 100 |  |  |  | 0 | 0
106 | 18.22.1 | 995413 |  | 18% | confirmed |  | Providing and fixing C.P. brass shower rose with 15 or 20 mm inlet :100 mm diameter | each | 38 |  | Included | 0 | 0 | 0
107 | 26.22.1 mod | 995413 |  | 18% | confirmed |  | Providing and fixing false ceiling at all heights with integral densified calcium silicate reinforced with fibre and natural filler false ceiling tiles of Size 595x595mm of approved texture, design and patterns as per CPWD Specification 2019, to be laid in true horizontal level suspended on inter-locking metal T-Grid of hot dipped galvanised iron section of 0.33mmthick (galvanized @ 120 grams per sqm including both sides)comprising of main-T runners of size 24x38 mm of length 3000 mm,cross - T of size 24x27 mm of length 1200 mm and secondary intermediate cross-T of size 24x27 mm of length 600mm to formgrid module of size 600 x 600 mm, suspended from ceiling usinggalvanised mild steel items (galvanizing @ 80 grams per sqm) i.e. 12x50 mm long dash fasteners, 6 mm dia fully threaded hanger rod upto 2000 mm length and L-shape level adjuster of size 76x25x25x1.6 mm fixed with grid and Z cleat of size 25x37x25x1.6mm thick with precut hole on both 25mm flange to pierce into 12x50mm or even bigger size dash fastener if require, fixed with Glavanised iron perimeter wall angle or size 24x24x0.40 mm of length 3000 mm to be fixed on periphey wall / partition with the help of plastic rawl plugs at 450mm center to center and 40 mm long dry wall S.S screws. The workshall be carried out as per specifications, drawing and as per directionsof the Engineer-in- Charge. With 15 mm thick Tegular edged light weight calcium sliciate false ceiling tiles | sqm | 360 |  | Included | 0 | 0 | 0
PART - B NON SCHEDULED
108 | NS-1 | 995413 |  | 18% | confirmed |  | Supplying, laying, jointing, testing and commissioning approved make PVC-U pipe of grade SN4 conforming to IS 15328. The quoted rates shall include necessary fittings like Tees, bends, offsets, etc, including MS angle with GI clamps complete. Work includes jointing pipes from sanitary fitting outlet upto manhole/septic tank inlet whichever necessary as per directions of Engineer-in-charge. 160 mm dia | metre | 100 |  | Included | 0 | 0 | 0
109 | NS-2 | 995413 |  | 18% | confirmed |  | Supplying, laying, jointing, testing and commissioning approved make upvc pipes SWR grade B conforming to IS 13592. The quoted rates shall include necessary fittings like Tees, bends, offsets, etc, including MS angle with GI clamps complete. Work includes jointing pipes from sanitary fitting outlet upto manhole/septic tank inlet whichever necessary as per directions of Engineer-in-charge:110 mm dia. (Item includes clamping on walls with necessary clamps if required, cutting of holes in manhole or septic tank, and including all tools and tackles inculding scaffolding for first floor or wherever necessary. ) | metre | 100 |  | Included | 0 | 0 | 0
110 | NS-3 | 995413 |  | 18% | confirmed |  | Supplying, laying, jointing, testing and commissioning approved make upvc pipes SWR grade B conforming to IS 13592. The quoted rates shall include necessary fittings like Tees, bends, offsets, etc, including MS angle with GI clamps complete. Work includes jointing pipes from sanitary fitting outlet upto manhole/septic tank inlet whichever necessary as per directions of Engineer-in-charge. 75 mm dia. (Item includes clamping on walls with necessary clamps if required, and all tools and tackles inculding scaffolding for first floor or wherever necessary. ) | metre | 100 |  | Included | 0 | 0 | 0
111 | NS-4 | 995413 |  | 18% | confirmed |  | Supplying, laying, jointing, testing and commissioning approved make upvc pipes SWR grade B conforming to IS 13592. The quoted rates shall include necessary fittings like Tees, bends, offsets, etc, including MS angle with GI clamps complete. Work includes jointing pipes from sanitary fitting outlet upto manhole/septic tank inlet whichever necessary as per directions of Engineer-in-charge. 50 mm dia. (Item includes clamping on walls with necessary clamps if required, and all tools and tackles inculding scaffolding for first floor or wherever necessary. ) | metre | 60 |  | Included | 0 | 0 | 0
112 | NS-5 | 995413 |  | 18% | confirmed |  | Providing and fixing minimum 1.5mm thick acrylic sheet of approved quality to toilet doors with screws and washers without damaging the edge of shutter | sqm | 90 |  | Included | 0 | 0 | 0
113 | NS-6 | 995413 |  | 18% | confirmed |  | Providing and fixing 20mm thick commercial boards non decorative type core of block board construction with frame of first class hard wood and well matched commercial three ply veneering with vertical grains or cross bands and face veneers on both faces, fixed over 25mm x 12mm second class teak wood supports in to masonry, all cut edges of commercial boards finished with 20mm x 4mm teak wood beading, including painting with synthetic enamel paint on all surfaces over a coat of approved primer for shelves in cupboards or shoe racks complete in all respects as directed by engineer-in-charge. Area of each board or shelf shall be measured for payment. | sqm | 130 |  | Included | 0 | 0 | 0
114 | NS-7 | 995413 |  | 18% | confirmed |  | Providing and fixing of CP Brass over head arm of length minimum 30 cm for fixing shower through 15mm GI pipe with wall flange | Nos | 21 |  | Included | 0 | 0 | 0
115 | NS-8 | 995413 |  | 18% | confirmed |  | Providing nad fixing stainless steel gratings with or without hole for waste pipe for floor /nahni traps 100mm dia | Nos | 51 |  | Included | 0 | 0 | 0
116 | NS-9 | 995413 |  | 18% | confirmed |  | Supplying and fixing of approved make CP towel rail 600mm long including CP screws etc. complete.Jaquar make | Nos | 51 |  | Included | 0 | 0 | 0
117 | NS-10 | 995413 |  | 18% | confirmed |  | Supplying,installing ,testing and commissioning of approved make 15mm CP health faucet with CP flexible tube 1.0m long,CP crutch,nozzle and 2-way Bib cock with wall flange,fittings etc complete.Jaquar Model No.573 and 041 or Equivalent. | Nos | 38 |  | Included | 0 | 0 | 0
118 | NS-11 | 995413 |  | 18% | confirmed |  | Providing and fixing composite wall mixer with two inlets(for cold and hot water) one tap outlet and common shower outlet with CP brass arm of required length for connection including fittings.Wall flange lever controlled operation complete.Jaquar make | Nos | 21 |  | Included | 0 | 0 | 0
119 | NS-12 | 995413 |  | 18% | confirmed |  | Supplying and fixing of SS AISI-316 Liquid Soap Dispenser(Round shape) 200 ml capacity fixed to the wall with PVC rubber plug with CP brass screws etc complete. (Jaquar/Kich/Roca/Arch/D-line) | each | 20 |  | Included | 0 | 0 | 0
120 | NS-13 | 995413 |  | 18% | confirmed |  | Supplying and fixing of SS AISI-316 soap dish holder (100mm length) fixed to the wall with PVC rubber plug with CP brass screws etc complete.(Jaquar/Kich/Roca/Arch/D-line) | each | 51 |  | Included | 0 | 0 | 0
Electrical works- Proposal for Renovation of B-type, B plus type, C-type & D-type quarters at Udumalpet SS
PART - A SCHEDULE ITEMS
1 | 1.10.2 | 995413 |  | 18% | confirmed |  | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required including all necessary fittings. - Group B | point | 166 |  | Included | 0 | 0 | 0
2 | 1.10.3 | 995413 |  | 18% | confirmed |  | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required including all necessary fittings. - Group C | point | 415 |  | Included | 0 | 0 | 0
3 | 1.10.2 mod | 995413 |  | 18% | confirmed |  | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required including all necessary fittings. - Group B. Single wire lenth/conduit length from Switchbox to lightpoint/fan point/exhaust point etc may vary upto 20m. | point | 116 |  | Included | 0 | 0 | 0
4 | 1.10.3 mod | 995413 |  | 18% | confirmed |  | Wiring for panel light point for false ceiling in community hall with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required including all necessary fittings. - Group C. Single wire lenth/ conduit length from Switchbox to lightpoint/fan point/exhaust point etc may vary upto 45m. | point | 10 |  | Included | 0 | 0 | 0
5 | 1.11 | 995413 |  | 18% | confirmed |  | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. | point | 155 |  | Included | 0 | 0 | 0
6 | 1.11 mod | 995413 |  | 18% | confirmed |  | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. Single wire/conduit length length may vary upto 20m for each point. | point | 39 |  | Included | 0 | 0 | 0
7 | 1.14.1 | 995413 |  | 18% | confirmed |  | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required. - 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | m | 3888.2 |  | Included | 0 | 0 | 0
8 | 1.14.2 | 995413 |  | 18% | confirmed |  | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required. - 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | m | 3588.2 |  | Included | 0 | 0 | 0
9 | 1.14.3 | 995413 |  | 18% | confirmed |  | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required. - 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | m | 1684 |  | Included | 0 | 0 | 0
10 | 1.14.4 | 995413 |  | 18% | confirmed |  | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required. - 2 X 6 sq. mm + 1 X 6 sq. mm earth wire | m | 661 |  | Included | 0 | 0 | 0
11 | 1.19 | 995413 |  | 18% | confirmed |  | Supply, drawing and termination of Co-axial TV cable, RG-6 grade, 0.7mm solid copper conductor, PE insulated, shielded with fine tinned copper braid, protected with PVC sheath | metre | 521 |  | Included | 0 | 0 | 0
12 | 1.21.2 | 995413 |  | 18% | confirmed |  | Supplying and fixing of 25mm sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. | Meter | 5432 |  | Included | 0 | 0 | 0
13 | 1.21.3 | 995413 |  | 18% | confirmed |  | Supplying and fixing of 32mm sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. | Meter | 661 |  | Included | 0 | 0 | 0
14 | 1.24.1 | 995413 |  | 18% | confirmed |  | Supply, Fixing and Termination of Modular type switches and accessories, on the existing modular plate- Telephone socket outlet - Power sockets - Modular Switch 6A | Each | 100 |  | Included | 0 | 0 | 0
15 | 1.24.4 | 995413 |  | 18% | confirmed |  | Supply, Fixing and Termination of Modular type switches and accessories, on the existing modular plate- Telephone socket outlet - Power sockets - 6A, 5 Pin (Universal type-Provision for insertion of both round and Flat pins tops) | Each | 100 |  | Included | 0 | 0 | 0
16 | 1.24.7 | 995413 |  | 18% | confirmed |  | Supply, Fixing and Termination of Modular type switches and accessories, on the existing modular plate- TV Socket (for co-axial cable) | Each | 19 |  | Included | 0 | 0 | 0
17 | 1.24.8 | 995413 |  | 18% | confirmed |  | Supply, Fixing and Termination of Modular type switches and accessories, on the existing modular plate- Modular Bell Push | Each | 19 |  | Included | 0 | 0 | 0
18 | 1.25 | 995413 |  | 18% | confirmed |  | Supplying and fixing two module stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | Each | 88 |  | Included | 0 | 0 | 0
19 | 1.31 | 995413 |  | 18% | confirmed |  | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 A modular socket outlet and 5/6 A modular switch, connections etc. as required. | Each | 191 |  | Included | 0 | 0 | 0
20 | 1.32 | 995413 |  | 18% | confirmed |  | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | Each | 117 |  | Included | 0 | 0 | 0
21 | 1.33 | 995413 |  | 18% | confirmed |  | Supplying and fixing 3 pin, 5 A ceiling rose on the existing junction box/ wooden block including connections etc. as required. | Each | 276 |  | Included | 0 | 0 | 0
22 | 1.34 | 995413 |  | 18% | confirmed |  | Supplying and fixing brass batten/ angle holder including connection etc. as required. | Each | 233 |  | Included | 0 | 0 | 0
23 | 1.38 | 995413 |  | 18% | confirmed |  | Calling Bell of reputed make and model,as per directions of Engineer-in-charge | Each | 19 |  | Included | 0 | 0 | 0
24 | 1.41 | 995413 |  | 18% | confirmed |  | Installation, testing and commissioning of pre-wired, LED fitting of all types, complete with all accessories and tube/lamp etc. directly on ceiling/ wall, including connections with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 271 |  | Included | 0 | 0 | 0
25 | 1.44 | 995413 |  | 18% | confirmed |  | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc. as required. | Each | 92 |  | Included | 0 | 0 | 0
26 | 1.50.1 | 995413 |  | 18% | confirmed |  | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required-Upto 450 mm sweep | Each | 78 |  | Included | 0 | 0 | 0
27 | 1.51 | 995413 |  | 18% | confirmed |  | Extra for fixing the louvers/ shutters complete with frame for a exhaust fan of all sizes | Each | 78 |  | Included | 0 | 0 | 0
28 | Modified 5.2 | 995413 |  | 18% | confirmed |  | Earthing with G.I. earth pipe 3 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | Set | 9 |  | Included | 0 | 0 | 0
29 | 5.15 | 995413 |  | 18% | confirmed |  | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | m | 665 |  | Included | 0 | 0 | 0
30 | DSR AOR BLDC mod | 995413 |  | 18% | confirmed |  | Supply, Installation, Testing and Commissioning of 1200 mm sweep, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, Power Factor not less than 0.9, Service Value (CMM/W) minimum 6.85, Air delivery minimum 215 CMM, 350 RPM (tolerance as per IS : 374- 2019), THD less than 10%, remote or electronic regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase AC Supply, earthing etc. complete as required.Item inludes wiring also, single wire may vary upto 20m for each connection. | No | 90 |  | Included | 0 | 0 | 0
PART - B NON SCHEDULED
1 | NS-1 | 995413 |  | 18% | confirmed |  | Exhaust fan 250 V A.C 50 Hz,200mm (or nearest higher size) sweep, with Louvers, frame. Item includes wiring with 1.5sqmm, single length may vary upto 20m for each fan. | Nos | 51 |  | Included | 0 | 0 | 0
2 | NS-2 | 995413 |  | 18% | confirmed |  | Wall Mounted Fan -450mm sweep. Item includes wiring with 1.5sqmm, single length may vary upto 20m for each fan.Item includes wiring with 1.5sqmm, single length may vary upto 20m for each fan. | Nos | 19 |  | Included | 0 | 0 | 0
3 | NS-3 | 995413 |  | 18% | confirmed |  | Supply and fixing of Square panel light of size 2ftx2ft 36W in false ceiling. | Nos | 25 |  | Included | 0 | 0 | 0
4 | NS-4 | 995413 |  | 18% | confirmed |  | 18 W LED sleek tube light fitting, cool white colour light | No's | 90 |  | Included | 0 | 0 | 0
5 | NS-5 | 995413 |  | 18% | confirmed |  | 9W LED light fitting ( with T5 tube ) , cool white colour light | No's | 85 |  | Included | 0 | 0 | 0
[7 empty] | Community hall | [5 empty] | Revaluation of J column | Tax Calculation | Tax Calculation
PART - A SCHEDULE ITEMS
1 | 26.22.1 mod | 995413 |  | 18% | confirmed |  | Providing and fixing false ceiling at all heights with integral densified calcium silicate reinforced with fibre and natural filler false ceiling tiles of Size 595x595mm of approved texture, design and patterns as per CPWD Specification 2019, to be laid in true horizontal level suspended on inter-locking metal T-Grid of hot dipped galvanised iron section of 0.33mmthick (galvanized @ 120 grams per sqm including both sides)comprising of main-T runners of size 24x38 mm of length 3000 mm,cross - T of size 24x27 mm of length 1200 mm and secondary intermediate cross-T of size 24x27 mm of length 600mm to formgrid module of size 600 x 600 mm, suspended from ceiling usinggalvanised mild steel items (galvanizing @ 80 grams per sqm) i.e. 12x50 mm long dash fasteners, 6 mm dia fully threaded hanger rod upto 1000 mm length and L-shape level adjuster of size 76x25x25x1.6 mm fixed with grid and Z cleat of size 25x37x25x1.6mm thick with precut hole on both 25mm flange to pierce into 12x50mm or even bigger size dash fastener if require, fixed with Glavanised iron perimeter wall angle or size 24x24x0.40 mm of length 3000 mm to be fixed on periphey wall / partition with the help of plastic rawl plugs at 450mm center to center and 40 mm long dry wall S.S screws. The workshall be carried out as per specifications, drawing and as per directionsof the Engineer-in- Charge. With 15 mm thick Tegular edged light weight calcium sliciate false ceiling tiles | sqm | 360 |  | Included | 0 | 0 | 0
[7 empty] | Total for Civil & Electrical Portion |  |  |  | 0
[7 empty] | Total GST Tax as confirmed by Bidder |  |  |  |  | 0
[7 empty] | Grand Total including GST |  |  |  | 0
Click for Sch-4

## Schedule-1
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II.
Schedule- 1 (Schedule of Items and Prices)
To:
C&M Department
Name : | [6 empty] | Power Grid Corporation of India Ltd.
Address : | [6 empty] | SR-II, RHQ
Singanayakkanahalli, Yelahanka
Bangalore
All Price in Indian Rupees
SAC (Service Accounting Codes) | Whether SAC in column '2’ is confirmed. If not indicate applicable the SAC * | Rate of GST applicable ( in %) | Whether rate of GST in column ‘ 4 ’ is confirmed. If not indicate applicable rate of GST * | Sr. No. | DSR 2023 Ref. | Description | Unit | Quantity | Unit Rate in Rs. | Total in Rs. | GST TAX as confirmed by Bidder
995413 |  | 18% | confirmed | 1 | NS | Supplying, filling and compacting stone boulders mixed with sand under foundations, roads, cable trenches, drains etc in layers notexceeding 250mm thickness including ramming, watering compacting | M3 | 100 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 2 | NS | Supplying, filling and compacting CNS material as per specification under floors, foundations, roads, cable trenches, drains etc inlayers not exceeding 200 mm thickness | M3 | 100 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 3 | NS | All civil works for Drains construction of Section D-D including crossings if any as per technical specification and tender drawingscomplete in all respect with all labour and materials. | M | 213.3333 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 4 | NS | All civil works for Drains construction of Section C-C including crossings if any as per technical specification and tender drawingscomplete in all respect with all labour and materials. | M | 320 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 5 | NS | All civil works for Drains construction of Section B-B including crossings if any as per technical specification and tender drawingscomplete in all respect with all labour and materials. | M | 960 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 6 | NS | All civil works for Drains construction of Section A-A including crossings if any as per technical specification and tender drawingscomplete in all respect with all labour and materials. | M | 640 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 7 | NS | RCC culvert crossings including supplying and laying hume pipe 600mm dia of grade (NP-3) excluding concrete as per specification. | M | 16.6667 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 8 | NS | RCC culverts and cable trench crossings including supplying and laying hume pipe 450mm dia of grade (NP-3) excluding concrete as perspecification. | M | 33.3333 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 9 | NS | RCC culverts and cable trench crossings including supplying and laying hume pipe 300mm dia of grade (NP-3) excluding concrete as perspecification. | M | 33.3333 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 10 | NS | RCC culverts and cable trench crossings including supplying and laying hume pipe 250mm dia of grade (NP-3) excluding concrete as perspecification. | M | 66.6667 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 11 | NS | 3.75m wide Bitumen road with earthen shoulder including 100 mm dia RCC Hume Pipe @ 100 metre interval as per drawing and TS (as perDSR item no 16.35 and 16.30.1) and including 225 mm thick WBM in three equal layers of 75 mm each as per CPWD specification. | M2 | 4000 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 12 | NS | Antiweed treatment | M2 | 52000 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 13 | NS | Stone spreading in switchyard excluding PCC | M2 | 52000 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 14 | NS | Misc. Structural steel including rails, embedments, edge protection angles, gratings etc. but excluding the reinforcement steel andsteel for lattice and pipe structures. | MT | 3.06 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 15 | NS | Steel Reinforcement | MT | 372 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 16 | NS | Providing and laying of Reinforced Cement Concrete M25 mix including pre cast, shuttering, Grouting of pockets & underpinning butexcluding steel reinforcement | M3 | 4645 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 17 | NS | Providing and laying of Plain Cement Concrete (PCC) (1:2:4) | M3 | 49.7145 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 18 | NS | Providing and laying of Plain Cement Concrete (PCC) (1:4:8) | M3 | 764.567 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 19 | NS | Excavation in hard rock which require blasting (including chemical blasting and rock excavated using specialized tools) for allfoundation works including stacking, measuring, disposal etc.for all leads and lifts as per technical specification. | M3 | 100 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 20 | NS | Excavation in all kind of soil including rock for all leads and lifts, backfilling, disposal of surplus earth within a lead up to2Km as per technical specification. The surplus earth shall be roughly graded . | M3 | 26206.9424 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 21 | NS | 14.4.3 Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointingwith cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required. : 250 mm dia | M | 66.6667 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 22 | NS | 14.4.2 Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointingwith cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required. : 150 mm dia | M | 33.3333 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 23 | NS | Cable Trench including all types of crossings, all metallic works and sump pit including concrte and reinforcement steel Section 2-2 | M | 500 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 24 | NS | Cable Trench including all types of crossings, all metallic works and sump pit including concrete and reinforcement steel Section2A-2A | M | 533.3333 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 25 | NS | Cable Trench including all types of crossings, all metallic works and sump pit including concrte and reinforcement steel Section 3-3 | M | 333.3333 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 26 | NS | Cable Trench including all types of crossings, all metallic works and sump pit including concrte and reinforcement steel Section 4-4 | M | 266.6667 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 27 | NS | Swtichyard fencing: Providing and fixing fencing of GI barbed wire consisting of galvanized MS tubular posts at 3 m intervals; GIbarded wire shall run horizontally from post to post at a spacing of 300 mm (vertically) and a cross formation in each panel,complete as per technical specification and drawing. | M | 300 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 27 | NS | Providing & laying non-woven Geo-synthetics fabric of minimum 200 GSM in separration layer between sub garde and stone spreading inswitchyard as per Technical Specification and direction of Engineer-in-Charge. | M2 | 52000 |  | Included | 0 | 0 | 0
SPR WORKS
995413 |  | 18% | confirmed | 1 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and for all lift, as directed by Engineer-incharge. All kinds of soil | Cum | 129 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 2 | 2.8.1 | Earth work in excavation by mechanical means (Hydraulic excavator) /manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms,for all lift, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | Cum | 15 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 3 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth,sides of foundations etc. in layers not exceeding 20cm in depth,consolidating each deposited layer by ramming and watering, lead upto 50 m and for all lift . | Cum | 90 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 4 | 2.27 | Supplying and filling in plinth with sand under floors, including watering,ramming, consolidating and dressing complete | Cum | 9 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 5 | 2.34.1 | Supplying chemical emulsion in sealed containers including delivery as specified. Chlorpyriphos/ Lindane emulsifiable concentrate of 20% | Ltr | 60 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 6 | 2.35.3.1 | Diluting and injecting chemical emulsion for POST-CONSTRUCTIONAL anti-termite treatment (excluding the cost of chemical emulsion) :Treatment of soil under existing floors using chemical emulsion @ one litre per hole, 300 mm apart including drilling 12 mm diameter holes and plugging with cement mortar 1 :2 (1 cement : 2 Coarse sand) to match the existing floor: With Chlorpyriphos/Lindane E.C. 20% with 1% concentration | Sqm | 90 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 7 | 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources) | Cum | 6.3 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 8 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:4:8 (1 Cement : 4 coarse sand (zone-III) derived from natural sources : 8 graded stone aggregate 40 mm nominal size derived from natural sources) | Cum | 9.9 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 9 | 4.1 | Providing and laying damp-proof course 40mm thick with cement concrete 1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 12.5mm nominal size derived from natural sources) | Sqm | 15 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 10 | 4.17 | Making plinth protection 50mm thick of cement concrete 1:3:6 (1 cement : 3 coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 20 mm nominal size derived from natural sources) over 75mm thick bed of dry brick ballast 40 mm nominal size, well rammed and consolidated and grouted with fine sand, including necessary excavation, levelling & dressing & finishing the top smooth. | Sqm | 69 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 11 | 5.9 | Centering and shuttering including strutting, propping etc. and removal of form for | [5 empty] | 0 | 0
995413 |  | 18% | confirmed | 12 | 5.9.1 | Foundations, footings, bases of columns, etc. for mass concrete | Sqm | 45 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 13 | 5.9.2 | Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | Sqm | 174 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 14 | 5.9.3 | Suspended floors, roofs, landings, balconies and access platform | Sqm | 129 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 15 | 5.9.5 | Lintels, beams, plinth beams, girders, bressumers and cantilevers | Sqm | 102 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 16 | 5.9.6 | Columns, Pillars, Piers, Abutments, Posts and Struts | Sqm | 120 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 17 | 5.9.16.1 | Edges of slabs and breaks in floors and walls Under 20 cm wide | Metre | 72 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 18 | 5.22.6/5.22A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level.Thermo-Mechanically Treated bars of grade Fe-500D or more. | Kg | 6300 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 19 | 5.33 | Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centering, shuttering, finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete. Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement. | [5 empty] | 0 | 0
995413 |  | 18% | confirmed | 20 | 5.33.1.1 | All works upto plinth level. Concrete of M25 grade with minimum cement content of 330 kg /cum | Cum | 42 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 21 | 5.33.2.1 | All works above plinth level upto floor V level Concrete of M25 grade with minimum cement content of 330 kg /cum | Cum | 25.5 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 22 | 6.4.2 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :Cement mortar 1:6 (1 cement : 6 coarse sand) | Cum | 69 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 23 | 9.147A | Providing and fixing factory made uPVC glazed/wire mesh windows/doors comprising of lead free uPVC multi-chambered frame, sash and mullion/coupler (where ever required) extruded profiles having minimum wall thickness of 1.70 mm for Series R1 and R2 profiles and 2.10 mm for Series R3 and R4 profiles conforming to EN: 12608 in any shape, colour and design duly reinforced with galvanized mild steel section made of required shape & size as per CPWD Specification, uPVC extruded glazing beads, interlocks and Inline sash adaptor (where ever required) of appropriate dimension, EPDM gasket, hardware, SS 304 grade fasteners of minimum 8 mm dia with countersunk head, comprising of matching polyamide PA6 grade sleeve for fixing frame to finished wall as per IS 1367 : Part 1 to 14, plastic packers, plastic caps and necessary stainless steel screws etc. Profile of frame, sash & mullion (if required) shall be mitred cut and fusion welded/mechanically jointed duly sealed at all corners, including drilling of holes for fixing hardware and drainage of water etc. After fixing frame the gap between frame and adjacent finished wall shall be filled with weather proof silicon sealant over backer rod of approved size and quality, all complete as per approved drawing conforming to CPWD specification & direction of Engineer-in-Charge. Section of steel reinforcement and cross sections of uPVC profiles to be as per design approved by Engineer-in-Charge.Wire mesh / Glazing of plain/ toughened/ laminated/ double glass unit with / without high performance coatings as per design requirements and conforming to IS: 3548 & IS: 16231 shall be paid separately. | [5 empty] | 0 | 0
995413 |  | 18% | confirmed | 24 | 9.147.E2.1 | Casement window double panels with fixed mullion with S.S. 304 friction hinges as per size and weight of sash, multi-point locking system, zinc alloy (zamak) powder coated handles.Using R2 series with frame (39mm & above) x (39mm & above) & sash (39mm & above) x(60mm & above) & mullion (39mm & above) x (60mm & above). (Height upto 1.2 metre). | Sqm | 13.5 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 25 | 9.147.F1.1 | Casement door single panel with zinc alloy (zamak) 3D hinges, multi-point locking system with cylinder, zinc alloy (zamak) powder coated handles on both sides. Using R3 series with frame (55 mm & above) x (50mm & above) & sash (55 mm & above) x (85mm & above) (Height upto 2.5 metre). | Sqm | 5.4 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 26 | 9.147.F2.1 | Casement door double panel with French (False) Mullion with zinc alloy (zamak) 3D hinges,multi-point locking system with cylinder, zinc alloy (zamak) powder coated handles on both sides. Using R3 series with frame (55 mm & above) x (50mm & above) & sash (55 mm & above) x (85mm & above) & French (False) mullion (55 mm & above) x (60mm & above). (Height upto 2.5 metre) | Sqm | 10.8 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 27 | 10.1 | Structural steel work in single section, fixed with or without connecting plate, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete.(This shall include angles,MS plate,ISMC,Chequered plate,stiffener,flats etc) | Kg | 600 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 28 | 11.41.2 | Providing and laying vitrified floor tiles in different sizes (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS: 15622, of approved make, in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand), jointing with grey cement slurry @ 3.3 kg/ sqm including grouting the joints with white cement and matching pigments etc., complete.Size of Tile 600x600 mm | sqm | 81 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 29 | 11.46.2 | Providing and laying Vitrified tiles in different sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and conforming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), jointing with grey cement slurry @ 3.3 kg/ sqm including grouting the joint with white cement & matching pigments etc. complete.Size of Tile 600x600 mm | Sqm | 9.6 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 30 | 11.56.1 | Providing and laying Polished Granite stone flooring in required design and patterns, in linear as well as curvilinear portions of the building all complete as per the architectural drawings with 18 mm thick stone slab over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with cement slurry and pointing with white cement slurry admixed with pigment of matching shade including rubbing, curing and polishing etc. all complete as specified and as directed by the Engineer-in-Charge. Polished Granite stone slab colour of Black, Cherry/Ruby Red or equivalent | Sqm | 24 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 31 | 13.1.2 | 12 mm cement plaster of mix :1:6 (1 cement: 6 fine sand) | Sqm | 225 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 32 | 13.11 | 18 mm cement plaster in two coats under layer 12 mm thick cement plaster 1:5 (1 cement : 5 coarse sand) finished with a top layer 6 mm thick cement plaster 1:6 (1 cement : 6 fine sand). | Sqm | 255 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 33 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement : 3 fine sand) | Sqm | 81 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 1 | 13.26 | Providing and applying plaster of paris putty of 2 mm thickness over plastered surface to prepare the surface even and smooth complete. | sqm | 306 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 2 | 13.47.1 | Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade: New work (Two or more coats applied @ 1.43 ltr/10 sqm over and including priming coat of exterior primer applied @ 0.9 ltr/10 sqm) | Sqm | 255 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 3 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | Sqm | 255 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 4 | 13.83.2 | Wall painting with premium acrylic emulsion paint of interior grade, having VOC (Volatile Organic Compound ) content less than 50 grams/ litre of approved brand and manufacture, including applying additional coats wherever required to achieve even shade and colour.Two coats | Sqm | 387 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 5 | 13.85.3 | Applying priming coats with primer of approved brand and manufacture, having low VOC (Volatile Organic Compound ) content.With water thinnable cement primer on wall surface having VOC content less than 50 grams/litre | Sqm | 387 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 6 | 19.6.5 | Providing and laying non-pressure NP2 class (light duty) R.C.C. pipes with collars jointed with stiff mixture of cementmortar in the proportion of 1:2 (1 cement : 2fine sand) including testing of joints etc. complete : 450 mm dia. R.C.C. pipe | Metre | 18 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 7 | 22.7 | Providing and laying integral cement based water proofing treatment including preparation of surface as required for treatment of roofs, balconies, terraces etc consisting of following operations:(a) Applying a slurry coat of neat cement using 2.75 kg/sqm of cement admixed with water proofing compound conforming to IS. 2645 and approved by Engineer-in-charge over the RCC slab including adjoining walls upto 300 mm height including cleaning the surface before treatment. (b) Laying brick bats with mortar using broken bricks/brick bats 25 mm to 115 mm size with 50% of cement mortar 1:5 (1 cement : 5 coarse sand) admixed with water proofing compound conforming to IS : 2645 and approved by Engineerin-charge over 20 mm thick layer of cement mortar of mix 1:5 (1 cement :5 coarse sand ) admixed with water proofing compound conforming to IS : 2645 and approved by Engineerin-charge to required slope and treating similarly the adjoining walls upto 300 mm height including rounding of junctions of walls and slabs. (c) After two days of proper curing applying a second coat of cement slurry using 2.75 kg/ sqm of cement admixed with water proofing compound conforming to IS : 2645 and approved by Engineer-in-charge. (d) Finishing the surface with 20 mm thick jointless cement mortar of mix 1:4 (1 cement :4 coarse sand) admixed with water proofing compound conforming to IS : 2645 and approved by Engineer-in-charge including laying glass fibre cloth of approved quality in top layer of plaster and finally finishing the surface with trowel with neat cement slurry and making pattern of 300x300 mm square 3 mm deep. (e) The whole terrace so finished shall be flooded with water for a minimum period of two weeks for curing and for final test.“All above operations to be done in order and as directed and specified by the Engineer-in-Charge : With average thickness of 120 mm and minimum thickness at khurra as 65 mm. | Sqm | 90 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 8 | 100001721 | Supplying, filling and compacting stone boulders mixed with sand under foundations,roads, cable trenches, drains etc in layers not exceeding 250mm thickness including ramming, watering, compacting etc. | Cum | 18 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 9 | 100001720 | Supplying, filling and compacting CNS material as per specification under floors, foundations, roads, cable trenches, drains | Cum | 30 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 10 | NS-1 | Providing & fixing mesh Arpita or equivalent made out of galvanized iron of nominal thickness 0.35 mm with a zinc coating of 120 gms per sqm along the junctions of masonry and concrete works including fixing,scaffolding,lead & lifts etc. | Sqm | 60 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 11 | NS-2 | Providing & fixing of Float glass panes of nominal thickness 5 mm/5.5mm to uPVC Window & door (weight not less than 12.50 kg/sqm) as per direction of Engineer Incharge | Sqm | 27 |  | Included | 0 | 0 | 0
SPR Electrical Works
995413 |  | 18% | confirmed | 12 | 1.1 | Wiring for light point / fan point / exhaust fan point / call bell point with 1.5 sq mm FR LS PVC insulated copper conductor single core cable in surface / recessed PVC conduit, with modular switch, modular plate, suitable G.I. box and earthing the point with 1.5 sq mm FRLS PVC insulated copper conductor single core cable etc. as required. | [5 empty] | 0 | 0
995413 |  | 18% | confirmed | 13 | 1.10.2 | Group B | Point | 24 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 14 | 1.14.2 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required. 2 x 2.5 sq.mm. + 1 x 2.5 sq. mm earth wire | Meter | 150 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 15 | 1.14.3 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required. 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | Meter | 150 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 16 | 1.21 | Supplying and fixing of following sizes of PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recess conduit as required. | [5 empty] | 0 | 0
995413 |  | 18% | confirmed | 17 | 1.21.1 | 20 mm | Metre | 150 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 18 | 1.27 | Supplying and fixing following size/ modules, GI box along with modular base & cover plate for modular switches in recess as required. | [5 empty] | 0 | 0
995413 |  | 18% | confirmed | 19 | 1.27.3 | 4 Module ( 125 mm x 75 mm) | Each | 6 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 20 | 1.27.4 | 6 Module ( 200 mm x 75 mm) | Each | 3 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 21 | 1.27.5 | 8 Module ( 125 mm x 125 mm) | Each | 3 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 22 | 1.26 | Supplying and fixing blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 6 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 23 | 1.31 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection, painting etc. as required.( For light plugs to be used in non residential buildings.) | Each | 6 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 24 | 1.32 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection, painting etc. as required. | Each | 6 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 25 | 1.57 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess including providing and fixing 25A modular socket outlet and 25A modular SP MCB "C" curve including connection painting etc. as required. | Each | 18 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 26 | 2.4 | Supplying and fixing following way,horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper busbar, neutral busbar, earth bar, din bar, detachable gland plate, interconnections, phosphatized and powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) (Havells/L&T/Schneider/Equivalent makes) | [5 empty] | 0 | 0
995413 |  | 18% | confirmed | 27 | 2.4.1 | 4 way (4 + 12), Double door, horizontal TPN DB. | Each | 6 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 28 | 2.1 | Supplying and fixing of 'C' series, SP MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, 'C' series, miniature circuit breaker, suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required (Havells/L&T/Schneider/Equivalent makes) | [5 empty] | 0 | 0
995413 |  | 18% | confirmed | 29 | 2.10.1 | Single pole | Each | 18 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 30 | 2.11 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc., as required | Each | 30 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 31 | 2.13.2 | Supplying and fixing following rating Four pole 415V isolator in existing MCB DB complete with connections, testing, and commissioning etc., as required - 63 A | Each | 3 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 32 | 2.14.2 | Supplying and fixing following rating double pole (single phase and neutral) 240V RCCB having current sensitivity of 30mA in existing DB complete with testing connections and commissioning etc as required - 40A | Each | 9 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 33 | NS | Supplying, laying (Underground/recessed as required), installation, testing and commissioning of following sizes and core insulated PVC sheathed ,heavy duty, armoured electrical cable with copper conductor for working voltage upto and including 1100 volts (Powergrid Approved make cables) with glands of appropriate size 1.1KV GRADE 4CX16 SQMM (PVC) POWER CABLE ARMOURED | Meter | 900 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 29 | NS | Supplying, laying (Underground/recessed as required), installation, testing and commissioning of following sizes and core insulated PVC sheathed ,heavy duty, armoured electrical cable with copper conductor for working voltage upto and including 1100 volts (Powergrid Approved make cables) with glands of appropriate size 1.1KV GRADE 4CX6 SQMM (PVC) POWER CABLE ARMOURED | Meter | 900 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 30 | NS | Supply, installation, testing and commissioning of 2x2 40 Watts LED Surface Panel Light as per direction of Engineer - Incharge | Each | 24 |  | Included | 0 | 0 | 0
995413 |  | 18% | confirmed | 31 | NS | Supply, installation, testing and commissioning of 16A 415V Receptacles suitable for Termination of 4Cx6 Sqmm PVC Cable as per direction of Engineer - Incharge | Each | 6 |  | Included | 0 | 0 | 0
[6 empty] | Total excluding GST |  |  |  | 0
[6 empty] | Total GST Tax as confirmed by Bidder |  |  |  |  | 0
[6 empty] | Grand Total including GST |  |  |  | 0

## Schedule-2
SR-II/C&M/WC-4332/2025 |  |  |  | Schedule - 2
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II.
(SUMMARY OF TAXES & DUTIES APPLICABLE ON PLANT & EQUIPMENT)
Bidder’s Name and Address (Bidder) : |  |  | To:
Sr.GM , Contracts & Materials Department,
Name : |  |  | Power Grid Corporation of India Ltd.,
Address : |  |  | SRTS-II, RHQ
Singanayakanahalli
Bengaluru-560064
Sl. No. | Item Nos. |  | Total Price (INR) |  | After Discount |  | After MPDiscount
1 | TOTAL GST ON Service |  |  |  | Excise Duty | #REF! | Excise Duty | #REF!
| Total GST for Supply of Services between the Contractor and the Employer (identified in Schedule 1') which are not included in the Unit price as per the provision of the Bidding Documents, as applicable. |  | 0
2 | TOTAL GST ON GOODS
Total GST on AMC charges
Date : | --2025 | Printed Name :
Place : |  | Designation :
Click for Sch-6

## Sch-5 Dis (hidden)
SR-II/C&M/WC-4332/2025 |  |  |  | Schedule - 5
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II.
SUMMARY OF TAXES & DUTIES APPLICABLE ON GOODS
Bidder’s Name and Address (Bidder) : |  |  | To:
Sr.GM , Contracts & Materials Department,
Name : |  |  | Power Grid Corporation of India Ltd.,
Address : |  |  | SRTS-II, RHQ
Singanayakanahalli
Bengaluru-560064
Sl. No. | Item Nos. |  | Total Price (INR)
1 | TOTAL GST ON GOODS |  | #REF!
Total GST for Supply of Goods (inter-alia including Type Test Charges) between the Contractor and the Employer (identified in Schedule 1') which are not included in the Ex-works price as per the provision of the Bidding Documents, as applicable.
2 | TOTAL GST ON SERVICES |  | #REF!
Total GST on Installation Services (Schedule-3) and Training to be imparted in India (Schedule-4)
| GRAND TOTAL [1+2] |  | #REF!
Date : | --2025 | Printed Name :
Place : |  | Designation :
Click for Sch-6

## Sch-3
SR-II/C&M/WC-4332/2025 |  |  | Schedule - 3
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II.
(GRAND SUMMARY)
Bidder’s Name and Address (Bidder) : |  |  | To:
Sr.GM , Contracts & Materials Department,
Name : |  |  | Power Grid Corporation of India Ltd.,
Address : |  |  | SRTS-II, RHQ
Singanayakanahalli
Bengaluru-560064
Sl. No. | Description |  | Total Price (INR)
1 | TOTAL SCHEDULE NO. 1 |  | 0
Ex-works price of Plant and Equipment
2 | TOTAL SCHEDULE NO. 2 |  | 0
RATES AND PRICES : FREIGHT & INSURANCE CHARGES
1 | TOTAL SCHEDULE NO. 3 |  | 0
Service/ Installation
2 | TOTAL SCHEDULE NO. 5 |  | 0
GST
6 | TOTAL SCHEDULE NO. 7 |  | 0
Type Test Charges [Total of this Schedule is included in Schedule - 1 above.]
| GRAND TOTAL [1+2] |  | 0
Date : | --2025 | Printed Name :
Place : |  | Designation :
Click for Sch-7

## Sch-7 (hidden)
SR-II/C&M/WC-4332/2025 |  |  |  |  | Schedule 7
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II. | [7 empty] | As per Lum-sum |  | 0%
(SCHEDULE OF RATES AND PRICES ) | [7 empty] | AS per Percent |  | #REF!
[8 empty] | As per lum-sum on Sch-7 |  | 0%
Bidder’s Name and Address (Bidder) : |  |  | To: |  |  |  |  | As per Percent on Sch-7 |  | #REF!
|  |  | Sr.GM , Contracts & Materials Department, |  |  |  |  | Total Discount |  | #REF!
Name : |  |  | Power Grid Corporation of India Ltd.,
Address : |  |  | SRTS-II, RHQ
|  |  | Singanayakanahalli |  |  |  |  | Multipackage Discount |  | #REF!
Bengaluru-560064
Type test Charges
SL. NO. | Description of Test | Unit | Quantity | Unit Test Charge | Total Test Charges (Rs.) |  | #REF! |  | Total Test Charges After Discount (Rs.) |  | Dis Alert | Total Test Charges After MPD (Rs.)
NOT APPLICABLE
#REF!
#REF!
#REF!
| TOTAL TYPE TEST CHARGES |  |  |  | 0
[8 empty] | Dis Alert | #REF!
Date : | --2025 | Printed Name :
Place : |  | Designation :
Note : | Bidder should indicate the name of test laboratories where type tests are proposed to be conducted
SR-II/C&M/WC-4332/2025
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II. | 0 | 0 |  |  |  | 0
(SCHEDULE OF RATES AND PRICES ) | 0 | 0 |  |  |  | 0
Bidder’s Name and Address (Bidder) : | [5 empty] | 0
| 0 | 0 |  |  |  | 0
Name : |  | 0 |  |  |  | 0
Address : |  | 0 |  |  |  | 0
|  | 0 |  |  |  | 0
|  | 0 |  |  |  | 0
SL. NO. | Description of Test | 0
#REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
Click for Bid Form 2nd Envelope

## Sch-7 Dis (hidden)
SR-II/C&M/WC-4332/2025
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II. | [6 empty] | As per Lum-sum |  | 0%
(SCHEDULE OF RATES AND PRICES : TYPE TEST CHARGES) | [6 empty] | AS per Percent |  | #REF!
[7 empty] | As per lum-sum on Sch-7 |  | 0%
Bidder’s Name and Address (Bidder) : |  |  |  | To: |  |  | As per Percent on Sch-7 |  | #REF!
|  |  |  | Sr.GM , Contracts & Materials Department, |  |  | Total Discount |  | #REF!
Name : |  |  |  | Power Grid Corporation of India Ltd.,
Address : |  |  |  | SRTS-II, RHQ
|  |  |  | Singanayakanahalli |  |  | Multipackage Discount |  | #REF!
Bengaluru-560064
Type Tests on Earthwire
SL. NO. | Description of Test | Unit | Quantity | Unit Test Charge | Total Test Charges (Rs.) |  |  | Total Test Charges After Discount (Rs.) |  | Dis Alert | Total Test Charges After MPD (Rs.)
I | 0
(a) | #REF! | #REF! | #REF! | #REF! | #REF!
(b) | #REF! | #REF! | #REF! | #REF! | #REF!
| Sub-Total (I) |  |  |  | #REF!
| TOTAL TEST CHARGES (I) |  |  |  | #REF!
[7 empty] | Discount Sche-7 | #REF! |  | MPD Sche-7 | #REF!
[7 empty] | Dis Alert | #REF!
Signature :
Date : | --2025 | Printed Name :
Place : |  | Designation :
Common Seal :
Note : | Bidder should indicate the name of test laboratories where type tests are proposed to be conducted
SR-II/C&M/WC-4332/2025
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II. | 0 | 0 |  |  |  | 0
(SCHEDULE OF RATES AND PRICES : TYPE TEST CHARGES) | 0 | 0 |  |  |  | 0
Bidder’s Name and Address (Bidder) : | [5 empty] | 0
| 0 | 0 |  |  |  | 0
Name : |  | 0 |  |  |  | 0
Address : |  | 0 |  |  |  | 0
|  | 0 |  |  |  | 0
|  | 0 |  |  |  | 0
SL. NO. | Description of Test | 0
#REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
Click for Bid Form 2nd Envelope

## Octroi (hidden)
Details of Octroi
Sl No. | Description of Items | Amount on which Octroi is applicable | Rate of Octroi | Octroi
(1) | (2) | (3) | (4) | (5) =(3) x (4)
1 |  |  |  | 0
2 |  |  |  | 0
3 |  |  |  | 0
4 |  |  |  | 0
5 |  |  |  | 0
6 |  |  |  | 0
7 |  |  |  | 0
8 |  |  |  | 0
9 |  |  |  | 0
10 |  |  |  | 0
| Total |  |  | 0
Back to Sch 5

## Entry Tax (hidden)
Details of Entry Tax
Sl No. | Description of Items | Amount on which Entry Tax is applicable | Rate of Entry Tax | Entry Tax
(1) | (2) | (3) | (4) | (5) =(3) x (4)
1 |  |  |  | 0
2 |  |  |  | 0
3 |  |  |  | 0
4 |  |  |  | 0
5 |  |  |  | 0
6 |  |  |  | 0
7 |  |  |  | 0
8 |  |  |  | 0
9 |  |  |  | 0
10 |  |  |  | 0
| Total |  |  | 0
Back to Sch 5

## Other Taxes & Duties (hidden)
Details of Other Taxes & Duties
Sl No. | Description of Items | Amount on which Other Taxes & Duties are applicable | Description of Taxes & Duties | Rate of Taxes & Duties | Amount of Taxes & Duties
(1) | (2) | (3) | (4) | (5) | (6) =(3) x (4)
1 |  |  |  |  | 0
2 |  |  |  |  | 0
3 |  |  |  |  | 0
4 |  |  |  |  | 0
5 |  |  |  |  | 0
6 |  |  |  |  | 0
7 |  |  |  |  | 0
8 |  |  |  |  | 0
9 |  |  |  |  | 0
10 |  |  |  |  | 0
| Total |  |  |  | 0
Back to Sch 5

## Bid Form
SR-II/C&M/WC-4332/2025 |  |  |  |  | Bid Form | Sole Bidder |  | 1 | st |  | 1 | January
[6 empty] | 0 |  | 2 | nd |  | 2 | February
BID FORM (Price bid) | [7 empty] | 3 | rd |  | 3 | March
[8 empty] | 4 | th |  | 4 | April
Bid Proposal Ref. No. | [7 empty] | 5 | th |  | 5 | May
Date : | --2025 | [6 empty] | 6 | th | #VALUE! | 6 | June
[8 empty] | 7 | th | #VALUE! | 7 | July
To: | [7 empty] | 8 | th | #VALUE! | 8 | August
Sr.GM , Contracts & Materials Department, | [7 empty] | 9 | th | #VALUE! | 9 | September
Power Grid Corporation of India Ltd., | [7 empty] | 10 | th |  | 10 | October
SRTS-II, RHQ | [7 empty] | 11 | th |  | 11 | November
Singanayakanahalli | [7 empty] | 12 | th |  | 12 | December
Bengaluru-560064 | [7 empty] | 13 | th
[8 empty] | 14 | th
Name of Contract : |  | Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II. | [5 empty] | 15 | th
Dear Ladies and/or Gentlemen, | [7 empty] | 16 | th
1 | In continuation of Techno commercial part of our Bid, we hereby submit the price schedules of the Bid, both of which shall be read together and in conjunction with each other, and shall be construed as an integral part of our Bid. Accordingly, we the undersigned, offer to design, manufacture, test, deliver, under the above-named package in full conformity with the said Bidding Documents as may be determined in accordance with the terms and conditions of the Bidding Documents. |  |  |  |  | In continuation of Techno commercial part of our Bid, we hereby submit the price schedules of the Bid, both of which shall be read together and in conjunction with each other, and shall be construed as an integral part of our Bid. Accordingly, we the undersigned, offer to design, manufacture, test, deliver, under the above-named package in full conformity with the said Bidding Documents | as may be determined in accordance with the terms and conditions of the Bidding Documents. | 17 | th
| The above amounts are in accordance with the price schedules attached herewith and are made part of this bid. | [6 empty] | 18 | th
2 | Price Schedules | [6 empty] | 19 | th
2.1 | In line with the requirements of the Bidding documents, we enclose herewith the following Price Schedules, duly filled - in as per your proforma: | [6 empty] | 20 | th
| Schedule 1 |  | Plant and Equipment |  |  |  |  | 21 | st
| Schedule 2 |  | Local Transportation, In-transit Insurance, loading and unloading |  |  |  |  | 22 | th
| Schedule 4 |  | Training charges for training to be imparted. |  |  |  |  | 24 | th
| Schedule 5 |  | Taxes and Duties not included in Schedule 1 |  |  |  |  | 25 | th
| Schedule 6 |  | Grand Summary [Schedule 1to 5] |  |  |  |  | 26 | th
| Schedule 7 |  | Break-up of Type Test Charges for Type Tests to be conducted |  |  |  |  | 27 | th
2.2 | We are aware that the Price Schedules do not generally give a full description of the Work to be performed under each item and we shall be deemed to have read the Technical Specifications and other sections of the Bidding Documents and Drawings to ascertain the full scope of Work included in each item while filling-in the rates and prices. We agree that the entered rates and prices shall be deemed to include for the full scope as aforesaid, including overheads and profit. | [6 empty] | 28 | th
2.3 | We declare that as specified in Clause 11.5, Section –II:ITB, Vol.-I of the Bidding Documents, prices quoted by us in the Price Schedules shall be in line with the bid documents & Contract Agreement. | [6 empty] | 29 | th
2.4 | We understand that in the price schedules, where there are errors between the total of the amounts given under the column for the price Breakdown and the amount given under the Total Price, the former shall prevail and the latter will be corrected accordingly. We further understand that where there are discrepancies between amounts stated in figures and amounts stated in words, the amount stated in words shall prevail. Similarly, any discrepancy in the total bid price and that of the summation of Schedule price (price indicated in a Schedule indicating the total of that schedule), the total bid price shall be corrected to reflect the actual summation of the Schedule prices. | [6 empty] | 30 | th
2.5 | We declare that items left blank in the Schedules will be deemed to have been included in other items. The TOTAL for each Schedule and the TOTAL of Grand Summary shall be deemed to be the total price for executing the Facilities and sections thereof in complete accordance with the Contract, whether or not each individual item has been priced. | [6 empty] | 31 | st
3 | We confirm that except as otherwise specifically provided our Bid Prices in this Second Envelope include all taxes, duties, levies and charges as may be assessed on us/our Associate (applicable for Foreign Bidder), our Sub-Contractor/Sub-Vendor or their employees by all municipal, state or national government authorities in connection with the Facilities, in and outside of India.
3.1 | 100% of applicable Taxes and Duties i.e GST, which are payable by the Employer under the Contract, shall be reimbursed by the Employer on production of satisfactory documentary evidence by the Contractor in accordance with the provisions of the Bidding Documents.
3.2 | We further understand that notwithstanding 3.0 above, in case of award on us, you shall also bear and pay/reimburse to us, GST applicable on supplies by us to you, imposed on the Plant & Equipment to be incorporated into the Facilities of the Price Schedule in this Second Envelope; by the Indian Laws.
3.3 | We confirm that we have also registered/we shall also get registered in the GST Network with a GSTIN, in all the states where the project is located and the states from which we shall make our supply of goods.
4 | # (For Joint Venture only) We, the partners of Joint Venture submitting this bid, do agree and confirm that in case of Award of Contract on the Joint Venture, we shall be jointly and severally liable and responsible for the execution of the Contract in accordance with Contract terms and conditions.
5 | We, hereby, declare that only the persons or firms interested in this proposal as principals are named here and that no other persons or firms other than those mentioned herein have any interest in this proposal or in the Contract to be entered into, if the award is made on us, that this proposal is made without any connection with any other person, firm or party likewise submitting a proposal is in all respects for and in good faith, without collusion or fraud.
Thanking you, we remain,
Yours faithfully,
For and on behalf of
Signature :
Date : | --2025 |  |  | Printed Name :
Place : |  |  |  | Designation :
Common Seal :
Please provide additional information of the Bidder
Business Address :
Country of Incorporation :
State/Province to be indicated :
Name of Principal Officer :
Address of Principal Officer :
Note: Bidders may note that no prescribed proforma has been enclosed for Attachment 2 : Power of Attorney. Bidders may use their own proforma for furnishing the required information with the bid.
* * *
Back to Cover Page

## Q & C (2) (hidden)
STATEMENT OF QUOTED / CORRECTED PRICES
All Figures are in Rupees
Bidder |  | #VALUE!
Sl. No. | Price Component | Quoted Price | Corrected Price
1 | TOTAL SCHEDULE NO. 1:Ex-Works Price of Plant and Equipment including Type Test Charges | 0 |  | 0
2 | TOTAL SCHEDULE NO.2: Local Transportation, Insurance and other Incidental Services. | 0 |  | 0
3 | TOTAL SCHEDULE NO.3: Installation Charges | #REF! |  | #REF!
4 | TOTAL SCHEDULE NO.4: Training Charges | Not Applicable |  | Not Applicable
5 | TOTAL BID PRICE: (Excluding Taxes & Duties) | #REF! |  | #REF!
6 | DISCOUNT | #REF! |  | #REF! | #REF!
7 | NET BID PRICE (Excluding Taxes & Duties) | #REF! |  | #REF!
8 | TAXES & DUTIES PAYABLE ADDITIONALLY
| A) EXCISE DUTY | #REF! |  | 0
| B) CENTRAL SALES TAX | #REF! |  | 0
| C) VAT | #REF! |  | 0
| D) ENTRY TAX / OCTROI | #REF! |  | 0
E) OTHERS
| F) TOTAL TAXES & DUTIES | #REF! |  | 0
8 | TOTAL BID PRICE (INCLUDING TAXES & DUTIES) | #REF! |  | #REF!
9 | TOTAL SCHEDULE NO.7: Type Test Charges [Total of this Schedule is included in Schedule-1 above] | 0 |  | 0
I) | Bidder has indicated the following taxes and duties additionally applicable for their bid:
| #REF! |  |  |  | Excise Duty | #REF! | #REF!
| #REF! |  |  |  | CST | #REF! | #REF!
| #REF! |  |  |  | VAT | #REF! | #REF!
| #REF! |  |  |  | Entry Tax/ Octroi | #REF! | #REF!
| Others as |  |  |  | Others
II) | With regard to Entry Tax, it may be mentioned that the substations covered under the subject pacakge falls in State of MP, where an entry tax @ 2% of Purchase Price is applicable. In view of the above, the taxes and duties inter-alia including entry tax applicable for the bids are calculated :
a) | Ex-Works Price of Direct Supplies (after discount, if any) |  | Rs. | 0
b) | Excise Duty, as applicable on (a) above at the rate : | 10% | Rs. | 0
c) | Amount on which Sales Tax is applicable | 0 |  | 0
d) | CST, as applicable on (a) + ED (b) above at the rate : | 2% | Rs. | 0
e) | VAT, as applicable on (a) + ED (b) above at the rate : | 1% |  | 0
f) | Others [……………………………………………] |  | Rs.
g) | Purchase Price for Entry Tax (Total Ex-Works+F&I+ED+CST+Others) |  | Rs. | 0
h) | Entry Tax, as applicable on (e) above at the rate : |  | Rs. | 0
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II. |  | Statement of Quoted / Corrected Prices |  | Page
Spec. No. | SR-II/C&M/WC-4332/2025

## Q & C (hidden)
STATEMENT OF QUOTED / CORRECTED PRICES
All Figures are in Rupees
Bidder
Sl. No. | Price Component | Quoted Price | Corrected Price
1 | TOTAL SCHEDULE NO. 1:Ex-Works Price of Plant and Equipment including Type Test Charges | 0 |  | 0
2 | TOTAL SCHEDULE NO.2: Local Transportation, Insurance and other Incidental Services. | 0 |  | 0
3 | TOTAL SCHEDULE NO.3: Installation Charges | #REF! |  | #REF!
4 | TOTAL SCHEDULE NO.4: Training Charges | Not Applicable |  | Not Applicable
5 | TOTAL BID PRICE: (Excluding Taxes & Duties) | #REF! |  | #REF!
6 | DISCOUNT | #REF! |  | #REF!
7 | NET BID PRICE (Excluding Taxes & Duties) | #REF! |  | #REF!
8 | TAXES & DUTIES PAYABLE ADDITIONALLY
| A) EXCISE DUTY | #REF! |  | #REF!
| B) CENTRAL SALES TAX /VAT | #REF! |  | #REF!
| C) ENTRY TAX / OCTROI | #REF! |  | #REF!
| D) OTHERS | #REF! |  | 0
| E) TOTAL TAXES & DUTIES | #REF! |  | #REF!
8 | TOTAL BID PRICE (INCLUDING TAXES & DUTIES) | #REF! |  | #REF!
9 | TOTAL SCHEDULE NO.7: Type Test Charges [Total of this Schedule is included in Schedule-1 above] | 0 |  | 0
I) | Bidder has indicated the following taxes and duties additionally applicable for their bid:
a) | Excise Duty |  | Rs. | #REF!
b) | CST /VAT |  | Rs. | #REF!
c) | Entry Tax / Octroi |  | Rs. | #REF!
d) | Others |  | Rs. | #REF!
II) | Bidder has offered following discount(s)
III) | With regard to Entry Tax, it may be mentioned that the substations covered under the subject pacakge falls in State of MP, where an entry tax @ 1% of Purchase Price is applicable. In view of the above, the taxes and duties inter-alia including entry tax applicable for the bids are calculated : |  |  |  | Details of dicounts
a) | Ex-Works Price of Direct Supplies (after discount, if any) |  | Rs. | #REF! | Gross LS | #REF! | #REF! | #REF! | Gross % | #REF! | #REF! | #REF!
b) | Excise Duty @ 10.3% of (a) above |  | Rs. | #REF! |  |  |  | #REF! |  |  |  | #REF!
c) | CST / VAT @ 2% of Ex-Works of Direct Supplies (a) + ED (b) above |  | Rs. | #REF! | Sch-1 Direct LS | #REF! | #REF! | #REF! | Sch-1 Direct % | #REF! | #REF! | #REF!
d) | Others |  | Rs. |  | Sch-1 BO LS | #REF! | #REF! | #REF! | Sch-1 BO % | #REF! | #REF! | #REF!
e) | Purchase Price for Entry Tax (Total Ex-Works+F&I+ED+CST+Others) |  | Rs. | #REF! | Sch-2 LS | #REF! | #REF! | #REF! | Sch-2 % | #REF! | #REF! | #REF!
f) | Entry Tax @ 1% of (e) above |  | Rs. | #REF! | Sch-3 LS | #REF! | #REF! | #REF! | Sch-3 % | #REF! | #REF! | #REF!
[5 empty] | Sch-7 LS | #REF! | #REF! | #REF! | Sch-7 % | #REF! | #REF! | #REF!
Construction of 220 kV Bays including SPR Rooms, common facilities for the augmentation portion of 400/220 kV Gadag-II PS under “System strengthening at Koppal-II and Gadag-II for integration of RE generation projects” under TBCB SR-II. |  | Statement of Quoted / Corrected Prices |  | Page | Different Manner | #REF!
[5 empty] | Text for Discount | #REF!
#REF!
#REF!

## N to W (hidden)
0
Rs. Zero Only
0
0
0
0
0
0
1 | One
2 | Two
3 | Three
4 | Four
5 | Five
6 | Six
7 | Seven
8 | Eight
9 | Nine
10 | Ten
11 | Eleven
12 | Twelve
13 | Thirteen
14 | Fourteen
15 | Fifteen
16 | Sixteen
17 | Seventeen
18 | Eighteen
19 | Nineteen
20 | Twenty
21 | Twenty One
22 | Twenty Two
23 | Twenty Three
24 | Twenty Four
25 | Twenty Five
26 | Twenty Six
27 | Twenty Seven
28 | Twenty Eight
29 | Twenty Nine
30 | Thirty
31 | Thirty One
32 | Thirty Two
33 | Thirty Three
34 | Thirty Four
35 | Thirty Five
36 | Thirty Six
37 | Thirty Seven
38 | Thirty Eight
39 | Thirty Nine
40 | Forty
41 | Forty One
42 | Forty Two
43 | Forty Three
44 | Forty Four
45 | Forty Five
46 | Forty Six
47 | Forty Seven
48 | Forty Eight
49 | Forty Nine
50 | Fifty
51 | Fifty One
52 | Fifty Two
53 | Fifty Three
54 | Fifty Four
55 | Fifty Five
56 | Fifty Six
57 | Fifty Seven
58 | Fifty Eight
59 | Fifty Nine
60 | Sixty
61 | Sixty One
62 | Sixty Two
63 | Sixty Three
64 | Sixty Four
65 | Sixty Five
66 | Sixty Six
67 | Sixty Seven
68 | Sixty Eight
69 | Sixty Nine
70 | Seventy
71 | Seventy One
72 | Seventy Two
73 | Seventy Three
74 | Seventy Four
75 | Seventy Five
76 | Seventy Six
77 | Seventy Seven
78 | Seventy Eight
79 | Seventy Nine
80 | Eighty
81 | Eighty One
82 | Eighty Two
83 | Eighty Three
84 | Eighty Four
85 | Eighty Five
86 | Eighty Six
87 | Eighty Seven
88 | Eighty Eight
89 | Eighty Nine
90 | Ninety
91 | Ninety One
92 | Ninety Two
93 | Ninety Three
94 | Ninety Four
95 | Ninety Five
96 | Ninety Six
97 | Ninety Seven
98 | Ninety Eight
99 | Ninety Nine
100 | One Hundred