| Sl. No. | VOL./SEC/ CLAUSE No. | EXISTING TEXT | TO BE AMENDED AS |
| --- | --- | --- | --- |
|  | Vol. II-Technical Specification, Section-Project, Rev 00 Clause 3.1.A.b) (i) | Clause: 3.1.A.b) (i) One (1) No. 3-phase, 3150A, SF6 insulated circuit breaker without PIR and with CSD (CSD is available in existing Tie bay of Nakodar-tie-ICT2 diameter which shall be dismantled and shifted to this Tie Module) complete with operating mechanism. … | Clause to be Modified as: Clause: 3.1.A.b) (i) One (1) No. 3-phase, 3150A, SF6 insulated circuit breaker without PIR and with CSD (CSD is available in existing Tie bay of Nakodar-tie-ICT2 diameter which shall be dismantled and shifted to this Tie Module) complete with operating mechanism. … |
|  | Vol. II-Technical Specification, Section-Project, Rev 00 Clause 10.2 | Clause: 10.2 The CSD available in existing tie bay of Nakodar-Tie-ICT 2 diameter shall be dismantled and re-erected and commissioned in the new GIS Tie bay module. Any supply /service needed for successful commissioning of CSD with the new GIS Tie bay module shall be included in the scope of the contractor. | Clause Deleted. |
|  | Vol. II-Technical Specification, Section-Project, Rev 00 Clause 3.1.G.(ii) | Clause: 3.1.G.(ii) - The existing 765/400/220kV Moga (PG) Substation is equipped with substation automation system of M/s. ALSTOM make based on IEC 61850. Augmentation of above mentioned existing Substation automation, based on IEC 61850 for following bays, under present scope (bay as defined in technical specification, Sec.-Substation Automation). - 400kV Bay: Main bays – 2 Nos. (viz. Bus Sectionaliser Bays) - 400kV Bay: Tie bays – 1 No. In the present scope, bidder will provide BCUs required for 400kV bays including all necessary hardware and software to integrate with the existing Substation Automation System. The Scope of bidder shall include but not limited to integration of IEDs under present scope of augmentation with existing substation automation (which is based on IEC 61850) and compatibility enhancement of same as required including hardware (if any required), updating of system database, displays, development of additional displays and reports as per requirement. | Clause to be Modified as: Clause: 3.1.G.(ii) - The existing 765/400/220kV Moga (PG) Substation is equipped with substation automation system of M/s. ALSTOM make based on IEC 61850. Augmentation of above mentioned existing Substation automation, based on IEC 61850 for following bays, under present scope (bay as defined in technical specification, Sec.-Substation Automation). - 400kV Bay: Main bays – 2 Nos. (viz. Bus Sectionaliser Bays) - 400kV Bay: Tie bays – 1 No. In the present scope, bidder will provide BCUs required for 400kV bays including all necessary hardware and software to integrate with the existing Substation Automation System. Further, all necessary augmentation of existing SAS for fully integrating both the Bus sections (AIS & GIS) including its associated feeders through necessary modifications/updation along with supply of any additional items for complete automation of both bus sections and its feeders as per Technical Specification: Section-Substation Automation System is in the present scope of work. The Scope of bidder shall include but not limited to integration of IEDs under present scope of augmentation with existing substation automation (which is based on IEC 61850) and compatibility enhancement of same as required including hardware (if any required), updating of system database, displays, development of additional displays and reports as per requirement. |