| Clarification No.-1 (Technical Portion) to the Bidding Documents for GIS Substation Extension Package-SS-58 for extension of 400kV Moga substation under Transmission scheme for controlling high loading and high short circuit level at Moga substation; Spec. No.: CC-CS/980-NR2/GIS-4081/3/G3 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sl. No. | VOLUME/SEC No. | CLAUSE Ref (if any) | Relevant Clause | Description of Query | Reply |
|  | VOLUME-II Section of Project Page 5 of 13 b) Tie bay module |  | - One (1) No. 3-phase, 3150A, SF6 insulated circuit breaker without PIR and with CSD (CSD is available in existing Tie bay of Nakodar-tie-ICT2 diameter which shall be dismantled and shifted to this Tie Module) complete with operating mechanism. | Which company manufactured the existing Tie bay of Nakodar-tie-ICT 2 diameter? Is it GIS or AIS type? And Which company manufactured the CSD? Is it located in GIS/AIS LCC, or in a centralized room like control room? | Refer S. No. 1 & 2 of Amendment No.2 |
|  | VOLUME-II GIS Rev 5A |  | 27.4. Portable Partial Discharge(PD) monitoring system (Shall generally applicable for 220kV&132 kV) 27.5 Online Partial Discharge Monitoring System (Applicable for 765kV& 400 kV GIS) & Price Schedules SS01 | It is said to be online partial discharge monitoring system for 420 kV GIS in GIS Rev 5A. However, in the Price Schedules SS01, it is only said to be 1 set of Partial discharge monitoring system for 220kV GIS station. Kindly ask you to confirm whether Portable Partial discharge monitoring system is applicable for these 400kV GIS bays of Moga Extension station. | Portable Partial discharge monitoring system shall be applicable under present scope. |
|  | 02-Second Envelope Price Schedules_SS58 | PDM |  | This is a 400kVGIS substation, but in BOQ the description for PDM is "PDM system for 220kV Substation". Please confirm it should be Portable PDM Kit or On-line PDM equipment. | Refer our reply to S. No. 2 above. |
|  | GIS rev_5A | Spares |  | This is an extension substation, but 400kVGIS is a new project. So the quantity of spares for 400kVGIS in Annexure 10 in GIS rev_5A shall be as per "New S/S" or "Extn. S/S". | Spares for GIS shall be corresponding to Extension S/S in Annexure-10 Rev.1 of GIS Rev.5A. |