| Clarification No.-1 (Technical Portion) to the Bidding Documents for GIS Substation Extension Package-SS-58 for extension of 400kV Moga substation under Transmission scheme for controlling high loading and high short circuit level at Moga substation; Spec. No.: CC-CS/980-NR2/GIS-4081/3/G3 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sl. No. | VOLUME/SEC No. | CLAUSE Ref (if any) | Relevant Clause | Description of Query | Reply |
|  | Layout (drawing C/ENGG-SS/NR/ BUS-SPLIT/MOGA-EXTN/400kV/GA/00 Sheet 1 OF 2) | - | Conductor details. | Please furnish the existing conductor details of 400kV switchyard bays. | Available major relevant drawings and details of existing old substation installations are enclosed with bidding documents. Other drawings & details, if available will be shared with the successful bidder during detailed engineering. However bidders are requested to visit the substation sites in accordance to clause no 3.5 of section project, technical specification. |
|  | Layout (drawing C/ENGG-SS/NR/ BUS-SPLIT/MOGA-EXTN/400kV/GA/00 Sheet 1 OF 2) | - | Sectional Drawings. | Please provide the sectional detail / Drawing of all the bays which are to be modified under present scope. | Available major relevant drawings and details of existing old substation installations are enclosed with bidding documents. Other drawings & details, if available will be shared with the successful bidder during detailed engineering. However bidders are requested to visit the substation sites in accordance to clause no 3.5 of section project, technical specification. |
|  | Layout (drawing C/ENGG-SS/NR/ BUS-SPLIT/MOGA-EXTN/400kV/GA/00 Sheet 1 OF 2) |  |  | Please refer the snap of Layout. Please clarify the scope of rotating the isolator and provide the BoQ item of dismantling and erection for same. | The scope of work involves positioning the Earthswitch of ISO with respect to connection of the respective feeder with the bus section mentioned in TS, if required as per site condition. No separate BOQ line item is envisaged, it is deemed to be included in the present scope of work. Bidder shall quote accordingly. |
|  | Layout (drawing C/ENGG-SS/NR/TR. SEZ/400kV/220kV BHADLA-Extn/GA/01) | - | SPR Location. | We understand that location of SPR shown in Layout is indicative only which shall be finalised during detailed engineering. Please confirm. | Bidder’s understanding is correct. |
|  | Bid price schedule - item no. 140 |  | Erection Hardware for 400kV D type layout- bus work (for one diameter)as per technical specification | We understand that line item covers all the Bus work related under present package instead of Bus for one dia. Please confirm. | Kindly refer clause 10.3 of Section Project. Bidder shall comply with requirements of Technical Specification. |
|  | General | - | Cable trench route | Please provide the existing cable trench layout drawing. | Available major relevant drawings and details of existing old substation installations are enclosed with bidding documents. Other drawings & details, if available will be shared with the successful bidder during detailed engineering. However bidders are requested to visit the substation sites in accordance to clause no 3.5 of section project, technical specification. |
|  | General | - | Guy Insulators | Guy Insulator not envisaged for the drop connection of SF6 to Air Bushing due to space constraint and as per present standard practice. Please confirm. | Guy insulators are not envisaged under 400kV System. |
|  | Technical Specification, Section – Project, Rev 0 | Clause no- 3.1-G.ii, page no 6 of 13 | In the present scope, bidder will provide BCUs required for 400kV bays including all necessary hardware and software to integrate with the existing Substation Automation System. | i) We understand that our scope is limited to totally 3 nos. ( 1 for TIE + 2 for BS) BCU & it's integration with existing SAS system as per BPS. Any other SAS augmentation including any hardwired modification due to conversion of AIS BUS section-1 to GIS BUS shall not be in our scope. ii) Dedicated Bus voltage monitoring for Bus section is not envisaged. Kindly confirm. | Refer S. No. 3 of Amendment No.2 |
|  | Technical Specification, Section – Project, Rev 0 | Clause no- 3.1-G.iii-a/b, page no 6/7 of 13 | a. For bays under present scope Complete Relay & Protection System as per Section Control and Relay Panel of the Technical Specifications. The existing 400 kV Bus bar protection relay is ALSTOM make MSAH34 (High Impedance type). The Bus Bar Protection for feeders of Bus Section-2 shall be done using existing Bus Bar protection relay mentioned above. | There is no line item for the Existing bus bar augmentation work. Kindly include the same. | Since the bus bar for existing Bus section-2 is existing at site, necessary modification/ updation/rearrangement required for Bus bar protection of the feeders to be connected to Bus Section-2 is included in present scope. The same shall be quoted under line item for main Bus bar panel. Other minor items if required for Bus Bar Protection augmentation is also to be considered. Bidder is to quote accordingly |
|  | Technical Specification, Section – Project, Rev 0 | Clause no- 3.1-G.iii-c, page no 7 of 13 | For new Bus Section-1, complete Bus Bar Protection as per Technical Specification shall be provided and all feeders of Bus Section-1 shall be integrated with this new Bus Bar Scheme is under present scope. | i) We propose centralized bus-bar scheme for Bus-Section-1. And we presume LBB protection for bays connected to high impedance Bus-bar is already existing and no new LBB protection is required. ii) LBB augmentation scheme/ modification scheme for new system - line item in not mentioned in BPS. Kindly confirm the requirement. | In case bidder offers Centralised Bus bar protection meeting TS for Bus Section-1, existing LBB relays at site may be used for respective feeders. However, all necessary modification/updation in the LBB Schemes of bays in both the bus sections: 1 & 2 (as applicable) including supply of additional items (if any) for complete Relay & Protection System as per TS is included in the present scope of work. |
|  | Technical Specification, Section – Project, Rev 0 | Clause no- 3.1-G.iii-d, page no 7 of 13 | Further necessary cabling/wiring modification to disintegrate the feeders of Bus Section-1 from existing Bus bar protection scheme and coordinate the protection system respective feeders of each Bus Section with the respective Bus Bar protection system is included under present scope. Supply of necessary cables, trip relays, auxiliary relays/contactors, bay units, etc. for completion of same is included under present scope of work. | i) We understand that there is no requirement of CMR (Contact Multiplier Relay), existing equipment contacts shall be used for status/monitoring. iii) Kindly provide acceptance to utilize existing control cables wherever possible. Kindly confirm. | i) Bidder to quote as per provisions of bidding document. iii) Use of existing control cable shall be subject to availability & clearance by site. However, in case of requirement of new/ additional cables, same shall be supplied at no additional cost implications to POWERGRID. |
|  | Technical Specification, Section – Project, Rev 0 | Clause no- 10.2 | The CSD available in existing tie bay of Nakodar-Tie-ICT 2 diameter shall be dismantled and re-erected and commissioned in the new GIS Tie bay module. | i) Kindly provide details of existing CSD make. | Refer S. No. 1 & 2 of Amendment No.2 |
|  | SUBSTATION PACKAGE – SS58: 765/400/220KV MOGA (PG) EXTENSION | SLD | TIE BAY (2) - for ICT-2 interconnection with BUS-IIA | i) We understand that Protection panel for the same is not mentioned in BPS. Kindly include. ii) We understand that PMU data for new bus sections shall be catered by existing PMU's only. | i) Breaker Control Panel for Tie Bay is already considered in BPS along with Breaker Control Panel for bus sectionaliser bays. Protection panels for ICT-2 already exist at site. ii) Bidder’s understanding is correct. |
|  | General |  |  | As per the Volume III price schedule, We understand that any modification/Refurbishment work towards any existing civil foundations is not in the bidder's scope .Please confirm | Except for any modifications (if needed) for rotation of marked isolator in tender drawings, no modification /refurbishment of any existing civil foundations are envisaged under present scope. |