POWER GRID CORPORATION OF INDIA LTD.

(Corporate Engineering Deptt.)

संदर्भ : C:Engg-TL:ER/RTM/TS/TL01&02/ANI	                                           दिनांक : 28/10/2025

# विषय : Approval of  Technical Specifications(TS) and BOQ consideration for Transmission line packages TL01 & TL02 for Project Implementation services for design, engineering, procurement, supply, erection, testing and commissioning of interconnection work of North, Middle & South Andaman under RDSS in UT of Andaman & Nicobar Islands. under domestic funding (DCB).

- Package List for Transmission Line works associated with Project Implementation services for design, engineering, procurement, supply, erection, testing and commissioning of interconnection work of North, Middle & South Andaman under RDSS in UT of Andaman & Nicobar Islands has been approved vide e-note File No. CC-EgTL-11-11/0021/2025/ER and NER Group (Computer No. 1091532) (copy of approved package list is enclosed at Appendix-I).

- As per the approved packaging, the following scope is envisaged under packages TL01 & TL02 (briefly indicated in table below):

| Bid Doc | Package | Transmission Line(s) | Brief Scope |
| --- | --- | --- | --- |
| I | Transmission line Package TL01 | Total – 97 Km (a)66kV D/C Diglipur-Mayabunder Transmission line (45km) (b) 66kV D/C Mayabunder-Rangat Transmission line (52km) | Transmission line works including Survey, Monopole Design and Testing, Supply of Tower & Monopole Parts including Bolts& Nuts, Supply of Line Materials including conductor (Covered & Bare), OPGW, Hardware fittings & Accessories, Insulators, Foundation (Opencast / Pile) for Monopole & Lattice tower, Installation, Erection, Stringing, testing and commissioning. |
| II | Transmission line Package TL02 | Total – 136 Km (a)66kV D/C Rangat-Baratang Transmission line (64km) (b) 66kV D/C Baratang-Bambooflat Transmission line (72km) |  |

- Transmission Lines under subject package traverse through WZ-3 (Coastal/Marine) region. Salient considerations for the preparation of BOQ are as follows:

- Tower weights and Foundation quantities under the subject package has been worked out based on the following standard inhouse deigned towers/foundations:

(i) For lattice towers, only 66KV DD type tower is envisaged. Standard design of 66KV DD type tower is not currently available. Accordingly, it is proposed to adopt the available design of 66KV DD tower of WZ-4 under Comprehensive scheme in Sikkim with suitable modification in span for subject transmission line packages.

(ii)For DD60+25M extensions required for long span (river crossing, etc.), 400KV standard Inhouse designed WZ-4 Lattice towers suitable for WZ-3 coastal region have been adopted to maintain required navigable clearances.

(iii) Suitable quantities have been estimated for Towers, Towers extensions & foundations whose design/BOM are not available.

(iv) All 66KV monopole structures design and testing shall be kept in the scope of contractor. However, monopole foundations shall be designed in house.

(v) Pile foundation shall be designed in house.

- In the initial estimation by EDANA, ACSR Dog conductor was considered. However, to reduce the number of structures and achieve higher span, AAAC panther bare conductor and panther equivalent covered conductor have been considered. The same was intimated to EDANA vide letter dated ……

- In site BOQ, retaining wall of … m is mentioned. Accordingly, retaining wall with an average length of 10m, height of 3.5m and foundation depth of 1 meter for … number of Location has been considered. Additional quantities arising from ULE towers, strengthening and raised chimney have been estimated based on following assumptions:

|  | Tower weight quantity | Foundation Quantity |
| --- | --- | --- |
| ULE Type Towers | 5% of total weight of DD Normal tower (NT) | 5% of Foundation quantities of DD type tower. |
| Strengthening of Lattice Tower | 5% of total weight of DD Normal tower (NT) | NA |
| Raised Chimney- Lattice Tower (Upto 2m) | NA | 2% of Foundation quantity of DD type Tower |
| Raised Chimney- Monopole structure (Upto 2m) | NA | 2% of sum of foundation quantities for all monopole structure |

- Installation of Heavy-duty Mat/Elevated platforms etc for creek crossing locations & shallow areas and Erection through crane have not been included in the BOQ.

- New line-item namely “stringing through drone in forest area with covered conductor” has been included in BOQ.

- 90KN Composite long rod insulators(30kv/mm) of length 1160mm & creepage 2232mm have been adopted. Clevis & tongue end fitting type insulator are considered for pole structure and Pin & ball fitting type insulators have been considered for Lattice tower.

- As per site BOQ, Number of locations for Benching is…... Accordingly, for Calculation of Quantities for Benching, 200CuM per Loc has been assumed.

- Technical specification for the transmission line packages TL01& TL 02 have been prepared based on latest standard technical specification for transmission line tower package (Rev upto June’2025) with following considerations: -

- As pile foundations are envisaged under package TL01 & TL02, QR for design and construction of pile foundations have been kept in the specification. The following parameters have been considered for QR of pile foundation:

- Minimum Diameter: - 750mm {at clause 2.1.1.1 (i)}

- Completion period: - 22 months (As per MNW schedule for completion of foundation)

- Rate of pile boring calculated and incorporated based on estimated BOQ for pile foundation.

Calculation of rate of boring is enclosed at annexure-IV & V for transmission line package TL01 & TL02 respectively.

- Standard Technical Qualification requirement for line materials pertaining to 66KV Transmission line, as envisaged in subject packages, are not specified in Section-I B of Technical specifications. Accordingly, following Technical Qualification requirement mentioned in Section IB of Technical specifications for 132KV voltage are proposed to be adopted for 66KV line materials.

| S.No. | Line material | Proposed Technical Qualification requirement |
| --- | --- | --- |
| (a) | Hardware fittings | Clause 2.36 - Hardware fittings for 132kV voltage level transmission lines |
| (b) | Accessories for conductor | Clause 2.41 - Accessories for conductor and Earthwire for 132kV transmission line. |
| (c) | Composite Insulators having 90KN rating with pin & ball and clevis & tongue end fittings. | Clause 2.8 - Composite Insulators for 132kV voltage level transmission lines with Single Panther configuration |
| (d) | AAAC panther equivalent covered conductor. | Clause 2.23 - AAAC PANTHER Conductor |

- Two additional sections-Section-VI C (Clamp fitting and accessories for covered conductor) and Section-VII C (Covered Conductor) have been included in Technical specifications.

- Following provisions have been defined in Section-1 A for 66KV Transmission lines & monopole design:

- System parameter.

- STP for composite long Rod insulator (90KN).

- Design span, weight span & wind span.

- Other design criteria for monopoles.

- Sampling from field as per RDSS Norms.

- Proposed Section 1A, Section-VI C, Section-VII C of Technical Specification is attached at Annexure-(I&II), Annexure-III and Annexure-IV respectively for subject transmission line packages.

- As per Integrated Systems Procedures, annexure-II, Sr No. A) 3 & delegation of power vide e-file No. CC-EgTL-14-20/0011/2024/NR Grp (Computer No. 839258), ED (Engg) is competent authority to approve the above proposal.

Put up for approval please.

उप महाप्रबंधक (अभि.-टी.एल.)

वरिष्ठ उप महाप्रबंधक (अभि.-टी.एल.)

महाप्रबंधक (अभि.-टी.एल.)

वरिष्ठ महाप्रबंधक (अभि.-टी.एल.)

मुख्य- महाप्रबंधक (अभि.-टी.एल.

मुख्य- महाप्रबंधक (अभि.-टी.एल./उपकेंद्र/ सिविल) – प्रभारी