| Sl. No. | Clause/Section | Existing Provision | Amended Provision |
| --- | --- | --- | --- |
| 1 | Clause of 1.1.3 of SECTION-VIIC (VOLUME-II), Rev 0 (Sep’2025) | Sr. No; Parameter; Unit; Value. 1; Voltage Grade (U0/U); KV; 38.10/66. 2; Rated current carrying capacity in air at 45Deg C ambient & 90 Deg C Operating temp (min), Solar Radiation 1045 w/sqm, Emissivity constant – 0.45, Wind velocity – 0.56m/Sec, effective angle of incidence of sun’s ray 90 Deg.; Amps; 511. 3; Cores; Nos; Single. 4; Nominal system voltage; KV; 66. 5; Highest System Voltage; KV; 72.5. 6; System Frequency; Hertz; 50. 7; Frequency variation limits; Percentage; 5. 8; Fault level (Conductor); KA/sec; 59.22. 9; Maximum allowable temperature. 9 (a); Max allowable temperature at design continuous operation at rated full load current; Degree; 90. 9 (b); Conductor’s temperature (Max) after short circuit 1.0 sec.; Degree; 250. 10; Minimum UTS; KN; 84.71. 11; Maximum DC resistance of the conductor at 20°C; ohm/km; 0.1182. 12; Max Sag at 200Mtr span at 90°C; Mtr; 6.18. | Sr. No; Parameter; Unit; Value. 1; Voltage Grade (U0/U); KV; 38.10/66. 2; Rated current carrying capacity in air at 45Deg C ambient & 80 Deg C Operating temp (min), Solar Radiation 1045 w/sqm, Emissivity constant – 0.45, Wind velocity – 0.56m/Sec, effective angle of incidence of sun’s ray 90 Deg.; Amps; 511. 3; Cores; Nos; Single. 4; Nominal system voltage; KV; 66. 5; Highest System Voltage; KV; 72.5. 6; System Frequency; Hertz; 50. 7; Frequency variation limits; Percentage; 5. 8; Fault level (Conductor); KA/sec; 59.22. 9; Maximum allowable temperature. 9 (a); Max allowable temperature at design continuous operation at rated full load current; Degree; 80. 9 (b); Conductor’s temperature (Max) after short circuit 1.0 sec.; Degree; 250. 10; Minimum UTS; KN; 84.71. 11; Maximum DC resistance of the conductor at 20°C; ohm/km; 0.1182. 12; Max Sag at 200Mtr span at 80°C; Mtr; 6.18. 13; Colour of outer insulation; Light Grey. 14; Slippage Factor; %; Should be sufficient for safe operation under maximum loads on the conductors and Hardware. Conductor manufacturer to coordinate with the hardware supplier and finalise the same.. |
| 2 | Clause 2.1 of SECTION-VIIC (VOLUME-II), Rev 0 (Sep’2025) | # If other than carbon black or a lower percentage than 2,0 % of carbon black is used for UV-stabilization $ For thermoplastic polyethylene only. ^Water column connected to one end of specimen by means of an appropriate fitting | # If other than carbon black or a lower percentage than 2.5 % of carbon black is used for UV-stabilization $ For thermoplastic polyethylene only. ^Water column connected to one end of specimen by means of an appropriate fitting |
| 3 | Clause 2.2 of SECTION-VIIC (VOLUME-II), Rev 0 (Sep’2025) | a); Visual and dimensional check on drum; Annexure-A. b); Visual check for joints, scratches etc. and length measurement of conductor by rewinding. c); Measurement of diameters of individual Steel and Aluminium strands. d); Check for lay-ratios of various layers. e); Galvanizing test on steel strands. f); Torsion and Elongation tests on steel strands. g); Breaking load test on steel and Aluminium strands; IS 398 (Part 2 or Part 5 as applicable). h); Breaking load test & Elongation test on Aluminium Alloy strands; IS 398 (Part 4 or Part 6 as applicable). i); Wrap test on Steel & Aluminium strands; IS 398 (Part 2 or Part 5 as applicable). j); Wrap test on Aluminium Alloy strands; IS 398 (Part 4 or part 6 as applicable). k); DC resistance test on Aluminium strands; Annexure-A. l); DC resistance test on Aluminium Alloy strands of AAAC/ AACSR conductor; Annexure-A. m); Resistivity Test on Aluminium Alloy strands of Al59 conductor; IS 398 (Part 6). n); Procedure qualification test on welded joint of Aluminium/ Aluminium Alloy strands; Annexure-A. o); Drum strength test (steel drum); Annexure-A. p); Barrel Batten strength test (wooden drum); Annexure-A. | a); Visual and dimensional check on drum; Annexure-A. b); Visual check for joints, scratches etc. and length measurement of conductor by rewinding. c); Measurement of diameters of individual Steel and Aluminium strands. d); Check for lay-ratios of various layers. e); Galvanizing test on steel strands (If applicable). f); Torsion and Elongation tests on steel strands (If applicable). g); Breaking load test on steel (If applicable) and Aluminium strands; IS 398 (Part 2 or Part 5 as applicable). h); Breaking load test & Elongation test on Aluminium Alloy strands; IS 398 (Part 4 or Part 6 as applicable). i); Wrap test on Steel (If applicable) & Aluminium strands; IS 398 (Part 2 or Part 5 as applicable). j); Wrap test on Aluminium Alloy strands; IS 398 (Part 4 or part 6 as applicable). k); DC resistance test on Aluminium strands; Annexure-A. l); DC resistance test on Aluminium Alloy strands of AAAC/ AACSR conductor; Annexure-A. m); Resistivity Test on Aluminium Alloy strands of Al59 conductor (If applicable); IS 398 (Part 6). n); Procedure qualification test on welded joint of Aluminium/ Aluminium Alloy strands; Annexure-A. o); Drum strength test (steel drum); Annexure-A. p); Barrel Batten strength test (wooden drum); Annexure-A. |
| 4 | Clause 2.11 of SECTION-VIIC (VOLUME-II), Rev 0 (Sep’2025) |  | New Clause added 2.11.14 For covered conductor. The barrel diameter of delivery drums shall not be smaller than 30 x D, where D is the outer diameter of the covered conductor. 2.11.15 For covered conductor Drums shall be transported with the drum axis horizontal, and any drum movement shall be avoided. The distance between the outer layer of the covered conductor on the filled drum and the ground or lagging should be at least 50 mm. 2.11.16 In covered conductor drum ends shall be firmly attached to the drum during transport and storage without damaging the conductor ends. It is recommended that both conductor ends are accessible. 2.11.17 Rewinding of conductor from one drum to another drum shall always be done from top of the drum to the top of the rewinding drum. 2.11.18 The Conductor shall be supplied as per the approved drum schedule finalised as per the approved detailed survey. The length of the conductor shall be finalised to minimize the number of the joints and wastage of the conductor. |
| 5 | New Clause added in SECTION-VIIC (VOLUME-II), Rev 0 (Sep’2025) |  | New clause added 2.14 Transportation & Installation of MVCC Conductor 2.14.1 Installation of covered conductors shall be done by authorized and skilled contractors only. Covered conductors shall be installed and operated in such a way not to impair their properties. Care shall be exercised during installation to avoid any damage to the conductor covering and to the conductor itself. 2.14.2 Drums of covered conductor shall always be transported and stored with the drum axis parallel to the ground. Drums shall be rolled only for short distances over flat solid ground in the direction indicated on the flange. 2.14.3 Unwinding of covered conductor shall always be done while keeping the conductor drum axis parallel to ground with paving out from the top of the drum in the direction marked by the manufacturer and never be unwind keeping drum axis vertical to the ground. 2.14.4 Short lengths of covered conductors may be coiled. Coils shall be stored and transported horizontally on suitable palettes. The inner coil diameter shall not fall below the minimum permissible barrel diameter of the transporting drum. The coils shall be protected against mechanical stress and shocks. 2.14.5 Special attention shall be paid to avoid bending radii (not less than 30XD where D is the diameter of the covered conductor) which can cause deterioration of any property of the covered conductor. 2.14.6 Care shall be exercised during installation to avoid any damage to the conductor covering. The seal caps shall not be removed from the ends of the covered conductor until immediately prior to fixing, termination or jointing. The possibility of damage to moisture seals during installation shall be borne in mind. Where such damage may have occurred, the seals shall be inspected and remade if necessary. 2.14.7 Rollers of the appropriate diameter not less than 30XD where D is the diameter of the covered conductor and quantity shall be provided for installation. The rollers shall have a smooth clean surface, no sharp edges and shall rotate easily. To prevent the covering from damage any abrasive contact with soil or stone is not permitted. Abrasive contact of the covering with branches or similar shall be avoided. 2.14.8 Covered conductors shall be pulled by using appropriate pulling devices ensuring that the pulling force is distributed to the conductor. The pulling force in KN shall be continuously monitored during the pull-up procedure and shall not exceed 0.27 X (Slippage factor in %/100) X RTS in KN of the conductor. |
| 6 | Clauses 2.1 & 2.2 SECTION-VIIC (VOLUME-II), Rev 0 (Sep’2025) | Acceptance criteria as per column 4 of table 2 of EN 50397-1:2020 (E) | Acceptance criteria as per column 4 of table 2 of EN 50397-1:2020 (E). Acceptance, criteria for covering material shall be as per column 3 of table 1 of EN 50397-1:2020 (E). |
| 7 | Schedule-1 of the BPS (Price Schedule) | A TL01 66kV D/C Diglipur – Mayabunder TL. Item Description; Material Code; Description; Unit; Qty. 38; 1000080022; TENSION/ANCHORING CLAMP HELICAL TYPE 66KV COVERED AAAC PANTHEREQUIVALENT CONDUCTOR; EA; 1128. B TL01 66kV D/C Mayabunder - Rangat TL. Item Description; Material Code; Description; Unit; Qty. 38; 1000080022; TENSION/ANCHORING CLAMP HELICAL TYPE 66KV COVERED AAAC PANTHEREQUIVALENT CONDUCTOR; EA; 1260. | A TL01 66kV D/C Diglipur – Mayabunder TL. Item Description; Material Code; Description; Unit; Qty. 38; 1000080022; TENSION/ANCHORING CLAMP HELICAL TYPE 66KV COVERED AAAC PANTHEREQUIVALENT CONDUCTOR; EA; 564. Added new; 1000080775; COMPRESSION DEAD END WITH HEAT SHRIKABLE INSULATION SLEEVE FOR 66Kv AAAC PANTHER EQUIVALENT CONDUCTOR; EA; 564. B TL01 66kV D/C Mayabunder - Rangat TL. Item Description; Material Code; Description; Unit; Qty. 38; 1000080022; TENSION/ANCHORING CLAMP HELICAL TYPE 66KV COVERED AAAC PANTHEREQUIVALENT CONDUCTOR; EA; 630. Added new; 1000080775; COMPRESSION DEAD END WITH HEAT SHRIKABLE INSULATION SLEEVE FOR 66Kv AAAC PANTHER EQUIVALENT CONDUCTOR; EA; 630. |
| 8 | Clause 3.1.2 of SECTION-VI C (VOLUME-II), Rev 0 (Dec’2025) |  | a); Visual Examination; IS 2486 (Part-I). b); Verification of Dimensions; IS 2486 (Part-I). c); Chemical Analysis of Materials; Annexure-A. d); Electrical resistance test for dead end assembly.; IS 2486-(Part-I). e); Heating cycle test for dead end Assembly; IS 2486 (Part-I). f); Mechanical strength test on hardware fitting except clamps; Annexure-A. g); Slip strength test for dead end assembly; Annexure-A. h); Galvanising/ electroplating tests; Annexure-A. Added New Tension fitting compression type. |
| 9 | Clause 3.2.1 of SECTION-VI C (VOLUME-II), Rev 0 (Dec’2025) |  | (a); Slip strength test for dead end assembly; Annexure-A. Added New Tension fitting compression type. |
| 10 | Clause - 1.8 of - SECTION-VI C (VOLUME-II), Rev 0 (Dec’2025) | 1.8.11 The assembly shall consist of an Aluminum tube for installation of conductor, a forged Eye for mounting of clamp and another aluminum tube for jumper connection attached to the main tube through an aluminum pad using bolts and nut. Fasteners used in the assembly shall be Hot Dip Galvanized steel. Conductor shall be installed inside the tension clamp though crimping by Hexagonal compression. | 1.8.11 The assembly shall consist of an Aluminum tube of suitable length such that the tube must overlap the insulation of the covered conductor for suitable length to avoid water ingress. This portion of the tube shall be uncompressed, a forged Eye for mounting of clamp for fixing hardware. The dead-end assembly shall be compression type with provision for comprising jumper terminal at one end. The angle of jumper terminal to be mounted should be 30° with respect to the vertical line. The area of bearing surface on all the connections shall be sufficient to ensure positive electrical and mechanical contact and avoid local heating due to I2R losses. The resistance of the clamp when compressed on Conductor shall not be more than 75% of the resistance of equivalent length of Conductor. 1.8.12 Die compression areas shall be clearly marked on each dead-end assembly designed for continuous die compressions and shall bear the words ‘COMPRESS FIRST’ suitably inscribed near the point on each assembly where the compression begins. If the dead-end assembly is designed for intermittent die compressions it shall bear identification marks ‘COMPRESSION ZONE’ AND ‘NON-COMPRESSION ZONE’ distinctly with arrow marks showing the direction of compressions and knurling marks showing the end of the zones. The letters, number and other markings on the finished clamp shall be distinct and legible. 1.8.13 The assembly shall not permit slipping of, damage to, or failure of the complete conductor or any part thereof at a load less than 95% of the ultimate tensile strength of the conductor. 1.8.14 Heat shrinkable insulation sleeve shall be provided to cover the entire fitting to avoid the water ingress into fitting. The sleeve must have same UV resistant property as that of the conductor insulation. The sleeve should be rugged and must have same expected life as that of the insulation of the covered conductor. Fasteners used in the assembly shall be Hot Dip Galvanized steel. Conductor shall be installed inside the tension clamp though crimping by hexagonal compression. |
| 11 | Clause 1.8.9 of SECTION-VI C (VOLUME-II), Rev 0 (Dec’2025) | ………… The armored rod shall be made up of Aluminum clad steel with rubber coating and must be smooth and should not cause any damage to the insulation of the covered conductor during stringing & operation, if needed inner protection rods may also be provided. Cross over starting point should be marked on the fittings. All steel parts shall be hot dipped galvanized to suite marine environment. …………………… | ………… The armoured rod shall be made up of Aluminum clad steel with rubber coating and must be smooth and should not cause any damage to the insulation of the covered conductor during stringing & operation, if needed inner protection rods may also be provided. Cross over starting point should be marked on the fittings. All steel parts shall be hot dipped galvanized to suite marine environment. ……….. Sr No; Parameter; Requirement. 1; Wrap test (on a mandrel 2 times the dia of the sample and at the rate of 15 turns/minute); After close helix, the sample should not fracture. 2; Tensile strength; Table - 1. 3; Weight of coating; Table - 2. 4; Adherence of coating (in a close helix not exceeding 15 turns/minute) around a cylindrical mandrel having a diameter prescribed in table 3.; No cracking or flacking to such an extent that the aluminium coating can be removed by rubbing with the bare fingers. 5; Dimensional tolerance; +/- 0.013mm. Table - 1 Wire diameter (mm); Ultimate tensile strength minimum) MPa; Ultimate elongation (Min.) percent in 254 mm. 1.270 to 2.283 including; 1280; 3. 2.286 to 3.045 including; 1240; 3.5. 3.048 to 3.515 including; 1210; 4. 3.518 to 3.782 including; 1170; 4. 3.785 to 4.826 including; 1140; 4. Table - 2 Wire diameter (mm); Min. weight of aluminium coating on uncoated wire surface (g/m2). 1.270 to 1.521 including; 70. 1.524 to 1.902 including; 76. 1.905 to 2.283 including; 79. 2.286 to 2.639 including; 85. 2.642 to 3.045 including; 92. 3.048 to 3.553 including; 98. 3.556 to 4.569 including; 104. 4.572 to 4.826 including; 116. Table - 3 Wire diameter (mm); Min. ratio of mandrel diameter to wire diameter. 1.270 to 2.283 including; 3. 2.286 to 3.553 including; 4. 3.556 to 4.826 including; 5. Tolerance of formed fittings Item; Tolerance. Pitch length; + 0.6 mm (-)0.12 mm. Internal diameter; + 1% (-) 3%. Length of individual rod; (±) 1%. Difference in length; (±) 1% between the longest and the shortest rod in an individual set. |
| 12 | Clause 1.8.5 of SECTION-VI C (VOLUME-II), Rev 0 (Dec’2025) | The fittings shall be able to withstand the specific minimum failure load (SMFL) and shall not damage the covering of cable. SMFL is the minimum failure load for clamps. The SMFL (specific minimum failure load) shall be 20 KN for 50-70 sq mm and 28 KN for 95- 157 sq mm and 90 KN for 160-241 sq mm. | The fittings shall be able to withstand the specific minimum failure load (SMFL) and shall not damage the covering of cable. SMFL is the minimum failure load for clamps. The SMFL (specific minimum failure load) shall be specified by the purchaser or declared by the supplier below which mechanical failure will not take place. |
| 13 | Clause 1.9.4 of SECTION-VI C (VOLUME-II), Rev 0 (Dec’2025) | Screws or nuts assigned for fitting with IPC (Insulating Piercing connector), must be fitted with torque limiting shear heads to prevent over tightening or under tightening. While the min & max torque values are to be specified by Manufacturer, these should not exceed 27 N-M for IPC for main conductor < 95 sq mm, and 42 N-M for main conductor >95, but < 240 sq mm. | Screws or nuts assigned for fitting with IPC (Insulating Piercing connector), must be fitted with torque limiting shear heads to prevent over tightening or under tightening. The min & max torque values are to be specified by Manufacturer. |
| 14 | Clause 3.1.5 & 3.1.7 of SECTION-VI C (VOLUME-II), Rev 0 Dec’2025) | 8; Check for permanent marking; Cl.7.3 of EN 50397-2. 9; High Voltage Test; IS: 10810 Part-45. ……………. | 8; Check for permanent marking; Cl.7.3 of EN 50397-2. 9; High Voltage Test; Cl.1.2.2 EN 50397-1. …………. |
| 15 | Clause 3.2.4 of SECTION-VI C (VOLUME-II), Rev 0 Dec’2025) | Sr. No; Test; Reference. 1; Visual examination; Cl.7.1 of EN 50397-2. 2; Dimension verification; Cl.7.2 of EN 50397-2. 3.2; Slip test at ambient temperature; Cl.7.4 of EN 50397-2. 8; Check for permanent marking; Cl.7.3 of EN 50397-2. 9; High Voltage Test. | Sr. No; Test; Reference. 1; Visual examination; Cl.7.1 of EN 50397-2. 2; Dimension verification; Cl.7.2 of EN 50397-2. 3; Slip test at ambient temperature; Cl.7.4 of EN 50397-2. 4; Check for permanent marking; Cl.7.3 of EN 50397-2. 5; High Voltage Test; Cl.1.2.2 EN 50397-1. |
| 16 | Clause 3.2.5 of SECTION-VI C (VOLUME-II), Rev 0 Dec’2025) | Arc Protection Device Sr. No; Test; Reference. 1; Visual examination; Cl.7.1 of EN 50397-2. 2; Dimension verification; Cl.7.2 of EN 50397-2. 3.1; Clamp Bolt tightening test; Cl.7.4 of EN 50397-2. 3.2; Shear Head function test. 3.3; Hot Dip Galvanizing test. 8; Check for permanent marking; Cl.7.3 of EN 50397-2. 9; High Voltage Test. | Arc Protection Device Sr. No; Test; Reference. 1; Visual examination; Cl.7.1 of EN 50397-2. 2; Dimension verification; Cl.7.2 of EN 50397-2. 3.1; Clamp Bolt tightening test; Cl.7.4 of EN 50397-2. 3.2; Shear Head function test. 3.3; Hot Dip Galvanizing test. 4; Check for permanent marking; Cl.7.3 of EN 50397-2. 5; High Voltage Test; Cl.1.2.2 EN 50397-1. |
| 17 | Clause 3 of SECTION-VI C (VOLUME-II), Rev 0 Dec’2025) | Test at low temperature | Test at low temperature for all the fittings has been deleted. |
| 18 | Clause 3.1.3 of SECTION-VI C (VOLUME-II), Rev 0 Dec’2025) | Tension clamp Helically formed. Sr.No; Test; Standard. …; …..; …... 9; Galvanization test; Cl 7.11 of IS 12048. | Tension clamp Helically formed. Sr.No; Test; Standard. …; …..; …... 9; Galvanization test; Cl 7.11 of IS 12048. 10; Adherence of coating test; Annexure-A. |
| 19 | 11_Section XI Drawing Rev-2 (Jan’2025) | TS Note TL 01&02 ANDAMAN.docx | Deleted. |
| 20 | Schedule-2 of the BPS (Price schedule) |  | A TL01 66kV D/C Diglipur - Mayabunder TL. Item Description; Service Code; Description; Unit; Qty. Added new; 100056953; LAND SCHEDULING-COMPENSATION; KM; 45. B TL01 66kV D/C Mayabunder - Rangat TL. Item Description; Service Code; Description; Unit; Qty. Added new; 100056953; LAND SCHEDULING-COMPENSATION; KM; 52. |
| 21 | Clause 3.4 (s) of SECTION-IA (VOLUME-II), Rev 15 Sept’2025) |  | Open cast/Caisson foundations for monopoles Depending on actual site conditions, monopole foundations - open cast or caisson-type may be required. For caisson-type foundations, no separate BPS items have been kept. The BPS quantities specified for excavation, concreting, and reinforcement for “work associated tower + pole foundation” shall be deemed to include caisson foundations quantities as well. Rates quoted for “work associated tower + pole foundation” shall be inclusive of specialized equipment (if required), manpower, or other resources necessary for executing caisson foundations. No extra payment shall be admissible on this account. |
| 22 | Clause 3.4 (r) of SECTION-IA (VOLUME-II), Rev 15 Sept’2025) | - Technical Specification of Vibration dampers of covered conductor ………s. The clamp of the vibration damper should be designed such that it does not damage the insulation of the covered conductor. ……. | - Technical Specification of Vibration dampers of covered conductor ………s. The clamp/rods of the vibration damper should be designed such that it does not damage the insulation of the covered conductor. ……. |
| 23 | Clause 3.4 (k) of SECTION-IA (VOLUME-II), Rev 15 Sept’2025) |  | Added New 7. Galvanisation of Poles under Marine/Coastal/Creeks shall be 900gms/sqm. |
| 24 | Annexure-A of Section-VIC Volume-II |  | Added New Clause 2.10 Adherence of coating test (Aluminium Clad Steel wire) Adherence of coating (in a close helix not exceeding 15 turns/minute) around a cylindrical mandrel having a diameter prescribed in table 3 at 1.8.9. No cracking or flacking to such an extent that zinc coating can be removed by rubbing with bare fingers. |
| 25 | Annexure-C of SECTION-VIIC (VOLUME-II), Rev 0 (Sep’2025) |  | Temperature at current carrying capacity mentioned at Sr. No 5.3, 5.8 shall be 80°C. Sr. No 5.12 Slippage factor % to be specified in the in the GTP. |
| 26 | Part-1, Price_schedule | In view of above, the existing file “Price_schedule” stands replaced with “Price_schedule_Rev01” and is attached herewith this Amendment. Note: Bidders are requested to consider the revised excel file “Price_schedule_Rev01” for bid preparation/submission. It may be noted that while submitting the bid, bidders are requested to keep the excel file name as “Price_schedule_Rev01”. (Bidders may refer user manuals at the portal https://etender.powergrid.in regarding submission of bid) |  |  |