| Sl. No. | Cl. Ref. / Description of clause | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- |
|  | For Route Survey / Tower Schedule / Line Kilometers. | We request you to share the preliminary route survey, tower schedule, and Line Google earth KMZ file. Additionally, we are planning a site visit to Andaman & Nicobar next week. Kindly advise the contact person and coordination details for the site visit and coordination purpose | Bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines. For details of contact person, Bidders may refer to clause 1.4.1 of Section-IA (Volume-II) of Technical Specification. |
|  | Price Schedule: Items No. 20 and 21 of Schedule 1: Work associated with conductor AAAC Panther Conductor Supply of 66 KV AAAC Medium voltage covered conductor (MVCC) | We request you to kindly confirm the intended application of both conductors, specifically indicating the line sections where the bare conductor and the MVCC (Medium Voltage Covered Conductor) are to be utilized. | MVCC conductor are proposed in the stretches covered under forest and bare conductors are proposed for non forest zones and long spans in creeks. |
|  | Part 2/ Sec IV E&F/10: Corrosion resistant steel (CRS) of grade Fe500 / Fe 500D / Fe 550 / Fe 550D conforming to IS 1786 may be adopted as an alternative to epoxy coated reinforcement for foundation in coastal areas or creek or aggressive soil areas or under marine environment. | We request you to kindly confirm whether the use of CRS grade steel is acceptable as an alternative to epoxy-coated steel, provided all applicable technical, performance, and corrosion-protection requirements are met. | Provisions of the Technical Specifications are to be followed. |
|  | Part 2/ Sec IVF/26: The pole structures shall be proto type tested with the extension mentioned in the following table by the contractor at any testing station having facilities to testthe structures. The proto type pole structures after inspection by employer shall be transported to the test bed by the Contractor. ..** | We understand that the +9 m extension of 66 kV poles may require type testing, as the type-testing table in the technical specifications does not indicate voltage levels below 132 kV. We request you to kindly confirm the applicability of type testing for the 66 kV pole extensions. | Bidders may refer to clause 3.4 (k) Sr. No 5.0 of SECTION-I A (VOLUME-II), Rev 15 (Sept’2025) of the Technical Specification. |
|  | Part 2 / Sec VII C/4: The scope includes supplying, drawing, testing andcommissioning of AAAC (All Aluminum Alloy Conductor) panther equivalent covered conductor of as per STP mentioned at Annexure-B2 suitable for 66kV S/C and D/C transmission lines on Steel Monopoles/Towers being constructed in Marine Environment of Andaman and Nicobar Island and passing through dense forest and wet environment. | We request you to kindly provide the Guaranteed Technical Particulars (GTP) for MVCC, as manufacturers are seeking a reference. Certain parameters, such as minimum XLPE insulation thickness and other critical criteria, are not clearly specified in the technical specifications. We request you to kindly provide the Guaranteed Technical Particulars (GTP) for MVCC, as manufacturers are seeking a reference. Certain parameters, such as minimum XLPE insulation thickness and other critical criteria, are not clearly specified in the technical specifications. | Bidders may refer to SECTION-VIIC (VOLUME-II), Rev 0 (Sep’2025) of the Technical Specification in general and Clause 1.5.7 for insulation requirement. GTP for the MVCC has to be provided by the successful bidder during detail engineering. |
|  | Part 2 / Sec VII C/11: **Type tests specified under Clause 2.1 shall not be required to be carried out if supplier has conducted these tests earlier on the same conductor & same bundle configuration (applicable for tests ‘c’ & ‘d’) and valid type test certificates are available. The test certificate shall be considered valid if......** | From the referenced clause, we understand that if a manufacturer has already carried out type testing for a similar conductor within the last ten (10) years, further type testing may not be required. We request you to kindly confirm if the same conductor or higher capacity MVCC conductor can be considered. | If the tests are performed on same design and materials meeting technical requirement mentioned in the specification, the type testing shall not be required. |
|  | Part 2/ 13/TSNote TL/3.0(a)/1: (i) For lattice towers, only 66KV DD type tower is envisaged. Standard design of 66KV DD type tower is not currently available. Accordingly, it is proposed to adopt the available design of 66KV DD tower of WZ-4 under Comprehensive scheme in Sikkim with suitable modification in span for subject transmission line packages. (ii)For DD60+25M extensions required for long span (river crossing, etc.), 400KV standard Inhouse designed WZ-4 Lattice towers suitable for WZ-3 coastal region have been adopted to maintain required navigable clearances | We understand that the design of lattice structures is under the Employer’s scope and, accordingly, type testing of Lattice Structure is not envisaged under the Contractor’s scope. We request you to kindly confirm whether our understanding is correct. | Bidders may refer to Amendment No. 1 |
|  | Part 2/13/TSNote TL/3.0(a)/2: (iv) All 66KV monopole structures design and testing shall be kept in the scope of contractor. However, monopole foundations shall be designed in house. (v) Pile foundation shall be designed in house | We understand that the design of monopoles is under the scope of the Contractor, whereas the design of pile foundations is under the scope of the Employer. We request you to kindly confirm whether this understanding is correct. | Bidders may refer to Amendment No. 1 |
|  | SECTION-I A (VOLUME-II), Rev 15 (Sept’2025) SECTION-VIIA (VOLUME-II), Rev 3 (Dec’2023) Cl. 3.4,Pg 9 of 31, Pg. 27 of 33: Special Requirements As Transmission line covered under the subject packages passes through Coastal/Marine area, following requirements shall replace/supplement the requirements in different sections of the Technical Specification..** | 1. Confirmation of Conductor Properties and Sag–Tension Criteria Kindly confirm the technical properties of the Single AAAC Covered PANTHER conductor in accordance with Section VIIA (Volume–II), Revision 3 of the specification. Further, please clarify whether the sag–tension calculations for the subject conductor shall be carried out considering parameters applicable to: ACSR conductors, or HTLS conductors, or whether a separate, manufacturer-specific sag–tension model is to be adopted for the AAAC Covered PANTHER conductor. Additionally, if available, kindly provide the sag–tension wire file / stringing chart data compatible with standard transmission line design software, to ensure uniformity and accuracy in detailed engineering. | For Technical Specification of the covered conductor, bidders may refer to SECTION-VIIC (VOLUME-II), Rev 0 (Sep’2025) of the Technical Specification. Bidder shall provide GTP of the covered conductor during detail engineering for Sag Tension Calculation. |
|  | SECTION-I A (VOLUME-II), Rev 15 (Sept’2025) Cl. 3.4 (k) ,Pg 12 of 31: (k) Tower/Pole Loading Conditions: Following loading condition shall be considered in design of poles in addition of conditions mentioned in Sec- IV F 1. All Poles (PA, PB, PC & PD) shall be designed for covered conductor and its hardware/accessories and Disc Insulators considering creepage of 31 mm/kV i.e maximum of length/dia/weight amongst CLR & Disc insulators string shall be considered. Further, PD type poles shall also be suitable for installation of surge arrestor. The loads due to surge arrestor and clearances required shall be considered in design of PD. 2. All Poles shall be designed for maximum of dia/weight amongst EW 7/3.15 & OPGW. ..** | 2. Design Basis of PD Type Poles with Surge Arrester Provision As per the clause stating that “PD type poles shall also be suitable for installation of surge arrester. The loads due to surge arrester and clearances required shall be considered in design of PD,” kindly clarify the following: Whether the PD type pole is required to be designed inherently to meet the CT pole load and clearance requirements, or Whether a separate design case / enhancement is to be considered and quoted to satisfy the CT pole requirements in addition to the standard PD pole design. Furthermore, please provide the standard CT attachment details, including mounting arrangement to enable proper integration of surge arresters on PD type poles. | Load of surge arrester shall be considered as permanent dead load and associated wind load. No separate design load case shall be required. The details of mounting shall be finalised during detail engineering. |
|  | SECTION-I A (VOLUME-II), Rev 15 (Sept’2025) Cl. 3.4,Pg 9 of 31: Special Requirements As Transmission line covered under the subject packages passes through Coastal/Marine area, following requirements shall replace/supplement the requirements in different sections of the Technical Specification: - | 3. Consideration of Cyclonic (K4) Importance Factor for Coastal/Marine Area Since the transmission line alignment passes through a Coastal/Marine area, and in accordance with CEA Guidelines Clause 4.7.1, it is specified that for pole structures located within 60 km from the sea coast, the importance factor for cyclonic region (K4 factor = 1.3) as per IS: 875 (Part 3) shall be considered while calculating the design wind speed. In this regard, kindly confirm that the cyclonic importance factor (K4 = 1.3) has been duly considered in the structural design of poles, including wind load calculations and load combinations, to ensure compliance with applicable statutory requirements and standards. | Design of poles is under bidders scope. Bidder may refer to SECTION-IVF (VOLUME-II), Rev 3 (Oct’2025) of the Technical Specification regarding applicability of the Cyclonic (K4) factor. |
|  | SECTION-I A (VOLUME-II), Rev 15 (Sept’2025) Cl. 2,Pg 5 of 31: The bidder/agency shall have successfully completed# execution of pile foundation work (s) within the last seven (7) years as on date of NOA. In the above work(s), the bidder’s experience should include the following: (i) (ii) (iii) The bidder/agency should have installed cast-in-situ vertical bored pile foundation having following minimum diameter and having minimum depth of 25 meters below ground level:- For Package TL01: 750 mm For Package TL02: 750 mm | As per the relevant clause, a pile foundation with a minimum diameter of 750 mm is stipulated for the foundation works. In this regard, kindly confirm whether the raised chimney is required to be considered as part of the design scope. Additionally, please advise whether a pier- or caisson-type foundation system may be proposed as an acceptable alternative, subject to design adequacy and approval. | Design of pile foundations are in the scope of Employer. |
|  | Part 2 /Sec VII C/1.1.1/1: The scope includes supplying, drawing, testing and commissioning of AAAC (All Aluminum Alloy Conductor) panther equivalent covered conductor of as per STP mentioned at Annexure-B2 suitable for 66kV S/C and D/C transmission lines on Steel Monopoles/Towers being constructed in Marine Environment of Andaman and Nicobar Island and passing through dense forest and wet environment. | We request you to kindly provide the approved vendor list, if any, for MVCC conductors and their associated hardware fittings manufacturers. | Bidders to explore the vendors meeting the technical QR mentioned at clause 3.4 (q) in Section-IA Volume-II of Technical Specification. |
|  | Part 2/Sec III S&S/3.6.1 & 10: 3.6.1 - The Contractor shall count, mark and put proper numbers with suitable quality of paint at his own cost on all the trees that are to be cut by the Employer at the time of actual execution of the work as detailed below. Contractor may please note that Employer shall not pay any compensation for any loss or damage to the properties or for tree cutting due to Contractor’s work. | We undertand that Actual tree cutting and associated permissions/clearances are in the scope of the Employer (PGCIL). The Contractor’s scope is limited only to identification, counting, marking, and numbering of trees to be cut.Any compensation, charges, or liabilities arising out of tree cutting or damage to properties are not payable by the Contractor. Kindly confirm whether our above understanding is correct. | Bidders may refer to clause 3.6 of SECTION-III (VOLUME-II) |
|  | Part 2/ Sec 9A/Pile foundation/1.2.1.4/2.1.2 & 7,13: 1.2.1.4 - The Bidder's offer should be based on the mobilization of at least one no. piling rig for each tower location together with all associated working gangs, tool etc. (including at least one no. of Rotary Hydraulic drilling rig capable of boring suitable diameter piles up-to designed depth below existing ground level with necessary tools/ accessories for boring). *** 2.1.2 - ***. The minimum capacities of some key equipment are listed below. However, bidder has to furnish information regarding the equipments they intend to deploy for the project as per Performa stipulated in the relevant schedules of the BPS | We understand that any kind of Rig machine i.e Hydraulic Rig/Tractor mounted PRD Rotary Rig/Truck Mounted Rig/Winch/Tripod etc which has torque greater than 12T capacity are allowed for the Piling works for the subject tender packages | Bidders to comply with the provisions of bidding documents |
|  | General | For setting up the RMC batching plant, we request confirmation whether adequate space can be provided at the substation location, as most of the major locations under the subject tender package are situated in forest areas. | Bidders may refer to clause 1.4.1 of SECTION-IA (VOLUME-II) |
|  | General | 2. We need to carry our survey; therefore, we request you to kindly arrange to provide kmz file for the above mentioned line. | Bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines. For details of contact person Bidders may refer to clause 1.4.1 of Section-IA (Volume-II) of Technical Specification. |
|  | Site Visit : 66kV power source | During our site visit, it was observed that there is no existing power source of 66 kV or higher voltage level available across the entire island. In view of the above, kindly clarify and confirm the proposed methodology for energization of the transmission line upon completion of erection and installation works. | Bidders scope is limited to supply, installation, erection, testing and commissioning of the transmission line. |
|  | General: Project Commissioning | It has been observed that PGCIL has also floated separate tender for the substation project (SS01) proposed to be constructed between the transmission line. In this regard, kindly clarify whether a bidder executing only the transmission line project shall be required to wait for energization of the lines until the successful commissioning of the associated substation project. Please clarify. | Bidders scope includes supply, installation, erection, testing and successful commissioning of the transmission line. |
|  | BOQ: Tower Structure | Kindly confirm the Steel grade - IS2062 E250 & E350 grade A for MS and HT respectively. | Bidder may refer Clause 1.1.1 of SECTION-IV C (VOLUME-II) of the Technical Specification. |
|  | BOQ: Tower Structure | Kindly confirm the "BN grade - 5.6/5" to be considered. | Bidder may refer Clause 1.1.2 of SECTION-IV C (VOLUME-II) of the Technical Specification. |
|  | BOQ: Tower Structure | Kindly confirm the Galvanizing quoting - 610gms/sqm (Average) | Bidder may refer Clause 1.6 of SECTION-IV C (VOLUME-II) of the Technical Specification. Minimum overall zinc coating of 900 gm/ sqm is applicable for lines passing under Marine/costal/creek area. |
|  | General: Type test reports, GTP | You are requested to clarify that GTP&TTR for every item is required to submit at the time of bid submission or after getting LOA we have to submit GTP & TTR | Bidders may refer Clause 1.1.8 of SECTION-VI C (VOLUME-II) and Clause 1.1.4 of SECTION-VII C (VOLUME-II) of the Technical Specification . |
|  | General - Route | Please provide KMZ file of proposed route for better understanding of scope of work | Bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines. For details of contact person Bidders may refer to clause 1.4.1 of Section-IA (Volume-II) of Technical Specification. |
|  | General - Soil Investigation Report | Kindly Provide soil investigation report of proposed route. | Bidder may refer to Clause 1.4.1 of Section-IA (Volume-II) |
|  | General | Kindly provide the height restriction of the proposed TL for aviation clearance. | Bidder may refer to Clause 1.4.1 of Section-IA (Volume-II) |
|  | Section IA: Scope, Page-2: Cable bypass arrangement of 11KV/33KV/LT Powerline crossing. (wherever applicable & covered under BPS) | Please provide details of cable bypass arrangement (Buried /through RCC Cable trench). | Refer clause no. 3.1.8 of section IVC of Technical Specification. |
|  | General-Supply | Please provide the list of manufacturers who are having 66kV covered conductor. | Bidders to explore the vendors meeting the technical QR mentioned at clause 3.4 (q) in Section-IA Volume-II of Technical Specification. |
|  | General-Supply | Please provide the list of manufacturers who are having 66kV covered conductor hardware. | Bidders to explore the vendors meeting the technical QR mentioned at clause 3.4 (q) in Section-IA Volume-II of Technical Specification. |
|  | General | Kindly clarify if the Medium Voltage Covered Conductor supplier needs PGCIL Approval for this specific category or conventional conductor (ACSR/Al59) approval can suffice the requirement and the approval for 66kV MVCC category can be applied along with this tender. Your clarification in this regard will help us to progress further towards this tender | Bidders to explore the vendors meeting the technical QR mentioned at clause 3.4 (q) in Section-IA Volume-II of Technical Specification. |
|  |  | Referring to the subject tenders, we respectfully submit for your kind consideration the adoption of base-plated monopoles with steel caisson foundations as an effective alternative to the conventional base-plated monopoles with pile foundations for the Andaman & Nicobar transmission project. Based on our detailed assessment of site conditions, execution challenges and logistical constraints specific to the Andaman & Nicobar Islands, we believe that Steel Caisson monopoles offer a technically sound, time-efficient, and cost-optimized solution. With over two decades of experience in power transmission project management, tendering, and execution, Bajel Projects Ltd has successfully deployed this technology in challenging conditions, achieving measurable improvements in schedule adherence and overall project economy. Below are few considerations supporting this proposal: 1. Key Advantages of Monopoles with Steel Caisson foundation: Steel Caisson Foundation have a compact foundation footprint, enabling installation in confined and right of way constrained locations. Unlike pile foundations, which require heavy piling rigs, extensive excavation, multiple construction stages and prolonged curing periods, steel caissons foundation allow faster and more streamlined installation with minimal site preparation. From an engineering standpoint, steel caissons foundation provides high load-bearing capacity, long term durability in soft, saturated and coastal soils and improved structural performance under extreme environmental conditions without disturbing existing soil, including high wind and cyclonic loads prevalent in the Andaman & Nicobar region. Reduced concrete and reinforcement quantities coupled with simplified construction activities, typically result in overall foundation cost savings, primarily through reduced construction time and logistics. In addition, the monopole configuration offers better aesthetics, fewer components, and improved reliability, making it particularly suitable for environmentally sensitive and geographically constrained areas. 2. Proven Execution Experience – 66kV Double Circuit PSPCL Project Bajel Projects has successfully executed Steel Caisson Foundation in our already commissioned transmission project for PSPCL for 66kV Voltage Level, marking one of the earliest applications of this technology in India. The solution was adopted to overcome severe right of way constraints, proximity to a national highway, and multiple underground and overhead utility crossings, where conventional lattice or pile-based foundations were not feasible. The project achieved notable execution efficiency, including rapid installation cycles and was completed within the stipulated timelines. The innovation and execution methodology were formally acknowledged by PSPCL through an Appreciation Letter, which is enclosed herewith for your reference and needful action. 3. Relevance to Andaman Project For the Andaman & Nicobar Islands, Steel Caisson monopoles directly address several critical challenges, including: • Difficult access to remote and forest surrounded locations • Limited availability and high mobilization cost of heavy piling equipment • High groundwater levels and variable soil profiles • Environmental sensitivity and restrictions on large-scale excavation The proposed solution enables precise placement, faster erection and reduced dependence on heavy machinery, thereby aligning well with PGCIL’s objectives of timely project execution and optimized resource utilization under the RDSS framework. The reduced construction footprint also supports ecofriendly deployment in coastal and forest-adjacent zones. In view of the above, we firmly believe that adopting Steel Caisson Foundation type monopoles for the Andaman & Nicobar transmission project can deliver tangible benefits in terms of time, cost, constructability and environmental stewardship, compared to conventional base-plated monopoles with pile foundations. For your ready reference, we are enclosing: • The Appreciation Letter received from PSPCL, and • Photographs and Structure geometry of the Steel Caisson type monopole executed under the said project. We respectfully request PGCIL to consider this alternative solution and permit further technical evaluation and discussions to assess its suitability for implementation in the project. | Bidders to quote as per the provisions of the Bidding Documents. |