| Sl. No. | # Volume/ Section/ Description | # Clauses | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- |
| Volume-I: Condition of Contracts |  |  |  |  |
|  | ITB Clause 14.1, ITB, Section-II | Bids shall remain valid for the period of six months after the date of opening of Techno - Commercial Part i.e. First Envelope, prescribed by the Employer, pursuant to ITB Sub-Clause 20.1. A bid valid for a shorter period shall be rejected by the Employer as being non-responsive. | Please reduce the Bid Validity from 6 Months to 1 Month from the date of opening of Techno - Commercial Part | Provisions of the Bidding Documents remain unchanged. |
|  | ITB 24.1 (c), BDS, Section-III | The Time for Completion shall be as under: Sl. No.; Description; Duration in months from the effective date of Contract. (I); Taking Over by the Employer upon successful Completion of following elements of the 765kV Reactor Package 7RT-17-BULK for 30X80MVAR, 765kV 1-Ph Reactors under Bulk Procurement of 765kV and 400kV class Transformers and Reactors of various Capacities under Lot-4.; Remark (Indicative Period in Months from Award). (i); Unit-1; 18 Months; Engineering: 0-24 months Dispatch: 15-33 months 2 units in each month (15-25 months) 1 unit in each month (26-33 months) Receipt at site: 16-34 months 2 units in each month (16-26 months) 1 unit in each month (27-34 months) Erection & Ready for Commissioning:18-36 months 2 units in each month (18-28 months) 1 unit in each month (29-36 months). (ii); Unit-2; 18 Months. (iii); Unit-3; 19 Months. (iv); Unit-4; 19 Months. (v); Unit-5; 20 Months. (vi); Unit-6; 20 Months. (vii); Unit-7; 21 Months. (viii); Unit-8; 21 Months. (ix); Unit-9; 22 Months. (x); Unit-10; 22 Months. (xi); Unit-11; 23 Months. (xii); Unit-12; 23 Months. (xiii); Unit-13; 24 Months. (xiv); Unit-14; 24 Months. (xv); Unit-15; 25 Months. (xvi); Unit-16; 25 Months. (xvii); Unit-17; 26 Months. (xviii); Unit-18; 26 Months. (ix); Unit-19; 27 Months. (xx); Unit-20; 27 Months. (xxi); Unit-21; 28 Months. (xxii); Unit-22; 28 Months. (xxiii); Unit-23; 29 Months. (xxiv); Unit-24; 30 Months. (xxv); Unit-25; 31 Months. (xxvi); Unit-26; 32 Months. (xxvii); Unit-27; 33 Months. (xxviii); Unit-28; 34 Months. (xxix); Unit-29; 35 Months. (xxx); Unit-30; 36 Months. Note: The Unit mentioned above includes the aforesaid Reactor (including Insulating Oil) and any other item/equipment/material/services (as per BoQ/Price Schedules) to be supplied alongwith the said Reactor. The said item/ equipment/ material/ services (as per BoQ/Price Schedules) to be supplied along with the aforesaid Reactor (including Insulating Oil) shall be suitably intimated by POWERGRID during execution of the Contract prior to scheduled dispatch of the Reactor. | We intend to participate in the aforesaid tender wherein it is proposed from our end that Dispatch of the jobs may be between 24 to 32 months with 04 jobs per months accordingly Erection and ready for commissioning of the jobs may be between 28-36 Months with 04 jobs per months. Request your kind consideration | Provisions of the Bidding Documents remain unchanged. |
|  | Clause 3.0, IFB, Section-I | POWERGRID, therefore, invites bids from eligible bidders for the following package for this Bulk Procurement on Domestic Competitive Bidding basis under secured e-procurement procedure: 765kV Reactor Package 7RT-17-BULK for 30X80MVAR, 765kV 1-Ph Reactors under Bulk Procurement of 765kV and 400kV class Transformers and Reactors of various Capacities under Lot-4 | The Scope requires suppling 30 Units of 80 MVAr 765kV Reactors. We request to kindly keep the Bulk Procurement of Max. 7-10 units in a single Tender. Alternatively, please review the possibility of Splitting the quantity in Award Criteria. | Provisions of the Bidding Documents remain unchanged. |
|  | ITB Clause 31.1, ITB, Section-II | Subject to ITB Clause 32, the Employer will award the contract to the successful Bidder (also referred to as the L1 Bidder) whose bid has been determined to be substantially responsive and to be the lowest evaluated bid, further provided that the Bidder is determined to be qualified, as per the Qualification Requirement specified in Annexure-A (BDS) to perform the contract satisfactorily. |  |  |
| Volume-II: Technical Specifications |  |  |  |  |
|  | Cl. No 7.1.2 of Technical Specification, 765kV Shunt Reactor, C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | The requirement of post weld heat treatment of tank/stress relieving shall be based on recommendation of IS 10801. | IS 10801 is applicable to pressurize piping and pressure vessel. As inside pressure of transformer tank is approx. 1 kg/cm2, reactor tank does not come in pressure vessel category. Hence, this clause is not applicable. | Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No 7.1.6 of Technical Specification, 765kV Shunt Reactor, C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | The base of each tank shall be so designed that it shall be possible to move the complete transformer unit by skidding in any direction without damage when using plates or rails and the base plate shall have following minimum thickness: | MS Plate IS 2062:2011 refer IS 1730:1989 for dimension of steel plate. 26mm thk Plate is not in IS standard, alternate solution is 25mm thk plate. Hence requesting for length of tank over 5m but less than 7.5m plate thickness shall be 25 mm thk. Kindly accept. | Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No. 14.7.2 of Technical Specification, SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | All valves shall be painted with a shade (preferably red or yellow) distinct and different from of main tank surface and as per the painting system and procedure specified. | There is no such painting system and procedure specified in technical specification and in Annexure- E. Painting specification shall be follwed as per PGCIL approved supplier recommendation. Customer acceptance required. Gate and Globe valve only handle to be painted for identification. Kindly confirm | Bidder shall quote meeting the requirement of bidding documents |
|  | Section–Project, Rev.00 | Cable length | Kindly provide the below distance for cable length consideration - Distance between CMB1 to CMB2. - Distance between spare transformer to CMB1 or CMB2, if any | Bidding document is amply clear. Bidder shall quote meeting requirement of clause no. 2.2 (e) of Section Project. |
|  | Section–Project, Rev.00 & Reactor Spec Rev08 | 2.1 vi) In Bid price schedule two (2) types of 765kV bushings are available. i) Seismic zone-III (Minimum requirement) ii) Seismic Zone V & 765kV Reactor Spec Rev08 Annexure-Q page 3 of 5: Require number of holes in bushing flange (D5xN): Dia 32 x 12no. | Note that, to meet the seismic qualification of zone-V, bushing flange will have 16no holes instead of 12no holes. Bushings for zone-III will have 12holes as per specifications. This is for your information & approvals. Kindly Accept | Bushing shall be supplied meeting the TS requirement. Change of any technical/physical parameters shall have problem in interchangeability of bushing, hence bidder is requested to comply with TS requirement. However, change of number of holes in bushing for seismic zone-V may be accepted with suitable arrangements/adapter to comply with the interchangeability requirement in line with TS. |
|  | Price schedule-1 (BPS) | 1.1kV grade control cables (PVC insulated) along with lugs, glands, straight joints & accessories etc. | 1. Please confirm the cable mentioned in BPS (Price schedule) is meant for cabling between Reactor to IMB to CMB only. 2. And in the absence of cable type area size the same will be supplied as per Hitachi Energy standard practice/as per past supply to PGCIL. 3. Cables along with lugs, glands etc from CMB to control room are not in our scope. | Bidding document is amply clear. Bidder shall quote meeting the requirement of bidding documents |
|  | Price schedule-1 (BPS) | 1.1kV grade power cables (PVC insulated) along with lugs, glands, straight joints & accessories etc. |  |  |