| Sl. No. | # Volume/ Section/ Description | # Clauses | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- |
| Volume-I: Condition of Contracts |  |  |  |  |
|  | ITB Clause 11.3, BDS, Section-III | Bidders shall give a breakdown of the prices in the manner and detail called for in the Price Schedules. Where no Price Schedules are included in the Bidding Documents, Bidders shall present their prices in the following manner: ………….. Schedule 1 Plant and Equipment (including mandatory Spares) to be supplied including Type Test Charges Schedule 2 Local Transportation, In-transit insurance, loading and unloading (NOT APPLICABLE) # Schedule 3 Installation Services ……………. ……………….. # Bidders are not required to quote the Local Transportation, In-transit insurance, loading and unloading charges (hereinafter referred to as F&I charges) in their bid. Prices regarding F&I charges shall be finalized with the Contractor based on actual destination decided by Employer prior to scheduled dispatch of the equipment in the following manner: - After decision in respect of Destination has been taken by Employer, Contractor shall be asked to submit F&I charges for the finalized destination along with documentary evidence towards justification of prices such as copy of Rate Contract entered into by Contractor, Quotation etc. This activity shall be started preferably five months prior to the scheduled dispatch of the Equipment. | As site is not known to us at bidding stage, we are considering all 30 reactors are required for one site. If there are multiple sites, PGCIL to provide additional charges for site ETC activities. | Provisions of the Bidding Documents remain unchanged. |
|  | GCC Clause 21.1, SCC, Section-V | Time for Completion: ……………………………… ……………………………….. Note: The Unit mentioned above includes the aforesaid Reactor (including Insulating Oil) and any other item/equipment/material/services (as per BoQ/Price Schedules) to be supplied alongwith the said Reactor. The said item/ equipment/ material/ services (as per BoQ/Price Schedules) to be supplied along with the aforesaid Reactor (including Insulating Oil) shall be suitably intimated by POWERGRID during execution of the Contract prior to scheduled dispatch of the Reactor. | Only one bushing manufacturer has conducted seismic test for Zone V. Dependency on single vendor may impact on reactor delivery as per your requirement. Hence, we request you to do not charge LD on us because of the delay in Seismic test for Zone -V. | Provisions of the Bidding Documents remain unchanged. |
|  | GCC Clause 21.2, SCC, Section-V | If the Contractor fails to comply with the Time for Completion in accordance with Clause GCC 21 for the whole of the facilities, (or a part for which a separate time for completion is agreed) then the Contractor shall pay to the Employer a sum equivalent to 0.05% (zero point zero five percent) of the Contract Price for the whole of the facilities, (or a part for which a separate time for completion is agreed) as liquidated damages for such default and not as a penalty, without prejudice to the Employer's other remedies under the Contract, for each day which shall elapse between the relevant Time for Completion and the date stated in Taking Over Certificate of the whole of the Works (or a part for which a separate time for completion is agreed) subject to the limit of five percent (5%) of Contract Price for the whole of the facilities, (or a part for which a separate time for completion is agreed). ………………………….. |  |  |
| Volume-II: Technical Specifications |  |  |  |  |
|  | Cl. No 1.3 of Technical Specification, 765kV Shunt Reactor, C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | Any material and equipment not specifically stated in this specification, but which are necessary for satisfactory operation of the equipment shall be deemed to be included unless specifically excluded and shall be supplied without any extra cost. | Our offer shall be with fittings & accessories as per technical specification, which is suitable for satisfactory operation of reactor. Any additional material and equipment if required shall be provided with cost implication. Any civil work related to foundation etc are not in bidder scope. | Bidding document is amply clear. Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No 3.5 of Technical Specification, 765kV Shunt Reactor , C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | The Contractor shall despatch the Reactor filled with dry air at positive pressure. The necessary arrangement shall be ensured by the contractor to take care of pressure drop of dry air during transit and storage till completion of oil filling during erection. A dry air pressure testing valve with necessary pressure gauge and adaptor valve shall be provided. The dry air cylinder(s) provided to maintain positive pressure can be taken back by the contractor after oil filling. | Transformer can be stored with dry air-filled condition upto 6 months after dispatch from factory. For longer storage, transformer need to be filled with oil as per OEM manual. | Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No 7.1.2 of Technical Specification, 765kV Shunt Reactor , C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | The requirement of post weld heat treatment of tank/stress relieving shall be based on recommendation of IS 10801. | IS 10801 is applicable to Pressurize Piping and Pressure vessel. As inside pressure of transformer tank is approx. 1 kg/cm2 and hence not come to Pressure vessel category. Hence, not applicable. | Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No 7.1.6 of Technical Specification, 765kV Shunt Reactor, C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | The base of each tank shall be so designed that it shall be possible to move the complete transformer unit by skidding in any direction without damage when using plates or rails and the base plate shall have following minimum thickness: | MS Plate IS 2062:2011 refer IS 1730:1989 for dimension of steel plate. 26mm thick Plate is not in IS standard, alternate solution is 25mm thick plate. Hence requesting for length of tank over 5m but less than 7.5m plate thickness shall be 25 mm thick. Kindly accept. | Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No. 7.4 of Technical Specification, SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | 7.4 Foundation, Roller Assembly & Anti Earthquake Clamping Device The Reactor shall be placed directly on concrete plinth foundation. To facilitate the movement of reactor to its foundation over rail track, bi-directional flanged rollers shall be provided. It shall be suitable for fixing to the under carriage of Reactor. The rail track gauge shall be 1676 mm. Two rails shall be provided as per the drawing mentioned at Annexure-C. | Rails shall not be in bidder scope. Also, drawing referred in Annexure C is not available with the given specification Rev08. Kindly provide the drawing. | Bidder shall refer clause 3 of Section Project. Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No. 7.8, 7.9, 7.10 & 22.1 (i) of Technical Specification, SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | 7.8 Pressure Relief Device suitable canopy shall be provided to prevent ingress of rain water. 7.9 Sudden Pressure Relay suitable canopy shall be provided to prevent ingress of rain water. 7.10 Buchholz Relay suitable canopy shall be provided to prevent ingress of rain water. 22.1 (i) Magnetic oil level gauge | Canopy shall be provided as per bidder standard practice. If any specify requirement, kindly share the drawing of canopy to consider in our scope of supply. | Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No. 14.1 of Technical Specification,SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | All valves upto and including 100 mm shall be of gun metal or of cast steel/cast iron. Larger valves may be of gun metal or may have cast iron bodies with gun metal fittings. They shall be of full way type with internal screw and shall open when turned counter clock wise when facing the hand wheel. | As all Butterfly valve above 100mm are of Cast Iron bodies and brass fittings. For 100mm and 80mm Butterfly valve used at radiator also need to supply as Cast Iron bodies and brass fitting which is superseding the technical specification requirement of Cast Iron valve(i.e cast iron bodies and mild steel fittings). As we are superseding the technical specification requirement. Customer acceptance required. | Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No. 14.6 of Technical Specification,SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | Gland packing/gasket material shall be of “O” ring of nitrile rubber for all the valve‟s flanges. All the flanges shall be machined. | All “O” ring used for Valve mounting flange are as per technical specification and of “NBR” material. Valve Gland Packing is of “PTFE” (Teflon) material suitable to transformer oil and atmospheric air. PTFE required for better Oil sealing purpose compared to NBR as per Approved valve supplier. Customer acceptance required. | Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No.17.1.1 & 17.1.2 of Technical Specification, 765kV Shunt Reactor , C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | 17.1.1. All required power & control cables including optical cable, patch chord (if any) upto Common MB shall be in the scope of contractor. Further, any special cable between CMB to switchyard panel room/control room shall be under the present scope. 17.1.2. Fiber optic cable, power cable, control cables, as applicable, between CMB to switchyard panel room/control room and power supply (AC & DC) to MB and integration of above said IEC-61850 compliant equipment with Substation Automation System shall be under the scope of EPC contractor. | All power & control cables from transformer / Reactor accessories to marshalling box & CMB shall be in Bidder's scope of supply. As per Sr. No. 16 to 20 (cables) of Schedule - 1 of price schedule, we understand this requirement is for special cable between CMB to switchyard panel room / control room. Kindly confirm our understanding is correct. | Bidder shall refer clause 2.2 of Section Project. Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No. 22.(xxix) of Technical Specification, SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | xxix) All Cables (Power, control and shielded / twisted pair for 4-20mA cable from Reactor MB, etc. (as applicable) to CMB and CMB to employer’s C&R panel shall be under the present scope. Any special cable if required to be included upto employer’s C&R panel. | All Cables (Power, control and shielded / twisted pair for 4-20mA cable from Reactor MB, etc. (as applicable) to CMB shall be in Bidders scope of Supply. As per Sr. No. 16 to 20 (cables) of Schedule - 1 of price schedule, we understand this requirement is for special cable between CMB to switchyard panel room / control room. Kindly confirm our understanding is correct. | Bidder shall refer clause 2.2 of Section Project. Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No. 23.2 of Technical Specification, SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | Type Tests on fittings: Type test reports of following Bushing & accessories, shall be furnished by the contractor along with drawings. a) Bushing Type Test as per IS/ IEC:60137 for all voltage class (Seismic test on 800kV Bushings) b) Marshalling & Common Marshalling Box and other outdoor cubicle (IP-55) | Only one bushing manufacturer has conducted seismic test for Zone V. Dependency on single vendor may impact on reactor delivery as per your requirement. Hence, we request you to accept the reactor along with seismic calculations of the bushing | Seismic test for Zone-V is applicable for above Bushing. As per CEA letter dated 22.04.2024, Seismic Calculations shall be acceptable. Further seismic calculation shall be certified by NABL Labs as per TS requirement. It is further mentioned that contractor should carry out seismic test (successfully passed) on above bushing within one year from the date 22.04.2024 and submit report to POWERGRID. |
|  | GTR Rev 1, Annexure B | SEISMIC WITHSTAND TEST PROCEDURE | Seismic withstand test is not applicable on offered reactors. Kindly confirm. | Bidder may refer Annexure-B of Section-Technical Specification., 765kV Shunt Reactor, Rev 8 regarding requirement of tests to be conducted on reactor. Further bidder shall design the reactor to withstand seismic requirements as per TS. Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No 7.1.8 of Technical Specification, 765kV Shunt Reactor, C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | Tank, tank cover and associated structure should be adequately designed to withstand, without damage or permanent deflection / deformation, the forces arising out of normal oil pressure, test pressures, vacuum, seismic conditions, and short circuit forces specified. | There is contradiction in the requirement. We understand the permanent deflection will be acceptable up to the values specified in clause no. 17 (ii) of DOC. No.: POWERGRID/STD/TEST PROCEDURE/TR-RT/REV02. Page No. 52 of 69. Kindly confirm. | Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No. 7.2.7 & 14.7.1.7 of Technical Specification, SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | Clause No.7.2.7: The Reactor shall be provided with a 150 mm nominal diameter butterfly valve and bolted blanking plate, gasket and shall be fitted at the highest point of the Reactor for maintaining vacuum in the tank. Clause No.14.7.1.7: Valve for vacuum application on Tank: Type Gate | Since there is contradictory requirement in the specification in two different clauses. Our preference is 100 mm Gate valve. Customer acceptance required. | Gate type valve shall be provided for vacuum application. Bidder shall quote meeting the requirement of bidding documents. |
|  | Cl. No. 7.19.14 of Technical Specification, SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | Winding paper moisture shall be less than 0.5% | Noted, however testing shall be done with Karl Fischer method. Kindly confirm. | Bidder shall quote meeting the requirement of bidding documents |
|  | Cl. No. 14.7.2 of Technical Specification, SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | All valves shall be painted with a shade (preferably red or yellow) distinct and different from of main tank surface and as per the painting system and procedure specified. | There is no such painting system and procedure specified in technical specification and in Annexure- E. Painting specification shall be followed as per PGCIL approved supplier recommendation. Customer acceptance required. | Bidder shall quote meeting the requirement of bidding documents |
|  | Clause No. 2.2 b (ii) of Section Project | Seismic Zone V requirements. | We further wish to inform you that we will first supply reactors with bushings suitable to seismic zone - III & reactors with bushing suitable for seismic zone - V then after. | The schedule of delivery of reactors shall be as per Bidding documents. Bidder shall quote meeting the requirement of bidding documents |
|  | Clause No. 2.2 e of Section Project | One No. CMB shall be supplied for 2 x 1-Ph or 3 x 1-Ph 765KV Class Reactor unit at one location. | Our offer is for 30 Nos. shunt reactor, and we are considering only 10 No. CMB against 30 Nos. Shunt reactors. Based on 3 x 1 Phase 765 kV class reactor. | Bidder may refer clause 2.2 of Section Project regarding the requirement of CMB. Bidder shall quote meeting the requirement of bidding documents |
|  | S. No. 16 to 20 of BPS | Cables 1.1 kV GRADE 4Cx16 SQMM (PVC) POWER CABLE : 8kM 4 PAIR, 0.5SQMM SCREENED CABLE : 16 kM 1.1 kV GRADE 19Cx1.5 SQMM CONTROL CABLE : 8 kM 1.1 kV GRADE 3Cx2.5 SQMM CONTROL CABLE : 8 kM 1.1 kV GRADE 5Cx2.5 SQMM CONTROL CABLE : 8 kM | As per our control scheme cables (PGCIL Standard cores & cable size) required between individual marshalling box to CMB shall be as follow instead of required cable in BPS. 1.1 kV GRADE 2Cx6 SQMM (PVC) POWER CABLE : 8kM 5 PAIR, 2.5SQMM SCREENED CABLE : 16 kM 1.1 kV GRADE 19Cx1.5 SQMM CONTROL CABLE : 8 kM 1.1 kV GRADE 14Cx2.5 SQMM CONTROL CABLE : 8 kM 1.1 kV GRADE 10Cx2.5 SQMM CONTROL CABLE : 8 kM If cables required more than specified length shall be provided with cost implication. Kindly confirm | Bidder shall quote meeting the requirement of bidding documents |
|  | S. No. 1,2 of BPS | 80 MVAR Reactor and Insulating Oil | Request PGCIL to split supply NOA between Main job and the spares requirement | Bidder shall quote meeting the requirement of bidding documents |