| ### Sr. No | ### REFERENCE | ### BIDDER’S CLARIFICATION | ### POWERGRID’S REPLY |
| --- | --- | --- | --- |
| 1 | Volume-II of Part II Section -02 -OPGW Specification for Fiber Optic cabling & associated items | 1.) Please confirm, Provided OPGW technical parameters in section-2 of OPGW technical specification -Clause No-2.1.3.2 are also applicable to Typical transmission line details provided in Appendix-A document of Table A1 (2) and Table A1(3) for Medium and heavy Snow regions. (or) please provide the OPGW parameters for medium and heavy snow regions for all transmission lines. 2.)While deriving sag and tension chart for the case of Typical transmission Line details provided in Table A1(3) heavy snow regions-Maximum Allowable Tension limit is exceeding than the required limit of < 45% of UTS at provided Condition "Design tension of Earth wire at (-) 20 Degree C, 25% of Full wind & 25 mm Ice thickness" and at 32 DegreeC Full wind condition Maximum allowable tension limit is meeting the requirement. Please confirm at which condition maximum allowable tension limit to be verified i.e at (-) 20 Degree C, 25% of Full wind & 25 mm Ice thickness" or " 32 DegreeC Full wind condition Maximum allowable tension limit" | In instant query, Bidder may kindly refer Section-II (of Vol.II) in conjunction with provisions mentioned in Section-I (of Vol.II). Parameters of earth wire provided in Vol.II, Appendix-A Table: A-1 (1), (2) & (3) are typical values. Bidder has to design OPGW for links mentioned in Table A-2. Bidder to supply as per the requirements stipulated in bidding documents. |