## Amendment-1
Amendment No.2 to Bidding Documents for Substation package-SS62: EXTENSION OF 400/220KV JATWAL (SAMBA) S/S UNDER NRSS-XLII; EXTENSION OF 400KV JALLANDHAR S/S & 400KV PATIALA S/S UNDER NRSS-XL; Specification No- CC-CS/924-NR2/SS-4049/3/G4
S. No | REFERENCE TO SECTION/ VOLUME | CLAUSE REF. NO. | Existing in Bidding Documents | To be Amended as
1 | SCH 1,2 OF BPS | Mandatory spares for Jalandhar s/s | 33. Mandatory Spares - Power Supply module of each type for B/B Protection - SET - 1 34. Mandatory Spares - Bay Unit module for Bus Bar Protection - EA-1 | 33. Mandatory Spares - Power Supply module of each type for B/B Protection - SET - 1 34. ITEM DELETED
2 | SCH 1,2,3 OF BPS | CRP Panel at Patiala s/s | 2 - Control & Relay Panel - Control panel for 400kV Diameter (For One-half Breaker Scheme) - EA - 1 3-Augmentation of existing 400kV bus bar protection scheme-SET 1 | ITEM DELETED ITEM DELETED
3 | Section Project | Extension of 400 kV Patiala substation: Clause 3.3(ii) | Complete Relay and Protection system for bays under present scope as per Section Control and Relay Panel. All the Control, protection and relay panels to be installed in the switchyard panel room. The existing bus bar protection scheme is High Impedance Differential Relay type FAC 34 of ALSTOM make and no space is available for tripping Relays in existing panels. Therefore for Bus Reactor bay and future bays CT’s are to be summed up in the SPR and only resultant is to be wired to the Bus Bar Panel. The scope includes the necessary wiring/cabling along with supply of trip relays for extension of Bus Bar & LBB Protection is in the SPR. | Section-Project Rev 01 Complete relay and protection system for 400kV bays as per Section–Control and Relay panels for the substation extension inter-alia Reactor protection, Circuit Breaker Protection and Bus Bar Protection scheme modification.
4 | Section Project | Extension of 400 kV Patiala substation: Clause 3.3(xiii) | NEW CLAUSE | Section-Project Rev 01 No new Control Panel is envisaged for new 400 kV bay in present scope.BCU shall be considered as part of the CB relay panel and necessary CB control shall be provided in Relay panel. Wiring/Scheme modification in existing control panel for interlocking etc. shall be included in the scope of the bidder.Integration of BCUs/RTUs with Gateway/RTU of NTAMC is also under present scope.
5 | SCH 1,2 OF BPS | Mandatory spares for Patiala s/s | 38. Mandatory Spares - Power Supply module of each type for B/B Protection - SET - 1 39. Mandatory Spares - Bay Unit module for Bus Bar Protection - EA-1 | ITEM DELETED
6 | Section Project | Extension of 400 kV Jalandhar substation:Clause 3.2(ii) | Complete Relay and Protection system for bays under present scope as per Section Control and Relay Panel. All the Control, protection and relay panels to be installed in the Switchyard Panel Room (SPR) .The existing bus bar protection scheme is Low Impedance differential relay type RADSS of ABB make. No space is available for tripping Relays in existing panels. Therefore for Bus Reactor bay CT’s are to be summed up in the SPR and only resultant is to be wired to the Bus Bar Panel. The scope includes the necessary wiring/cabling along with supply of trip relays for extension of Bus Bar & LBB Protection is in the SPR. The existing Time Synchronization unit is SNTP (LAN) type. Space is available in Event Logger for the upcoming Bus Reactor bay, however necessary wiring/cabling along with supply of any auxiliary items is in the present scope of work.The existing Time Synchronization unit is SNTP (LAN) type. Space is available in Event Logger for the upcoming Bus Reactor bay, however necessary wiring/cabling along with supply of any auxiliary items is in the present scope of work. | Section-Project Rev 01 Complete Relay and Protection system for bays under present scope as per Section Control and Relay Panel. All the Control, protection and relay panels to be installed in the control room.The existing bus bar protection scheme is Low Impedance differential relay type RADSS of ABB make. Retrofitting of existing bus bar protection with new 400 kV Redundant (1+1) numerical centralised Bus Bar protection scheme as per Section CRP for the complete (existing+present ) 400 kV bays as shown in SLD and additional two numbers 400 kV future bays are under present scope.Retrofitting of differential relay RADSS is under scope.Trip relays,auxiliary CT (if required) etc. may be retained and only those required for present bays and additional two nos. 400 kV future bays shall be supplied.Integration of the alarms and annunciations with localevent logger and NTAMC/RTAMC shall also be in present scope.The existing Time Synchronization unit is SNTP (LAN) type. Space is available in Event Logger for the upcoming Bus Reactor bay, however necessary wiring/cabling along with supply of any auxiliary items is in the present scope of work.
7 | Section Project | Extension of 400 kV Jalandhar substation:Clause 3.2(iii) | Supply of BCU and its integration up to local gateway of NTAMC SCADA as per specification for bays under present scope is included in the contract. However integration with NTAMC SCADA (Alstom make) is considered under a separate package. The scope also include necessary wiring & integration under present bays upto NTAMC SCADA system. | Section-Project Rev 01 Supply of BCU and its integration up to local gateway of NTAMC SCADA as per specification for bays under present scope is included in the contract.The scope also include necessary wiring & integration of present bays upto NTAMC SCADA system.
8 | Section Project | SCOPE Clause 3(ii) | Extension of 400 kV Jalandhar substation with the provision of following bays as per Single Line Diagram: a. One number 400 kV bay for one (1) number 125 MVAr, 420 kV Bus Reactor. | Section-Project Rev 01 Extension of 400 kV Jalandhar substation with the provision of following bays as per Single Line Diagram: a. two number 400 kV bay for one (1) number 125 MVAr, 420 kV Bus Reactor.
9 | Section Project | Extension of 400 kV Jalandhar substation:Clause 3.2(d)(iii) | Switchyard Panel Rooms | clause deleted,Section-Project Rev 01
10 | SCH 3OF BPS | Extension of 400 kV Jalandhar civil works | Switchyard Panel Room - Civil Works.-30M2 | ITEM DELETED
11 | SCH 1,2,3OF BPS | Extension of 400 kV Jalandhar Illumination Switchyard | Illumination System for switchyard panel room of 6 m length-SET 1 | ITEM DELETED
12 | SCH 1,2,3OF BPS | Extension of 400 kV Jalandhar Air conditioning & Ventilation System | Air conditioning system for Switchyard Panel Room of 6m length-SET 1 | ITEM DELETED
13 | Section Project | Extension of 400 kV Jalandhar substation:Clause 3.2(a)(x) | Illumination and Air conditioning of Switchyard panel room as per BPS. | clause deleted,Section-Project Rev 01
14 | Section Project in Vol-II Bidding Documents | The existing file 'Sec_Project' stands replaced with 'Sec_Project_R01'
15 | Price Schedule in Vol-III of Bidding Document | The existing file 'SS62-BPS' stands replaced with 'SS62-BPS Rev-I'