## Clarification-1
Clarifications No.1 to Bidding Documents for Substation package-SS62: EXTENSION OF 400/220KV JATWAL (SAMBA) S/S UNDER NRSS-XLII; EXTENSION OF 400KV JALLANDHAR S/S & 400KV PATIALA S/S UNDER NRSS-XL; Spec. No.: CC-CS/924-NR2/SS-4049/3/G4
S. No | REFERENCE TO SECTION/VOLUME | CLAUSE NO./PAGE NO. | DESCRIPTION IN BIDDING DOCUMENTS | CLARIFICATIONS RAISED BY BIDDER | POWERGRID REPLY
1 | 1 No. of 400kV Reactor Bay Jalandhar SS | 33. Mandatory Spares - Power Supply module of each type for B/B Protection - SET - 1 34. Mandatory Spares - Bay Unit module for Bus Bar Protection - EA - 1 |  | Suppy of these mandatory spares are not applicable as it is not part of main line item supply. Kindly confirm. | Pls refer Amendment 2.
2 | 1 No. of 400kV Reactor Bay Patiala SS | 2 - Control & Relay Panel - Control panel for 400kV Diameter (For One-half Breaker Scheme) - EA - 1 |  | We understand as per SLD & BPS (CB relay panel - 1nos) Reactor bay is in existing diameter. So please re- confirm on control panel requirement for complete diameter. | Pls refer Amendment 2.
3 | 1 No. of 400kV Reactor Bay Patiala SS | 5 - Control & Relay Panel - RTU's augmentation - SET - 1 |  | As this is exiting NTAMC CAT-II station, Hence NTAMC integration may be required also. Kindly confirm. | Bidders understanding is generally in order.
4 | 1 No. of 400kV Reactor Bay Patiala SS | 6 - Control & Relay Panel - Time synchronisation equipment - EA - 1 |  | As this is exiting NTAMC CAT-II station. So Kindly re- confirm on Time synchronisation equipment requirement. | Bidders understanding is generally in order.Bidder is to quote as per BPS.
5 | 1 No. of 400kV Reactor Bay Patiala SS | 38. Mandatory Spares - Power Supply module of each type for B/B Protection - SET - 1 39. Mandatory Spares - Bay Unit module for Bus Bar Protection - EA - 1 |  | Suppy of these mandatory spares are not applicable as it is not part of main line item supply. Kindly confirm. | Pls refer Amendment 2.
6 | Clause no- 2.2-b-ii, page no 7 of 20 | The existing bus bar protection scheme is Low Impedance differential relay type RADSS of ABB make. No space is available for tripping Relays in existing panels. Therefore for Bus Reactor bay CT’sare to be summed up in the SPR and only resultant is to be wired to the Bus Bar Panel. The scope includes the necessary wiring/cabling along with supply of trip relays for extension of Bus Bar & LBB Protection is in the SPR. |  | We understand existing ABB make RADSS BB relay have sufficienet CT Input/card for present bays ABB augmentation. Only trip/auxuliary relay & necessary wiring/cabling is required for BB augmenation. And present bays CT to be sumped up in reactor protection panel. Kindly confirm on our understing. | Pls refer Amendment 2.
7 | Clause no- 2.2-b-ii, page no 7 of 20 | The existing Time Synchronization unit is SNTP (LAN) type. Space is available in Event Logger for the upcoming Bus Reactor bay, however necessary wiring/cabling along with supply of any auxiliary items is in the present scope of work. |  | We don't understand why existing GPS details are provided here. Howevever existing event logger details are reuired. We understand event logger integration are part of present scope. Only auxiliary relay/contactors for input multipication shall be part of reactor CRP. Kindly confirm on our understing. | Bidders understanding is generally in order.Existing event logger is ALSTOM make C264.
8 | Clause no- 3.3-b-iii, page no 8 of 20 | The existing bus bar protection scheme is High Impedance Differential Relay type FAC 34 of ALSTOM make and no space is available for tripping Relays in existing panels. Therefore for Bus Reactor bay and future bays CT’s are to be summed up in the SPR and only resultant is to be wired to the Bus Bar Panel. |  | We understand reactor bay is in existing diameter. Hence these are no future CB/bay. And present bays CT to be sumped up in reactor protection panel only. Kindly confirm on our understing. | As reactor is to be installed in parallel to existing 125 MVAr Bus reactor bay hence no bus bar augmmentation is required.Pls refer Amendment 1.
9 | Clause no- 3.3-b-iii, page no 9 of 20 | The existing RTU (model C264) and SCADA (ETERRA Control) system at Patiala substation has been supplied from ALSTOM. The contractor shall be responsible for updating of displays, database, reports etc. of the SCADA system. |  | As this is exiting NTAMC CAT-II station, Hence NTAMC integration may be required also. Kindly confirm. | RTU Augmentation and integration with NTAMC gateway at Patiala s/s end shall be in the scope of Bidder.
10 | Panel Room Location of respective bays | General |  | The location of the panel room of respective bays under present scope is not indicated in the layouts provided for all three substations along with the tender documents. Thus, we are unable to estimate the power & control cabling quantities. Request you to provide the same. Also, request you to please indicate the existing trench route in the layout. | Panels for Jallandhar substation is to be placed in control room building.For Sambha and Patiala s/s panels are to be placed in switchyard panel room (SPR) in vicinity of bays under present scope.Further bidders are requested to visit the substation sites in accordance to clause no 3.5 of section project, technical specification.
11 | Sectional draewings of existing substation | General |  | The sectional drawing of the existing substation are not provided (only SLD & plan is provided) for all three substations along with the tender documents. Request you to provide the same which will enable us to estimate the hardware quantities. | Available major relavant drawings and details of existing old substation installations are enclosed with bidding documents. Other drawings & details, if avaialbel will be shared with the successful bidder during detailed engineering..Further bidders are requested to visit the substation sites in accordance to clause no 3.5 of section project, technical specification.
12 |  |  |  | Kindly clarify the make of 400kV CB for which CSD is required as per the BOQ. | 400 kV CB available at Saharanpur substation are of CGL make.