| S.N |  | Ref clause in the Specification |  |  |  |  |  |  |  | Description |  |  |  |  |  | Query raised by Bidder |  |  |  |  | POWERGRID's Reply |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ABB clarifications |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| General |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - . |  | General |  |  |  |  |  |  |  |  |  |  |  |  |  | Please specify creepage distance to be considered. |  |  |  |  | Gazuwaka S/s is identified as Coastal Area, however other S/s viz. Hosur, Madhugiri, Dharmapuri, Hiriyur, Pugalur (AIS) S/s Pugalur HVDC (GIS) S/s may be considered as Non Costal Area. In view of above creepage requirement as specified in TS shall be considered. |  |  |
|  |  | 400kV Extn. S/s at Hosur (AIS) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.1.4 e) Pg No. 4 of 30 |  |  |  |  |  |  |  | Switchyard Panel Room |  |  |  |  |  | As per Site visit conducted at our end, it is observed that there is sufficient space in Existing Switchyard Panel room for present scope of Bus Reactor Control & Protection panels. Hence New line item of Switchyard Panel room shall be deleted from Bid Price Schedule. |  |  |  |  | Refer S.No 01 of Amendment 01 (Part-2). |  |  |
|  |  | Tender GA/SLD drawing Existing Plan & Section drawing, C/ENGG/SRSS-XXV/SR/HOSUREXTN/ SLD/001 Rev 0 C/ENGG/SRSS-XXV/SR/HOSUREXTN/ GA/001 Rev 0 O12191-E-SY-S Y-EL-3002(2 sheets) |  |  |  |  |  |  |  |  |  |  |  |  |  | Tender GA & SLD drawings are not matching with Existing Plan & Section drawings. However we shall proceed as per Tender GA drawings shared by PGCIL. Please confirm. |  |  |  |  | It is clarified that bay allocation for 125 MVAr Bus reactor under present scope shall be as per SLD drg. No. C/ENGG/SRSS-XXV/SR/HOSUREXTN/ SLD/001 Rev 0. Existing drg. No. O12191-E-SY-SY-EL-3002 not to be referred for bay allocation. |  |  |
|  |  | Existing SAS drawings, 3269PN569/70-3-002 |  |  |  |  |  |  |  | Existing SAS drawings |  |  |  |  |  | As per Tender documents, Substation Automation System is present at Existing Substation however Augmentation line item is not available in Bid Price Schedule. |  |  |  |  | SAS is not envisaged at the Hosur S/s. The existing architecture (drawings No. 3269PN569/70-3-002) shows HMI/DR PC which is used for configuration of Protection relays only without any control feature. Local control of respective bays has been provided from control panels. For remote control from NTAMC separate BCU has been provided in existing system. The similar arrangement is to be considered for bay covered under present scope. Line item for augmentation of control panel and BCU is already there in BPS. Bidder to quote accordingly. |  |  |
|  |  | Bid Price Schedule |  |  |  |  |  |  |  | Augmentation of existing 400kV Control Panel (Bus Scheme as per SLD) |  |  |  |  |  | Please provide location of Existing 400kV Control Panel. |  |  |  |  | Existing 400kV Control Panel is located at Control Room building. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.1.2 d) Pg No. 4 of 30 |  |  |  |  |  |  |  | Fire Protection System |  |  |  |  |  | Request you to furnish Existing Firefighting drawings for present scope of Extension works. Also provide tap off point for Extension of Main Header. |  |  |  |  | Bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.1.2 c) Pg No. 4 of 30 |  |  |  |  |  |  |  | The CSD for existing tie breaker shall be placed in the CB panel of main breaker being supplied under present scope. |  |  |  |  |  | Please furnish make of Existing Tie Circuit Breaker for present scope of CSD supply for Existing Tie Circuit Breakers. |  |  |  |  | Existing Tie Circuit Breaker is CGL make. |  |  |
|  |  | General |  |  |  |  |  |  |  | LT Switchboards |  |  |  |  |  | Please confirm sufficient feeders in Existing LT Switchboards (MSB, ACDB, DCDB, MLDB, ELDB) for present scope of Extn. Works |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.1.2 d) Pg No. 4 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | We understand that existing Fire Fighting System of existing Substations is adequate to cater to requirement of additional Reactor / Hydrant to be installed as per respective scope. Please confirm our understanding. |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.1.2 d) Pg No. 4 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | HVWS system for reactors, the provision to integrate the reactor fire protections into EXISTING Fire Alarm & Annunciation in EXISTING control room & Firefighting Building shall be available. The present scope is limited to termination of signal cables from DV LCP to EXISTING Fire Alarm & Annunciation Panel. Please Confirm. |  |  |  |  | Confirmed. The present scope is termination of signal cables from DV LCP to EXISTING Fire Alarm & Annunciation Panel and Integration with NTAMC BCU. |  |  |
|  |  | Section Project Bid Price Schedule |  |  |  |  |  |  |  | Lightning Protection (DSLP) |  |  |  |  |  | For Lightning protection of present scope or work, please provide line item for Lightning Mast in Bid Price Schedule |  |  |  |  | Refer S.No 02 of Amendment 01 (Part-2). |  |  |
|  |  | General |  |  |  |  |  |  |  |  |  |  |  |  |  | Please provide following drawings for Extension S/s 1) Existing Outdoor Lighting Layout & Distribution diagram 2) Existing DSLP Layout 3) Existing Panel arrangement layout of Switchyard Panel Room & Control Room Building 4) Existing LT Board drawings (ACDB, DCDB, MLDB & ELDB) 5) Existing HVWS layout 6) Existing Firefighting Annunciation Panel drawings |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | Extension of 400kV Hosur Substation |  |  |  |  |  |  |  | NTAMC gateway / SCADA |  |  |  |  |  | Please confirm that configuration and Integrating works is limited only to bidder supplies and Alstom make gateway configuration and integration is not in bidder's scope. |  |  |  |  | The configuration and Integrating works with existing gateway at Housr s/s for present bay is covered under bidder’s scope. |  |  |
|  |  | 400kV Extn. S/s at Madhugiri (AIS) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Section Project Bid Price Schedule, General |  |  |  |  |  |  |  | Switchyard Panel Room |  |  |  |  |  | Please confirm sufficient space will be available in Existing Switchyard Panel room for present scope of Bus Reactor Control & Protection panels. |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.2.2 b) iv) Pg No. 5 of 30 |  |  |  |  |  |  |  | Substation Automation System |  |  |  |  |  | As per Tender documents, Substation Automation System is present at Existing Substation however Augmentation line item is not available in Bid Price Schedule. |  |  |  |  | Refer S.No.3 of Amendment 01 (Part-2). |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.2.2 d) Pg No. 6 of 30 |  |  |  |  |  |  |  | Fire Protection System |  |  |  |  |  | Request you to furnish Existing Firefighting drawings for present scope of Extension works. Also provide tap off point for Extension of Main Header. |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.2.2 c) Pg No. 5 of 30 |  |  |  |  |  |  |  | The CSD for existing tie breaker shall be placed in the CB panel of main breaker being supplied under present scope. |  |  |  |  |  | Please furnish make of Existing Tie Circuit Breaker for present scope of CSD supply for Existing Tie Circuit Breakers. |  |  |  |  | Existing Tie Circuit Breaker is Alstom make. |  |  |
|  |  | General |  |  |  |  |  |  |  | LT Switchboards |  |  |  |  |  | Please confirm sufficient feeders in Existing LT Switchboards (MSB, ACDB, DCDB, MLDB, ELDB) for present scope of Extn. Works |  |  |  |  | Confirmed |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.2.2 d) Pg No. 6 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | We understand that existing Fire Fighting System of existing Substations is adequate to cater to requirement of additional Reactor / Hydrant to be installed as per respective scope. Please confirm our understanding |  |  |  |  | Confirmed |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.2.2 d) Pg No. 6 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | HVWS system for reactors, the provision to integrate the reactor fire protections into EXISTING Fire Alarm & Annunciation in EXISTING control room & Firefighting Building shall be available. The present scope is limited to termination of signal cables from DV LCP to EXISTING Fire Alarm & Annunciation Panel. Please Confirm. |  |  |  |  | Confirmed. The present scope is termination of signal cables from DV LCP to EXISTING Fire Alarm & Annunciation Panel and Integration with NTAMC BCU. |  |  |
|  |  | Section Project Bid Price Schedule |  |  |  |  |  |  |  | Lightning Protection (DSLP) |  |  |  |  |  | For Lightning protection of present scope or work, please provide line item for Lightning Mast in Bid Price Schedule |  |  |  |  | Refer S.No 04 of Amendment 01 (Part-2). |  |  |
|  |  | General |  |  |  |  |  |  |  | Existing drawings are not available |  |  |  |  |  | Please provide following drawings for Extension S/s 1) Existing SLD Drawing 2) Existing Plan Layout with Equipments & busbar connection. 3) Exisitng Section Layout 4) Existing Earthmat Layout 5) Existing Structure Plan & Section Layout 6) Existing Cable Trench Layout 7) Existing Outdoor Lighting Layout & Distribution diagram 8) Existing DSLP Layout 9) Existing Panel arrangement layout of Control Room building 10) Existing SAS Architecture diagram 11) Existing LT Board drawings (ACDB, DCDB, MLDB & ELDB) 12) Existing Busbar CRP drawing |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | 400kV Extn. S/s at Dharmapuri (AIS) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Section Project Bid Price Schedule, General |  |  |  |  |  |  |  | Switchyard Panel Room |  |  |  |  |  | Please confirm sufficient space will be available in Existing Switchyard Panel room for present scope of Bus Reactor Control & Protection panels. |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.3.2 a) iii) Pg No. 7 of 30 |  |  |  |  |  |  |  | Substation Automation System |  |  |  |  |  | As per Tender documents, Substation Automation System is present at Existing Substation however Augmentation line item is not available in Bid Price Schedule. |  |  |  |  | Refer S.No 05 of Amendment 01 (Part-2). |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.3.2 b) Pg No. 7 of 30 |  |  |  |  |  |  |  | Fire Protection System |  |  |  |  |  | Request you to furnish Existing Firefighting drawings for present scope of Extension works. Also provide tap off point for Extension of Main Header. |  |  |  |  | Bidder is advised to visit site as per clause no. 2.4 of section project. The header line is traversing just opposite to the proposed bay. |  |  |
|  |  | Section Project Bid Price Schedule, Item No. 177 |  |  |  |  |  |  |  | CSD for Tie Circuit Breakers |  |  |  |  |  | Please furnish make of Existing Tie Circuit Breaker for present scope of CSD supply for Existing Tie Circuit Breakers. |  |  |  |  | Existing Tie Circuit Breaker is Siemens make.. |  |  |
|  |  | General |  |  |  |  |  |  |  | LT Switchboards |  |  |  |  |  | Please confirm sufficient feeders in Existing LT Switchboards (MSB, ACDB, DCDB, MLDB, ELDB) for present scope of Extn. Works |  |  |  |  | Confirmed |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.2.2 b) Pg No. 7 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | We understand that existing Fire Fighting System of existing Substations is adequate to cater to requirement of additional Reactor / Hydrant to be installed as per respective scope. Please confirm our understanding |  |  |  |  | Confirmed |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.2.2 b) Pg No. 7 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | HVWS system for reactors, the provision to integrate the reactor fire protections into EXISTING Fire Alarm & Annunciation in EXISTING control room & Firefighting Building shall be available. The present scope is limited to termination of signal cables from DV LCP to EXISTING Fire Alarm & Annunciation Panel. Please Confirm. |  |  |  |  | Confirmed. The present scope is termination of signal cables from DV LCP to EXISTING Fire Alarm & Annunciation Panel and Integration with NTAMC BCU. |  |  |
|  |  | Section Project Bid Price Schedule |  |  |  |  |  |  |  | Lightning Protection (DSLP) |  |  |  |  |  | For Lightning protection of present scope or work, please provide line item for Lightning Mast in Bid Price Schedule |  |  |  |  | For Lightning protection (DSLP) calculation of present Bus Reactor bay shall be done by providing GI Earthwire at Existing Tower/Gantries. |  |  |
|  |  | General |  |  |  |  |  |  |  | BCU Panel |  |  |  |  |  | As per site visit conducted at our end, it is observed that BCU panel of Alstom make is Existing for present scope of Bus reactor Bay. Please confirm |  |  |  |  | The existing BCU can be used for Bus reactor bay however work related to remounting/configuration/wiring of existing BCU etc. is covered under present scope of work. |  |  |
|  |  | General |  |  |  |  |  |  |  | Existing drawings are not available |  |  |  |  |  | Please provide following drawings for Extension S/s 1) Existing SLD Drawing 2) Existing Plan Layout with Equipments & busbar connection. 3) Exisitng Section Layout 4) Existing Earthmat Layout 5) Existing Structure Plan & Section Layout 6) Existing Cable Trench Layout 7) Existing Outdoor Lighting Layout & Distribution diagram 8) Existing DSLP Layout 9) Existing Panel arrangement layout of Control Room building 10) Existing SAS Architecture diagram 11) Existing LT Board drawings (ACDB, DCDB, MLDB & ELDB) 12) Existing Busbar CRP drawing |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | 400kV Extn. S/s at Hiriyur (AIS) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Section Project Bid Price Schedule, General |  |  |  |  |  |  |  | Switchyard Panel Room |  |  |  |  |  | Please confirm sufficient space will be available in Existing Switchyard Panel room for present scope of Bus Reactor Control & Protection panels. |  |  |  |  | Confirmed. |  |  |
|  |  | General |  |  |  |  |  |  |  |  |  |  |  |  |  | Please specify creepage distance to be considered |  |  |  |  | Gazuwaka S/s is identified as Coastal Area, however other S/s viz. Hosur, Madhugiri, Dharmapuri, Hiriyur, Pugalur (AIS) S/s Pugalur HVDC (GIS) S/s may be considered as Non Costal Area. In view of above creepage requirement as specified in TS shall be considered. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.4.2 Pg No. 8 of 30 |  |  |  |  |  |  |  | Substation Automation System |  |  |  |  |  | Please confirm whether Existing Substation is having Substation Automation System or not? If yes please share Existing details. |  |  |  |  | Existing Hiriyur substation is not having SAS. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.4.2 c) Pg No. 9 of 30 |  |  |  |  |  |  |  | Fire Protection System |  |  |  |  |  | Request you to furnish Existing Fire fighting drawings for present scope of Extension works. Also provide tap off point for Extension of Main Header. |  |  |  |  | Tapping from the adjacent bus reactor bay Bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.4.2 b) Pg No. 9 of 30 |  |  |  |  |  |  |  | The CSD for existing tie breaker shall be placed in the CB panel of main breaker being supplied under present scope. |  |  |  |  |  | Please furnish make of Existing Tie Circuit Breaker for present scope of CSD supply for Existing Tie Circuit Breakers. |  |  |  |  | Existing Tie Circuit Breaker is Alstom make. |  |  |
|  |  | General |  |  |  |  |  |  |  | LT Switchboards |  |  |  |  |  | Please confirm sufficient feeders in Existing LT Switchboards (MSB, ACDB, DCDB, MLDB, ELDB) for present scope of Extn. Works |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.4.2 c) Pg No. 9 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | We understand that existing Fire Fighting System of existing Substations is adequate to cater to requirement of additional Reactor / Hydrant to be installed as per respective scope. Please confirm our understanding |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.4.2 c) Pg No. 9 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | HVWS system for reactors, the provision to integrate the reactor fire protections into EXISTING Fire Alarm & Annunciation in EXISTING control room & Firefighting Building shall be available. The present scope is limited to termination of signal cables from DV LCP to EXISTING Fire Alarm & Annunciation Panel. Please Confirm. |  |  |  |  | Confirmed. The present scope is termination of signal cables from DV LCP to EXISTING Fire Alarm & Annunciation Panel and Integration with NTAMC BCU. |  |  |
|  |  | Section Project Bid Price Schedule, Lightning Protection (DSLP) |  |  |  |  |  |  |  |  |  |  |  |  |  | For Lightning protection of present scope or work, please provide line item for Lightning Mast in Bid Price Schedule |  |  |  |  | Refer S.No 6 of Amendment 01 (Part-2) |  |  |
|  |  | Bid Price Schedule |  |  |  |  |  |  |  | Augmentation of existing 400kV Control Panel (Bus Scheme as per SLD) |  |  |  |  |  | Please provide drawings of Existing 400kV Control Panel. Also share location of said panel. |  |  |  |  | Relay panel shall be kept in switchyard panel room and control panel for this bay is existing and the same has been kept in control room. The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | General |  |  |  |  |  |  |  | Existing drawings are not available |  |  |  |  |  | Please provide following drawings for Extension S/s 1) Existing SLD Drawing 2) Existing Plan Layout with Equipments & busbar connection. 3) Exisitng Section Layout 4) Existing Earthmat Layout 5) Existing Structure Plan & Section Layout 6) Existing Cable Trench Layout 7) Existing Outdoor Lighting Layout & Distribution diagram 8) Existing DSLP Layout 9) Existing Panel arrangement layout of Control Room building 10) Existing SAS Architecture diagram 11) Existing LT Board drawings (ACDB, DCDB, MLDB & ELDB) 12) Existing Busbar CRP drawing |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | Extension of 400kV Hiriyur substation |  |  |  |  |  |  |  | NTAMC gateway / SCADA |  |  |  |  |  | Please confirm that configuration and Integrating works is limited only to bidder supplies and Alstom make gateway configuration and integration is not in bidder's scope. |  |  |  |  | The configuration and Integrating works with existing gateway at Hiriyur s/s for present bay is covered under bidder’s scope. |  |  |
|  |  | 400kV Extn. S/s at Pugalur (AIS) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Section Project Bid Price Schedule, General |  |  |  |  |  |  |  | Switchyard Panel Room |  |  |  |  |  | Please confirm sufficient space will be available in Existing Switchyard Panel room for present scope of Bus Reactor Control & Protection panels. |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.5.2 a) iii) Pg No. 10 of 30 |  |  |  |  |  |  |  | Substation Automation System |  |  |  |  |  | As per Tender documents, Substation Automation System is present at Existing Substation however Augmentation line item is not available in Bid Price Schedule. |  |  |  |  | Refer S.No 7 of Amendment 01 (Part-2) |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.5.2 c) Pg No. 11 of 30 |  |  |  |  |  |  |  | Fire Protection System |  |  |  |  |  | Request you to furnish Existing Firefighting drawings for present scope of Extension works. Also provide tap off point for Extension of Main Header. |  |  |  |  | Bidder is advised to visit site as per clause no. 2.4 of section project. Tapping to be done from the adjacent Kalivanthapattu bay Line reactor FF system |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.5.2 b) Pg No. 11 of 30 |  |  |  |  |  |  |  | The CSD for existing tie breaker shall be placed in the CB panel of main breaker being supplied under present scope. |  |  |  |  |  | Please furnish make of Existing Tie Circuit Breaker for present scope of CSD supply for Existing Tie Circuit Breakers. |  |  |  |  | Existing Tie Circuit Breaker is CGL make. |  |  |
|  |  | General |  |  |  |  |  |  |  | LT Switchboards |  |  |  |  |  | Please confirm sufficient feeders in Existing LT Switchboards (MSB, ACDB, DCDB, MLDB, ELDB) for present scope of Extn. Works |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.5.2 c) Pg No. 11 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | We understand that existing Fire Fighting System of existing Substations is adequate to cater to requirement of additional Reactor / Hydrant to be installed as per respective scope. Please confirm our understanding |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.5.2 c) Pg No. 11 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | HVWS system for reactors, the provision to integrate the reactor fire protections into EXISTING Fire Alarm & Annunciation in EXISTING control room & Firefighting Building shall be available. The present scope is limited to termination of signal cables from DV LCP to EXISTING Fire Alarm & Annunciation Panel. Please Confirm. |  |  |  |  | Confirmed. The present scope is termination of signal cables from DV LCP to EXISTING Fire Alarm & Annunciation Panel and Integration with NTAMC BCU. |  |  |
|  |  | Section Project Bid Price Schedule |  |  |  |  |  |  |  | Lightning Protection (DSLP) |  |  |  |  |  | For Lightning protection of present scope or work, please provide line item for Lightning Mast in Bid Price Schedule |  |  |  |  | Refer S.No08 of Amendment 01 (Part-2) |  |  |
|  |  | General |  |  |  |  |  |  |  | Existing drawings are not available |  |  |  |  |  | Please provide following drawings for Extension S/s 1) Existing SLD Drawing 2) Existing Plan Layout with Equipments & busbar connection. 3) Exisitng Section Layout 4) Existing Earthmat Layout 5) Existing Structure Plan & Section Layout 6) Existing Cable Trench Layout 7) Existing Outdoor Lighting Layout & Distribution diagram 8) Existing DSLP Layout 9) Existing Panel arrangement layout of Control Room building 10) Existing SAS Architecture diagram 11) Existing LT Board drawings (ACDB, DCDB, MLDB & ELDB) 12) Existing Busbar CRP drawing |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | 400kV Extn. S/s at Pugalur HVDC (GIS) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.6.2 V) h) Pg No. 15 of 30 |  |  |  |  |  |  |  | Fire Protection System |  |  |  |  |  | Request you to furnish Existing Fire fighting drawings for present scope of Extension works. Also provide tap off point for Extension of Main Header. |  |  |  |  | Bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | General |  |  |  |  |  |  |  | LT Switchboards |  |  |  |  |  | Please confirm sufficient feeders in Existing LT Switchboards (MSB, ACDB, DCDB, MLDB, ELDB) for present scope of Extn. Works |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.6.2 V) h) Pg No. 15 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | We understand that existing Fire Fighting System of existing Substations is adequate to cater to requirement of additional Reactor / Hydrant to be installed as per respective scope. Please confirm our understanding |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.6.2 V) h) Pg No. 15 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | HVWS system for reactors, the provision to integrate the reactor fire protections into EXISTING Fire Alarm & Annunciation in EXISTING control room & Firefighting Building shall be available. The present scope is limited to termination of signal cables from DV LCP to EXISTING Fire Alarm & Annunciation Panel. Please Confirm. |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule |  |  |  |  |  |  |  | Lightning Protection (DSLP) |  |  |  |  |  | For Lightning protection of present scope or work, please provide line item for Lightning Mast in Bid Price Schedule |  |  |  |  | Refer S.No 09 of Amendment 01 (Part-2) |  |  |
|  |  | 400-220kV Extn. S/s at Gazuwaka (AIS) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Section Project Bid Price Schedule, General |  |  |  |  |  |  |  | Switchyard Panel Room |  |  |  |  |  | Please confirm sufficient space will be available in Existing Switchyard Panel room for present scope of ICT Control & Protection panels. |  |  |  |  | C&R panels shall be placed at HVAC Control Room. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.7.1 Pg No. 16 of 30 |  |  |  |  |  |  |  | Substation Automation System |  |  |  |  |  | Please confirm whether Existing Substation is having Substation Automation System or not? If yes please share Existing details. |  |  |  |  | Gazuwaka S/s is Non- SAS station. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.7.1 e) Pg No. 17 of 30 |  |  |  |  |  |  |  | Fire Protection System |  |  |  |  |  | Request you to furnish Existing Firefighting drawings for present scope of Extension works. Also provide tap off point for Extension of Main Header. |  |  |  |  | Bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.7.1 d) Pg No. 17 of 30 |  |  |  |  |  |  |  | The CSD for existing tie breaker shall be placed in the CB panel of main breaker being supplied under present scope. |  |  |  |  |  | Please furnish make of Existing Tie Circuit Breaker for present scope of CSD supply for Existing Tie Circuit Breakers. |  |  |  |  | Existing Tie Circuit Breaker is CGL make. |  |  |
|  |  | Bid Price Schedule |  |  |  |  |  |  |  | Modification of Existing Control Panel for the 400kV diameter associated with Transformer is under present scope. |  |  |  |  |  | Please provide drawings of Existing 400kV Control Panel. Also share location of said panel. |  |  |  |  | Bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | GA DRG |  |  |  |  |  |  |  |  |  |  |  |  |  | Tender GA drawing shared by PGCIL is not having scope marking for present scope of works in Existing 220kV Switchyard. Please provide details. |  |  |  |  | In GA Drg No.C/ENGG/SRSS-XXV/SR/GAZUWAKSA-EXTN./ GA/001, the present scope is clearly marked and shown by cloud also. |  |  |
|  |  | Section Project, Cl. No. 2.2.7.1 c) ii) Pg No. 16 of 30 |  |  |  |  |  |  |  | Augmentation of above Bus Bar protection shall be in the scope of AP TRANSCO. However supply and laying of CT cable from 220kV CT of POWERGRID to C&R panel of AP Transco shall be in thescope of contractor under present scope of this contract. For this additional cable trench needs to be constructed under present scope and it has to be joined with the existing cable trench which is already going to AP TRANSCO (For ICT-1&2). |  |  |  |  |  | With reference to said clause of Section Project please clarify below points : 1) Please provide location of Existing AP Transco Busbar panels 2) Please share Existing Cable Trench layout for present scope of Extension of cable trench. |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | Section Project, Cl. No. 2.2.7.1 c) iv) Pg No. 17 of 30 |  |  |  |  |  |  |  | Contractor shall also make available 220V DC redundant supply Bus Reactor Common MB for supply to Ethernet Switch. |  |  |  |  |  | Please provide sufficient DC feeders from Existing 220V DCDB. |  |  |  |  | No spare feeders are available in DCDB-1 and DCDB-2 for DC Supply to C&R panels. Bidder to include the scope. However, space is available for extending the DCDB-1&2 sections. Refer S.No 12 of Amendment 01 (Part-2). |  |  |
|  |  | Section Project, Cl. No. 2.2.7.1 i) Pg No. 17 of 30 |  |  |  |  |  |  |  | Grid spacing of existing Main earth mat is as per earthmat drawing enclosed in tender documents. |  |  |  |  |  | Mentioned drawing is not section project is not shared along with Tender documents. Please provide. |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.7.1 i) Pg No. 17 of 30 |  |  |  |  |  |  |  | 220kV, EHV XLPE cable along with cable termination kit (3 Run for R,Y, B Phase for ICT#3) shall be supplied and laid in cable trench from 220kV side bay equipment of ICT#3 up to 220kV Tower/structure (tentative route marked in GA drg) for work under present scope. Further connection from 220kV Tower/Gantry to 220kV Switchyard (APTRANSCO) is excluded from scope of this work the same shall be done by APTRANSCO from their end. |  |  |  |  |  | As per said clause it is understood that our scope in 220kV is only for cable termination from ICT#3 to 220kV Tower as per marking in Tender GA Drawing. Please confirm. Also confirm our understanding that 220kV AIS Equipments for ICT bay mentioned in Bid price Schedule shall be deleted from our scope & same shall be part of APTRANSCO. If not please provide marking of 220kV AIS scope on GA drawing providing more clarity. |  |  |  |  | 220kV AIS equipments for ICT#3 bay mentioned in BPS are part of bidders scope. Location of the same shall be finalized with successful bidder incase of award. |  |  |
|  |  | Section Project Bid Price Schedule, PR Line Item No 530 |  |  |  |  |  |  |  | Augmentation of existing 220kV bus bar protection scheme.(No. of baysas per specification)-(with Automation) |  |  |  |  |  | As per Section Project Augmentation of Existing 220kV Busbar protection is in APTRANSCO scope. Hence Line item shall be deleted. |  |  |  |  | BPS line item is for the scope given at clause no 2.2.7.1 c) ii) of Section project. Bidder to quote accordingly. |  |  |
|  |  | Section Project Bid Price Schedule, PR Line Item No 1020 |  |  |  |  |  |  |  | Augmentation of existing Simplex Control Panel for 220kV (Bus scheme as per SLD) |  |  |  |  |  | Please clarify mentioned scope of work. Furnish Existing Drawings of control panel & provide location of said panel. |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.7.1 l) Pg No. 18 of 30 |  |  |  |  |  |  |  | Additional cabling and installation work etc required from conventional RTCC panels (of existing Transformers 2 nos. at each) to new digital RTCC panels including supply, erection, testing and commissioning etc is covered under present scope of work. |  |  |  |  |  | Please confirm our understanding: 1) New Digital RTCC panel is only for New supplied 500MVA ICT (ICT#3) as per Bid price Schedule considering Qty mentioned as 1. 2) Please clarify our understanding whether New Digital RTCC panel will be utilised for ICT#1, ICT#2 & ICT#3 ? (ICT#1 & ICT#2 being Existing whose make is not known to us) 3) Please furnish details of Existing ICT#1 & ICT#2 in terms of Make, Detailed Drawings of Transformer including RTCC drawings 4) Please provide location of Conventional RTCC panels of ICT#1 & ICT#2 along with marking on drawing. 5) Please provide List of Signals to be transferred to New Digitial RTCC panel from old conventional RTCC panel. 6) Specify details of Relay used in Conventional RTCC panel. |  |  |  |  | 1) Bidder’s understanding is not correct. The exiting conventional RTCC panels(ICT#1 & ICT#2) shall be disconnected and new digital RTCC panel shall be used for ICT#1, ICT#2 & ICT#3. 2) Please refer reply at S.No 59 above. For replies to bidders clarification mentioned by S.No 60), 61) & 62)- Bidder is advised to visit site and get familiar with scope and equipment available. 5) List of signals to be transferred to digital RTCC shall be finalized with successful bidder in case of award. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.7.1 l) Pg No. 18 of 30 |  |  |  |  |  |  |  | Digital RTCC Panel |  |  |  |  |  | Please clarify the location for New Digital RTCC panel whether Control Room or Switchyard Panel room. |  |  |  |  | New digital RTCC panel shall be placed in HVAC control room. |  |  |
|  |  | General |  |  |  |  |  |  |  | LT Switchboards |  |  |  |  |  | Please confirm sufficient feeders in Existing LT Switchboards (MSB, ACDB, DCDB, MLDB, ELDB) for present scope of Extn. Works |  |  |  |  | Please refer S.No. 12 of Amendment 01 (Part-2). No spare feeders are available in MSB. Bidder to include the same and its price should be included in DCDB extn item. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.7.1 e) Pg No. 17 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | We understand that existing Fire Fighting System of existing Substations is adequate to cater to requirement of additional Reactor / Hydrant to be installed as per respective scope. Please confirm our understanding |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule, Cl. No. 2.2.7.1 e) Pg No. 17 of 30 |  |  |  |  |  |  |  | Fire Fighting System |  |  |  |  |  | HVWS system for reactors, the provision to integrate the reactor fire protections into EXISTING Fire Alarm & Annunciation in EXISTING control room & Firefighting Building shall be available. The present scope is limited to termination of signal cables from DV LCP to EXISTING Fire Alarm & Annunciation Panel. Please Confirm. |  |  |  |  | Confirmed. |  |  |
|  |  | Section Project Bid Price Schedule |  |  |  |  |  |  |  | Lightning Protection (DSLP) |  |  |  |  |  | For Lightning protection of present scope or work, please provide line item for Lightning Mast in Bid Price Schedule |  |  |  |  | There is one LM present near the area of ICT-3. The same may be used for DSLP. |  |  |
|  |  | General |  |  |  |  |  |  |  | Existing drawings are not available |  |  |  |  |  | Please provide following drawings for Extension S/s 1) Existing SLD Drawing 2) Existing Plan Layout with Equipments & busbar connection. 3) Exisitng Section Layout 4) Existing Earthmat Layout 5) Existing Structure Plan & Section Layout 6) Existing Cable Trench Layout 7) Existing Outdoor Lighting Layout & Distribution diagram 8) Existing DSLP Layout 9) Existing Panel arrangement layout of Control Room building 10) Existing SAS Architecture diagram 11) Existing LT Board drawings (ACDB, DCDB, MLDB & ELDB) 12) Existing Busbar CRP drawing |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | Extension of 400/220kV Gazuwaka substation, NTAMC gateway / SCADA |  |  |  |  |  |  |  |  |  |  |  |  |  | Please confirm that configuration and Integrating works is limited only to bidder supplies and Alstom make gateway configuration and integration is not in bidder's scope. |  |  |  |  | The configuration and Integrating works with existing gateway at Gazuwaka s/s for present bay is covered under bidder’s scope. |  |  |
|  |  | Section project, Cl. No. 2.2.7.1 (l) |  |  |  |  |  |  |  |  |  |  |  |  |  | Please inform whether in conventional RTCC, any AVR relay are there. If yes, please provide make and model of AVR. |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | Section project, Cl. No. 2.2.7.1 (l) |  |  |  |  |  |  |  |  |  |  |  |  |  | Kindly provide the OLTC & RTCC Schematic diagram of existing transformer. |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | Section project, Cl. No. 2.2.7.1 (l) |  |  |  |  |  |  |  |  |  |  |  |  |  | Please confirm whether Digital RTCC Relay will be kept in existing transformer RTCC Panel or New RTCC panel required. |  |  |  |  | All digital RTCC Relays under present scope shall be kept in new panel under present scope. . |  |  |
|  |  |  |  | 400kV Kozhikode Extn |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Section Project Bid Price Schedule |  |  |  |  |  | General |  |  |  | Switchyard Panel Room |  |  |  | Please confirm sufficient space will be available in Existing Switchyard Panel room for present scope of Thrissur Line#1 Control & Protection panels. |  |  | Confirmed |  |  |
|  |  |  |  | General |  |  |  |  |  |  |  |  |  |  |  |  |  | Please specify creepage distance to be considered |  |  | Creepage distance shall be 25mm/kV |  |  |
|  |  |  |  | Section Project Bid Price Schedule Cl. No. 2.2.8.1 c) Pg No. 19 of 30 |  |  |  |  |  |  |  |  |  | Substation Automation System |  |  |  | Please provide details of existing Substation Automation System. |  |  | Existing SAS architecture is enclosed |  |  |
|  |  |  |  | Section Project Bid Price Schedule |  |  |  |  |  |  |  |  |  | PMU system |  |  |  | Please provide details of existing PMU System for present scope of Extension works. |  |  | Bidder has to supply the PMU as per given scope & inline with TS. |  |  |
|  |  |  |  | Section Project Bid Price Schedule |  |  |  |  |  | PR Line Item No 1170 |  |  |  | Erection Hardware for 400kV I type layout-Line bay as per technical specification |  |  |  | Please correct Qty as 2 No.s |  |  | Please refer Sl no. 10 of Amendment 01 (Part-2) |  |  |
|  |  |  |  | GA drawing |  |  |  |  |  |  |  |  |  | 400kV Main Bus |  |  |  | We assume that Main Bus is Existing for present scope of Extension works. Please provide Conductor details of 400kV Main Bus & Jack Bus |  |  | Main Bus & Jack bus are of Quad ACSR moose conductor |  |  |
|  |  |  |  | Section Project Bid Price Schedule |  |  |  |  |  | Cl. No. 2.2.8.1 l) Pg No. 20 of 30 |  |  |  | Fire Protection System |  |  |  | Request you to furnish Existing Fire fighting drawings for present scope of Extension works. |  |  | Details shall be provided during detailed Engineering. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  |  |  | Section Project Bid Price Schedule |  |  |  |  |  | Cl. No. 2.2.8.1 k) Pg No. 20 of 30 |  |  |  | The main Earthmat already exists in switchyard area under present scope of work. All the equipments, structures, cable trenches, auxiliary earth mat for isolators etc. shall be earthed by connecting them to the main earthmat by the contractor. Main Earthmat drawing is enclosed with the Tender drawings. Grid spacing of existing Main earth mat is 10X10Mtr (approx.). |  |  |  | Please share mentioned drawing since it is not provided along with Tender drawings |  |  | Existing Earthmat Drg enclosed |  |  |
|  |  |  |  | General |  |  |  |  |  |  |  |  |  | LT Switchboards |  |  |  | Please confirm sufficient feeders in Existing LT Switchboards (MSB, ACDB, DCDB, MLDB, ELDB) for present scope of Extn. Works |  |  | Confirmed. |  |  |
|  |  |  |  | Section Project Bid Price Schedule |  |  |  |  |  | Cl. No. 2.2.8.1 l) Pg No. 20 of 30 Fire Fighting System |  |  |  |  |  |  |  | We understand that existing Fire Fighting System of existing Substations is adequate to cater the requirement of additional 400kV Switchyard Panel Room to be installed as per respective scope. Existing Fire Alarm panel & Annunciation panel shall be sufficient to integrate present scope of Extn works. Please confirm our understanding |  |  | Details shall be provided during detailed Engineering. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  |  |  | Section Project Bid Price Schedule |  |  |  |  |  |  |  |  |  | Lightning Protection (DSLP) |  |  |  | For Lightning protection of present scope or work, please provide line item for Lightning Mast in Bid Price Schedule |  |  | Bidder to quote as per BPS |  |  |
|  |  |  |  | General |  |  |  |  |  |  |  |  |  | Existing drawings are not available |  |  |  | Please provide following drawings for Extension S/s 1) Existing SLD Drawing 2) Existing Plan Layout with Equipments & busbar connection. 3) Exisitng Section Layout 4) Existing Earthmat Layout 5) Existing Structure Plan & Section Layout 6) Existing Cable Trench Layout 7) Existing Outdoor Lighting Layout & Distribution diagram 8) Existing DSLP Layout 9) Existing Panel arrangement layout of Control Room building 10) Existing SAS Architecture diagram 11) Existing LT Board drawings (ACDB, DCDB, MLDB & ELDB) 12) Existing Busbar CRP drawing |  |  | Existing Electrical layout- Plan & Section, Earthmat layout , Cable trench layout & SAS Architecture enclosed. Rest of the drawings shall be provided during detailed Engineering |  |  |
|  |  |  |  | FOTE - Kozikhode extn. |  |  |  |  |  |  |  |  |  |  |  |  |  | Kindly specify location of FOTE Panel. Also provide distance between Switchyard panel room & Control Room Building. |  |  | Equipmrnt/FOTE panel shall be installed in control room of Kozhikode. |  |  |
|  |  |  |  | 220kV Cochin Extn |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | General |  |  |  |  |  | Please specify creepage distance to be considered |  |  |  |  |  |  |  |  |  |  | Creepage distance shall be 25mm/kV |  |  |
|  |  |  |  | Section Project Bid Price Schedule Cl. No. 2.2.9.1 c) Pg No. 22 of 30 |  |  |  |  |  | Substation Automation System |  |  |  |  |  |  |  | Please provide details of existing Substation Automation System. |  |  | Existing SAS is of M/s GE make, system architecture enclosed |  |  |
|  |  |  |  | Section Project Bid Price Schedule Conductor details |  |  |  |  |  | Request you to furnish Type of Conductor for Outgoing Lines at each voltage level on SLD. |  |  |  |  |  |  |  |  |  |  | Details shall be provided during detailed Engineering |  |  |
|  |  |  |  | Section Project Bid Price Schedule Cl. No. 2.2.9.1 k) Pg No. 23 of 30 |  |  |  |  |  | Fire Alarm System |  |  |  |  |  |  |  | Request you to furnish Existing Fire fighting drawings for present scope of Extension works. |  |  | Details shall be provided during detailed Engineering |  |  |
|  |  |  |  | Section Project Bid Price Schedule |  |  | Cl. No. 2.2.8.1 j) Pg No. 23 of 30 |  |  | The main Earthmat already exists in 220kV switchyard area under present scope of work. All the equipments, structures, cable trenches, auxiliary earth mat for isolators etc. shall be earthed by connecting them to the main earth mat by the contractor. Main Earthmat drawing is enclosed with the Tender drawings. The earthmat spacing is 8 M in X-direction and 4.5 M to 10 M in Ydirection. |  |  |  |  |  |  |  | Please share mentioned drawing since it is not provided along with Tender drawings |  |  | Existing eartmat layout enclosed |  |  |
|  |  |  |  | General |  |  |  |  |  | LT Switchboards |  |  |  |  |  |  |  | Please confirm sufficient feeders in Existing LT Switchboards (MSB, ACDB, DCDB, MLDB, ELDB) for present scope of Extn. Works |  |  | Confirmed |  |  |
|  |  |  |  | Section Project Bid Price Schedule |  |  | Cl. No. 2.2.8.1 j) Pg No. 23 of 30 |  |  | Fire Fighting System |  |  |  |  |  |  |  | We understand that existing Fire Fighting System of existing Substations is adequate to cater the requirement of additional 400kV Switchyard Panel Room to be installed as per respective scope. Existing Fire Alarm panel & Annunciation panel shall be sufficient to integrate present scope of Extn works. Please confirm our understanding |  |  | Details shall be provided during detailed Engineering |  |  |
|  |  |  |  | Section Project Bid Price Schedule |  |  |  |  |  | Lightning Protection (DSLP) |  |  |  |  |  |  |  | For Lightning protection of present scope or work, please provide line item for Lightning Mast in Bid Price Schedule |  |  | LMs are already existing in the 220kV Switchyard. Bidder to submit DSLP layout based on the existing layout during detailed Engineering |  |  |
|  |  |  |  | General |  |  |  |  |  | Existing drawings are not available |  |  |  |  |  |  |  | Please provide following drawings for Extension S/s 1) Existing SLD Drawing 2) Existing Plan Layout with Equipments & busbar connection. 3) Exisitng Section Layout 4) Existing Earthmat Layout 5) Existing Structure Plan & Section Layout 6) Existing Cable Trench Layout 7) Existing Outdoor Lighting Layout & Distribution diagram 8) Existing DSLP Layout 9) Existing Panel arrangement layout of Control Room building 10) Existing SAS Architecture diagram 11) Existing LT Board drawings (ACDB, DCDB, MLDB & ELDB) 12) Existing Busbar CRP drawing |  |  | Existing Electrical layout Plan & Section is already provided. Eartmayt layout , cable trench layout & SAS Architecture is enclosed. Rest of the drawings shall be provided during detailed Engineering |  |  |
|  |  |  |  | 220kV Cochin (Kochi) substation |  |  | NTAMC gateway / SCADA |  |  |  |  |  |  |  |  |  |  | Please confirm that configuration and Integrating works is limited only to bidder supplies and Alstom make gateway configuration and integration is not in bidder's scope. |  |  | Confirmed |  |  |
|  |  |  |  | FOTE - Kochi extn. |  |  |  |  |  |  |  |  |  |  |  |  |  | Kindly specify location of FOTE Panel. Also provide distance between Switchyard panel room & Control Room Building. |  |  | Equipment/FOTE panel shall beinstalled in kochi Control Room. |  |  |
|  |  |  |  |  | General |  |  |  |  |  |  |  |  |  |  |  |  | Please provide the soil investigation report for all existing substations. |  |  | Soil investigation report shall be provided to the successful bidder. However, the bidder is advised to visit the site to acquaint themselves about the strata of soil. |  |  |
|  |  |  |  |  | Clause 5 of Civil works rev 11 A and 8.Hosur_Soil_Investigation2, Excavation and backfill of foundation |  |  |  |  |  |  |  |  |  |  |  |  | As per Clause 5 of civil works spec , rev-11A, the excavation and bakfilling of foundation in the mode of measurement is classified as a. Excavation in all kind of soil including soft/ disintegrated rock, PCC, WBM, Brickwork/ stone masonry etc (excluding hard rock) b. Excavation in hard rock work(required blasting) On the basis of above,we understand that if hard rock is encounterd during site execution. Same shall be commericaly dealt separately. Please confirm. |  |  | BPS shall prevail in this regards. |  |  |
|  |  |  |  |  | General |  |  |  |  |  |  |  |  |  |  |  |  | We understand that any modification/Refurbishment work towards any existing structure and foundations is not in the bidder's scope. Please confirm |  |  | Modification/Refurbishment work towards any existing structure and foundations is not envisaged |  |  |
|  |  |  |  |  | SLD_ GA Housur SS,SLD_ GA Hiriyur SS,SLD_GA Pugalur AIS SS,SLD_Gazuwaka SS,SLD & GA Cochin,SLD_Kozikode SS, Internal road |  |  |  |  |  |  |  |  |  |  |  |  | As per the Shedule 3 Civil BOQ , We understand that construction of Internal Swithyard Road is not in the scope of the bidder. Please confirm. |  |  | Confirmed. |  |  |
|  |  |  |  |  | BPS_Sch-1, Sl. No. 376 to 378 |  |  |  |  |  |  |  |  |  |  |  |  | Please note that due to limitation of technology PLCC & DTPC equipment at both end should be of same make and model. As per BPS, only Kochin end equipments are included, Request you to add remote end equipment in scope. |  |  | PLCC & DPC equipments for the remote end is covered in schedule 3 and inadvertently missed in Schedule 1 & 2. Please refer S.No 11 of Amendment 01 (Part-2). |  |  |
|  |  |  |  |  | Section Telecommunication System, Annexure-II |  |  |  |  | Section: Repeater Shelter |  |  |  |  |  |  |  | We understand that repeatershelter is not envisaged in current scope of work as same in not mentioned in BPS & Section project. Hence we understand that specification for Repeater Shelter is for academic purpose only. Please confirm . |  |  | Repeater Shelter is not in the current scope of Work. Bidder has to Bid as per BPS. |  |  |
|  |  |  |  |  | Hosur,Hiriyur,Gazuwaka, |  |  |  |  |  |  |  |  |  |  |  |  | Plesae provide the make /details of DGA, RTCC, OLTC and the NTAMC Architecture Drawing for the station. |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  |  |  |  | Madhugiri,Dharmapuri,Pugalur (AIS),Pugalur(GIS) |  |  |  |  |  |  |  |  |  |  |  |  | Please provide the make /details of DGA, RTCC and OLTC . |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  |  |  |  | Section Project, Gazuwaka, Hosur, Madhugiri, Dharmapuri, Hiriyur, Pugalur(AIS), clause 2.1 |  |  |  |  | 1x500MVA, 400/220kV ICT along-with associated ICT bays.. |  |  |  |  |  |  |  | Please note that lightning protection requirement is not specified in section project so we have considered DSLP (400KV) using shield wire for extension scope as per PGCIL practice.Please confirm. Please clarify that steel structure required for DSLP protection will be operated through lattice structure quantity specified in price schedule . |  |  | There is one LM present near the area of ICT-3. The same may be used for DSLP. |  |  |
|  |  |  |  |  | Section Project, Gazuwaka, Hosur, Madhugiri, Dharmapuri, Hiriyur, Pugalur(AIS), clause 2.1 |  |  |  |  | 1x500MVA, 400/220kV ICT along-with associated ICT bays.. |  |  |  |  |  |  |  | We understand that no dismantling/re-erection of existing bay equipment is envisaged for proposed ICT bay extension. Please confirm. |  |  | Confirmed. |  |  |
|  |  |  |  |  | Section Project, Gazuwaka, Hosur, Madhugiri, Dharmapuri, Hiriyur, Pugalur(AIS), clause 2.1 |  |  |  |  | 1x500MVA, 400/220kV ICT along-with associated ICT bays.. |  |  |  |  |  |  |  | We understand that existing MLDB and ELDB system have adequate rated wired feeders to cater the lighting requirement. for new ICT/Reactor bays .Hence no new extension MLDB and ELDB is envisaged for present scope of work. Please confirm. |  |  | Please refer S.No. 12 of Amendment 01 (Part-2)for DCDB Extn. No spare feeders are available in MSB. Bidder to include the same and its price should be included in DCDB Extn item. |  |  |
|  |  |  |  |  | Section Project, Gazuwaka, Hosur, Madhugiri, Dharmapuri, Hiriyur, Pugalur(AIS), clause 2.1 |  |  |  |  | 1x500MVA, 400/220kV ICT along-with associated ICT bays.. |  |  |  |  |  |  |  | We understand that existing ACDB, DCDB, Battery & battery Charger are sufficient to cater the load requirement for present scope of work. Please confirm. |  |  | Refer reply at S. No. 116 above. |  |  |
|  |  |  |  |  | Section Project, Gazuwaka, Hosur, Madhugiri, Dharmapuri, Hiriyur, Pugalur(AIS), clause 2.1 |  |  |  |  | 1x500MVA, 400/220kV ICT along-with associated ICT bays.. |  |  |  |  |  |  |  | Please furnish the conductor details of existing Reactor/ICT bay. |  |  | Bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  |  |  |  | Section Project, Gazuwaka, Hosur, Madhugiri, Dharmapuri, Hiriyur, Pugalur(AIS), clause 2.1 |  |  |  |  | 1x500MVA, 400/220kV ICT along-with associated ICT bays.. |  |  |  |  |  |  |  | Please furnish the existing main bus and equipment connection conductor details for 400kV/220KV system. |  |  | Bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  |  |  |  | Section Project, Gazuwaka, Hosur, Madhugiri, Dharmapuri, Hiriyur, Pugalur(AIS), clause 2.1 |  |  |  |  | 1x500MVA, 400/220kV ICT along-with associated ICT bays.. |  |  |  |  |  |  |  | We understand that illumination of ICT /Reactor bays will be achieved by mounting LED fiitings on bay gantries/towers. No sepeare lighting mast and street light poles are envisaged for new bays. Please confirm . |  |  | Please refer Section Lighting System Rev 07 for mounting of Lighting Fixtures. |  |  |
|  |  |  |  |  | Section Project, Gazuwaka, Hosur, Madhugiri, Dharmapuri, Hiriyur, Pugalur(AIS), clause 2.1 |  |  |  |  | 1x500MVA, 400/220kV ICT along-with associated ICT bays.. |  |  |  |  |  |  |  | We understand that existing 415V auxiliary board along with LT Transformer are sufficient to cater the load requirement under present scope of work. Please confirm. |  |  | Confirmed. |  |  |
|  |  |  |  |  | Section Project, Gazuwaka, Hosur, Madhugiri, Dharmapuri, Hiriyur, Pugalur(AIS), clause 2.1 |  |  |  |  | 1x500MVA, 400/220kV ICT along-with associated ICT bays.. |  |  |  |  |  |  |  | We understand the existing main cable trench between 400 kV/220KV switchyard and control room building has adequate space to accommodate the new bay cabling requirement. Please confirm. |  |  | Confirmed. However length of angels of the existing cable trench has to be increased as the existing cable trench already occupied the exuiting angels. |  |  |
|  |  |  |  |  | Gazuwaka, Hosur, Madhugiri, Dharmapuri, Hiriyur, Pugalur(AIS), clause 2.1 |  |  |  |  | 1x500MVA, 400/220kV ICT along-with associated ICT bays.. |  |  |  |  |  |  |  | Please provide Exsiting HVW Spary system layout drawings |  |  | Bidder is advised to visit site as per clause no. 2.4 of section project. |  |
| Augmentation of the Transformation Capacity 1x500MVA, 400/220kV ICT at Gazuwaka |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - 19 |  |  |  |  | Section Project, clause 2.1 |  |  |  |  | i) 1x500MVA, 400/220kV ICT at Gazuwaka along-with associated ICT bays.. |  |  |  |  |  |  |  | Please provide the Following drawing of Existing Substation:- 1. 220kV SLD & plan- section Drawing. 2. Earth mat Drawing 3.Exsiting HVW Spary system layout drawings |  |  | Bidder is advised to visit site as per clause no. 2.4 of section project. |  |
|  |  |  |  |  | BPS, Sch-1 SI.No:-80 |  |  |  |  | 220kV HV power Cable |  |  |  |  |  |  |  | Please furnish the 220kV cable Size for Gazuwaka S/S. |  |  | 220kV Cable Size shall be 1 RUN of 1Cx2500 Sq. mm, XLPE Cu Cable per Phase. |  |
|  |  |  |  |  | Section Project, clayse 2.1 |  |  |  |  | Switchyard panel room |  |  |  |  |  |  |  | We understand that present scope of C&R Panel shall be place in Exsiting SPR room .Please confirm |  |  | C&R Panel shall be place in Existing HVAC control room. |  |
| Extension of 400kV Hosur Substation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - 22 | Section Project |  |  |  |  |  |  | ii) Bus Bar Protection scheme: The existing 400kV bus bar protection scheme at Hosur substation is ABB make RADSS. The integration of present bays to the bus bar protection scheme including any wiring is in the scope of the contractor. |  |  |  |  |  |  |  |  |  | We understand that CT input module are available in existing RADSS relay. Bidder scope is limited to wring modifications. Please confirm. |  |  | CT input module is available and wired in Tie bay of the same diameter. The same can be used. However, all wiring/modifications etc are envisaged under present scope of work. |  |
| - 23 | Section Project, 2.2.1.4 Civil work |  |  |  |  |  |  | Switchyard panel room |  |  |  |  |  |  |  |  |  | We presume that present scope of C&R Panel shall be place in newly Constructed SPR room .Please confirm |  |  | Refer S.No 01 of Amendment 01 (Part-2). |  |
| Extension of 400kV Madhugiri Substation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - 24 | Section Project, clause 2.2.2.2 |  |  |  |  |  |  |  |  | Bus Bar Protection scheme: The existing 400kV bus bar protection scheme at Madhugiri S/S is Siemens make -7SS52 (Distributed type, duplicate bus-bar protection scheme for each bus). Associated Bus bar Bay units 7SS525 is already available at SS for present scope. Recommissioning/ Integration with CU/wiring of the same with new CT of present scope is required to be considered. |  |  |  |  |  |  |  |  | We understand that CT input module are available in existing RADSS relay. Bidder scope is limited to wring modifications. Please confirm |  | Existing Bus Bar Protection scheme at Madhugiri S/S is Siemens make -7SS52 not RADSS. |  |
| - 25 | Section Project, clasue 2.2.2.4 Civil work |  |  |  |  |  |  |  |  | Switchyard panel room |  |  |  |  |  |  |  |  | We presume that present scope of C&R Panel shall be place in newly Constructed SPR room .Please confirm |  | C&R Panel shall be place in newly Constructed Existing SPR room. |  |
| Extension of 400kV Dharmapuri Substation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - 26 | Section Project |  |  |  |  |  |  |  |  |  | Bus Bar Protection scheme: The existing 400kV bus bar protection scheme at Dharmapuri S/S is Siemens make -7SS52 (Distributed type, duplicate bus-bar protection scheme for each bus). Associated Bus bar Bay units 7SS525 is already available at SS for present scope. Recommissioning/ Integration with CU/wiring of the same with new CT of present scope is required to be considered. |  |  |  |  |  |  | We understand CT input module are available in existing RADSS relay. Bidder scope is limited to wring modifications. Please confirm |  |  | Existing Bus Bar Protection scheme at Dharmapuri S/S is Siemens make -7SS52 not RADSS. |  |
| - 27 | Section Project |  |  |  |  |  |  |  |  |  | Switchyard panel room |  |  |  |  |  |  | We presume that present scope of C&R Panel shall be place in Existing SPR room .Please confirm |  |  | Confirmed. |  |
| Extension of 400kV Hiriyur substation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - 28 | Section Project |  |  |  |  |  |  |  |  |  | Bus Bar Protection scheme: The existing 400kV bus bar protection scheme at Hiriyur substation is ABB MAKE RADAH model. The integration of present bays to the bus bar protection scheme including any wiring modification is in the scope of the contractor. |  |  |  |  |  |  | We understand CT input module are available in existing RADSS relay. Bidder scope is limited to wring modifications. Please confirm |  |  | Existing Bus Bar Protection scheme at Hiriyur S/S is ABB MAKE RADHA not RADSS. CT input module is available and wired in Tie bay of the same diameter. The same can be used. However, all wiring/modifications etc are envisaged under present scope of work |  |
| - 29 | Section Project |  |  |  |  |  |  |  |  |  | Switchyard panel room |  |  |  |  |  |  | We presume that present scope of C&R Panel shall be place in Existing SPR room Please confirm |  |  | Existing Control Panel is placed at control room and Relay Panel shall be place in Existing SPR room. |  |
| Extension of 400kV Pugalur(AIS) substation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - 30 | Section Project, clause 2.2.5.2 |  |  |  |  |  |  |  | ii) Bus Bar Protection scheme: The existing 400kV bus bar protection scheme at Pugalur S/S is GE make -P741/P743 (Distributed type, duplicate bus-bar protection scheme for each bus. The Peripheral units (PU’s) for the present scope are available at site. The integration of above Peripheral units (PU’s) to the bus bar protection scheme including any wiring is in the scope of the contractor. |  |  |  |  |  |  |  |  | We understand CT input module are available in existing RADSS relay. Bidder scope is limited to wring modifications. Please confirm |  |  | 400kV Busbar Protection scheme at Pugalur S/S is GE make -P741/P743 not RADSS. Bus bar Augumentation scope is given in clause 2.2.5.2. Bidder to quote accordingly. |  |
| - 31 | Section Project, clasuse 2.2.5.4 Civil work |  |  |  |  |  |  |  | Switchyard panel room |  |  |  |  |  |  |  |  | We presume that present scope of C&R Panel shall be place in Existing SPR room .Please confirm |  |  | Confirmed. |  |
| Extension of 400kV Pugalur HVDC (GIS) sub-station: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - 32 | Section Project, clause 2.2.6 |  |  |  |  |  |  |  | Extension of 400kV Pugalur HVDC (GIS) sub-station |  |  |  |  |  |  |  |  | We presume that present scope of C&R Panel shall be place in Existing relay & Control room .Please confirm |  |  | Confirmed. |  |
| - 33 | Cl 2.2.6.4, II civil works, points no a, b & d, Section project_Rev 02 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Since GIS hall shall be existing,we understand that there is no civil work inside GIS hall except grouting of foundtion bolt for GIS equipment. Please confirm . |  |  | Scope related to civil work is already given in Section project. |  |
| Extension of 220kV Cochin (Kochi) substation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - 34 | Section Project clause 2.2.9.3 Civil work |  |  |  |  |  |  |  | Switchyard panel room |  |  |  |  |  |  |  |  |  | We presume that present scope of C&R Panel shall be place in newly constructed SPR room .Please confirm |  | Confirmed |  |
| - 35 | Section Project, clause 2.2.9 |  |  |  |  |  |  |  | Extension of 220kV Cochin (Kochi) substation |  |  |  |  |  |  |  |  |  | Lightning protection system for extension substation is not specified in section project , we have considered DSLP using shield wire for 220kV Line bay as per PGCIL practice. Please confirm. |  | LMs are already existing in the 220kV Switchyard. Bidder to submit DSLP layout based on the existing layout during detailed Engineering |  |
| - 36 | Section Project, clause 2.2.9 |  |  |  |  |  |  |  | 2 no. of 220kV bays |  |  |  |  |  |  |  |  |  | We understand that existing control room has adeqaute space to accommodate new bay equipment. Please confirm. |  | Confirmed |  |
| - 37 | General |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Please providemake /model of existing version of PACIS operating in the S/S. |  | Existing SAS is of M/s GE make, system architecture enclosed |  |
| Extension of 400/220kV Kozhikode Substation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - 38 | Section Project, clause 2.2.8 |  |  |  |  |  |  |  |  |  | Extension of 400/220kV Kozhikode Substation |  |  |  |  | Please provide the Following drawing of Existing Substation:- 1.400kV SLD & plan- section Drawing. 2. Earth mat Drawing 3.Exsiting HVW Spary system layout drawings |  |  |  |  | Existing Plan, Section & Earthmat drgs enclosed. Existing HVWS system drg shall be provided during detailed Engineering |  |
| - 39 | Section Project, clause 2.2.8.1.2 civil works |  |  |  |  |  |  |  |  |  | Switchyard panel room |  |  |  |  | We presume that present scope of C&R Panel shall be place in newly constructed SPR room .Please confirm |  |  |  |  | For North Thrissur line 1 bay, the C& R Panels etc. shall be kept in the existing SPR & for Line 2, C&R ,etc. shall be kept in newly constructed SPR under present scope. |  |
| - 40 | Section Project, clause 2.2.8 |  |  |  |  |  |  |  |  |  | Extension of 400/220kV Kozhikode Substation |  |  |  |  | Lightning protection system for extension substation is not specified in section project , we have considered DSLP using shield wire for 400kV Line bay as per PGCIL practice. Please confirm. |  |  |  |  | Confirmed |  |
| - 41 | Section Project clause 2.2.8 |  |  |  |  |  |  |  |  |  | Extension of 400/220kV Kozhikode Substation |  |  |  |  | We understand existing control room has adeqaute space to accommodate new bay equipment |  |  |  |  | Confirmed |  |
| - 42 | Section Project |  |  |  |  |  |  |  |  |  | Extension of 400/220kV Kozhikode Substation |  |  |  |  | Please provide the make and model (version) of the SAS operating in the station. |  |  |  |  | Existing SAS is of M/s GE make, system architecture enclosed |  |
| - 1 |  |  |  | Section -Project,Extension of 400kV Pugalur HVDC (GIS) sub-station:, 2.2.6 pg 12 of 30 |  |  |  |  |  | Bidder shall design the interface arrangement to suit existing bus configuration so as to maintain the interconnection space between upcoming GIS and existing GIS (M/s. ABB make) as minimum as possible. |  |  |  |  |  | Please provide the Interface details (section drawings) for existing GIS make bus bar for extending the same with our GIS. |  |  |  | Interface drawing of existing GIS is already enclosed along-with tender documents. |  |  |
| - 2 |  |  |  | Section -Project,Extension of 400kV Pugalur HVDC (GIS) sub-station:, Annex-IV |  |  |  |  |  | In Pugalur, HVDC GIS S/s Extn, for GIS Mandatory Spares Standard list at Annexure-10 (TS GIS, Rev 05) is to be considered. |  |  |  |  |  | As present scope includes only extension of 400kV GIS bays. we presume, 400kV spares (with quantity) as indicated in Extension S/S column to be considered for Pugalur as applicable. Please confirm. |  |  |  | Confirmed |  |  |
| - 3 |  |  |  | GIS specification – Rev 5,Extension of 400kV Pugalur HVDC (GIS) sub-station:27.5 pg 51 of 80 |  |  |  |  |  | On-line Partial discharge monitoring system (applicable for 765kV and 400kV GIS) The PDM system shall be provided with all its hardware and software, with readily interfacing to the UHF PD couplers installed in the GIS of present bays and future bays as shown in SLD plus 20% additional as extra…. |  |  |  |  |  | Since this is an extension package , request you to confirm whether there is provision in existing PD monitoring system to accommodate the UHF sensors for present bays and future bays GIS as per given SLD. Please confirm. |  |  |  | Provision for connection of UHF sensors for bays under present scope has been kept in the existing PD monitoring system based on existing GIS supplier design. |  |  |
| - 4 |  |  |  | Annex-X – Mandatory Spares – 400kV (for Pugalur),Extension of 400kV Pugalur HVDC (GIS) sub-station:clause 1.9 |  |  |  |  |  | Pipe length (Copper or Steel as applicable) for SF6 Circuit of each type - 1Set |  |  |  |  |  | Please note that our design has no piping arrangement so it is not applicable to our design. Please confirm. |  |  |  | The requirement/applicability shall be reviewed during detailed engineering based on manufacturer’s design meeting the TS. If applicable/required, same shall deemed to be included. |  |  |
| - 5 |  |  |  | Annex-X – Mandatory Spares – 400kV (for Pugalur), clause 1.1 |  |  |  |  |  | Locking device to keep the Disconnectors (isolators) and earthing switches in close or open position in case of removal of the driving mechanism |  |  |  |  |  | Please note that when the operating mechanism of the disconnector or earthing switch is removed, the contacts cannot be disturbed from outside in our design. Hence locking device is not required. Please confirm. |  |  |  | Bidder to Quote as per The requirement of TS |  |  |
| - 6 |  |  |  | Annex-X – Mandatory Spares – 400kV (for Pugalur), clause 2.1 |  |  |  |  |  | Complete Circuit Breaker (one phase) with PIR complete with interrupter, main circuit, enclosure and Marshalling Box with operating mechanism to enable replacement of all applicable type / rating of CB by spare (if applicable) |  |  |  |  |  | Please note that " Complete CB " is not applicable for the present scope .We understand that same is not required to be offered for present scope. Please confirm. |  |  |  | Bidder to Quote as per The requirement of TS |  |  |
| - 7 |  |  |  | Annex-X – Mandatory Spares – 400kV (for Pugalur), clause 3.7 |  |  |  |  |  | Open / Close contactor assembly, timers, key interlock for one complete (3 phase) dis-connector and (3 phase) earthing switch of each type and rating - 1Set |  |  |  |  |  | Please note that proposed interlocks are all electrical with pad locking arrangement. So key interlocking is not applicable. Please confirm. |  |  |  | Bidder to Quote as per The requirement of TS |  |  |
| - 8 |  |  |  | Annex-X – Mandatory Spares – 400kV (for Pugalur), clause 5 |  |  |  |  |  | 5.0 – 400kV/220kV Voltage Transformer |  |  |  |  |  | Please note that there are no Bus VTs in Pugalur’s present scope. We understand that same is not required to be offered for present scope. Please confirm. |  |  |  | Noted. |  |  |
| - 9 |  |  |  | General, GA |  |  |  |  |  | Layout drawing |  |  |  |  |  | Please provide legible PDF drawing or CAD as-built drawing with SF6 to Air bushing termination points as provided drawings are not readable. |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
| - 10 |  |  |  | Project section, /BPS 400kV Hosur S/s Ext. 400kV Madhugiri S/s Ext. 400kV Dhrampari S/s Ext. 400kV Hiriyur S/s Ext. 400kV Puglur S/s Ext, clause 2.2.1/2.2.2/2.2.3/2.2.4/2.2.5 |  |  |  |  |  | Erection Hardware for spare bay of half dia Drawing No a.C/ENGG/SRSS-XXV/SR/SALEM-EXTN/SLD/001. b.C/ENGG/SRSS-XXV/SR/MADHUGIRI-EXTN/SLD/001 c.C/ENGG/SRSS-XXV/SR/HOSUR-EXTN/SLD/001 d.C/ENGG/SRSS-XXV/SR/HIRIYUR-EXTN/SLD/001 e.C/ENGG/SRSS-XXV/SR/PUGALUR-EXTN/SLD/001 |  |  |  |  |  | Please mark and mention the bay to be consider for spare half dia bay in tender SLD for each S/s .No such detail is mentioned in the Section -Project also. We understand that we need to consider earthing & cable work also for above referred spare half dia bay .Please include the same in price schedule. |  |  |  | Erection hardware, earthing & cable work etc related to bay to be consider for spare half as per SLD is to be included as an LS item in respective item for Main Bay. |  |  |
| - 11 |  |  |  | BPS,400kV Hosur S/s Ext. 400kV Madhugiri S/s Ext. 400kV Dhrampari S/s Ext. 400kV Hiriyur S/s Ext. 400kV Puglur S/s Ext sch-1 |  |  |  |  |  | 1.1kV grade power cables |  |  |  |  |  | we understand that power cabling between Control room to SPR and SPR to BMK is not in bidder scope. Please confirm |  |  |  | Power cable is LS item, bidder to estimate all power cable requirements for the scope mentioned for respective site in the BPS item. |  |  |
| - 12 |  |  |  | Section project, clasuse 2.2.6.2 V. c). |  |  |  |  |  | The existing Pugalur HVDC station is equipped with Substation Automation System of ABB make (MACH2 model) which gets the data of existing GIS from IEC61850 Ethernet FO ring. Bidder shall include BCU required for bays (Bay as defined in technical specification, Sec. - Substation Automation) as listed below including all necessary associated hardware and software. |  |  |  |  |  | We understand that, bidder scope of SAS integration is for AC switchyard SAS at Puglur HVDC station. Integration in HVDC SCADA/SAS is not envisaged. Please confirm our understanding. |  |  |  | The scope also includes connection of all Protection IEDs and BCUs including supply of necessary FO cable, LIU, Ethernet switch etc (to be mounted in respective CRP under present scope) required for successful data exchange with existing SAS Ethernet based Ring on IEC61850 protocol. Further, software integration of above BCUs and protection IEDs with existing Sub-station automation system is not included under present scope of work. |  |  |
| - 13 |  |  |  | Section project, clasue 2.2.6.2 V. c). |  |  |  |  |  | The Circuit breaker, isolator and earth switch status signals and circuit breaker trip signal, master trip relay signal, protection signals from IEDs shall be required for integration for VSC application. These signals shall be extended up to Employer’s Interface cubicle in GIS hall of LCC for VSC application. |  |  |  |  |  | Whether these signals are harwired or soft signal through IEC61850 ethernet ring. Please confirm. |  |  |  | These signals shall be provided as hardwired. |  |  |
| - 14 |  |  |  | Section project BPS_Gazuwaka schedule-1, clause , 2.2.7.1 c) ii. sl no 52 |  |  |  |  |  | AP TRANSCO Existing 220kV Bus scheme is Central Unit/Peripheral Unit type. Augmentation of above Bus Bar protection shall be in the scope of AP TRANSCO. However supply and laying of CT cable from 220kV CT of POWERGRID to C&R panel of AP Transco shall be in the scope of contractor under present scope of this contract. For this additional cable trench needs to be constructed under present scope and it has to be joined with the existing cable trench which is already going to AP TRANSCO (For ICT-1&2). |  |  |  |  |  | We understand that, 220kV existing bus bar protection augmentation is in the scope of APTRANSCO at Gazuwaka. But BPS is asking for 220kV bus bar protection augmentation in present scope. Please clarify. |  |  |  | As mentioned in the clause , 2.2.7.1 c) ii. The augmentation of 220kV Bus scheme above shall be in the scope of AP TRANSCO. BPS item is given for the other associated work specified in aforesaid clause. Bidder to quote accordingly. |  |  |
| - 15 |  |  |  | Section project, clause 2.2.7.1 |  |  |  |  |  | 220kV bay for ICT#3 at APTRANSCO switchyard at Gazuwaka |  |  |  |  |  | As per price schedule, 220kV bay for ICT-3 at APTRANSCO switchyard at Gazuwaka is in present bidder scope. Kindly provide the SLD & Layout of existing 220kV switchyard of APTRANSCO at Gazuwaka highlighting present bay. |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  |  |  | Section project, clause 2.2.8.1 c) |  |  |  |  |  | Augmentation of existing substation automation system by providing necessary bay IEDs alongwith associated equipments for 3 (three) numbers 400kV bays (bay as identified in Technical Specification, Section-Substation Automation). |  |  |  |  |  | We understand that existing SAS at Kozikode is of GE make. Please confirm . |  |  |  | Confirmed |  |  |
|  |  |  |  | Section project, clause 2.2.8.1 e) & 2.2.9.1 e) |  |  |  |  |  | Integration of supplied subsystem with SCADA system, PLCC equipment, PABX of RLDC/NLDC, RTAMC/NTAMC, VOIP (SIP compliant for voice. |  |  |  |  |  | We understand, bidder scope of integration is limited to substation end only. Integration works at RLDC/NLDC, NTAMC/RTAMC is excluded from bidder scope. Please confirm our understanding. |  |  |  | Confirmed |  |  |
|  |  |  |  | Section project & BPS schedule-3, clause 2.2.8.1 f) & BPS schedule-3 |  |  |  |  |  | The broad Scope of the procurement of PMU shall include planning, designing, engineering, supply, transportation, insurance, delivery at site, unloading handling, storage, installation, termination, testing and demonstration for acceptance, commissioning and documentation for PMU as per BPS at Kozhikode Substation and these PMU shall support IEEE C 37.118 protocols. These PMUs shall be integrated with Phasor data Concentrator (PDC) at RLDC/SLDC for the subject project. |  |  |  |  |  | We understand, bidder scope of PMU integration is limited to substation end switch only. Integration works at PDC of RLDC/SLDC is excluded from bidder scope. Please confirm our understanding. |  |  |  | Confirmed. However all the configuration work of PMU at substation required for integration with PDC at RLDC/SLDC end shall be in the scope of bidder |  |  |
|  |  |  |  | Section project, clause 2.2.9.1 c) |  |  |  |  |  | The necessary interface equipment and updation of database at Pugalur substation for transferring data to SRLDC (RSCC) & NTAMC is also under present scope. |  |  |  |  |  | We understand, data required for NTAMC shall be configured in existing SAS gateways at Kochi. Separate gateway for NTAMC is not envisaged. Please confirm our understanding. |  |  |  | The configuration and Integrating works with existing gateway at Gazuwaka s/s for present bay is covered under bidder’s scope |  |  |
|  |  |  |  | Section project, clause 7.0 |  |  |  |  |  | 17) Section- RTU & LDMS - Rev.03 |  |  |  |  |  | We understand that, Section- RTU & LDMS - Rev.03 is not applicable for present bidder scope of work. Please confirm our understanding. |  |  |  | Confirmed |  |  |
|  |  |  |  | Section project, Annexure-II |  |  |  |  |  | Bays covered under this package are to be provided with control panel and/or BCU based panel as specified in relevant section elsewhere and are to be integrated with the requirement of remote data transfer and control through existing Substation gateway. |  |  |  |  |  | We understand, configuration/database modification works in existing gateway of NTAMC of ALSTOM make is excluded from bidder scope. Bidder scope is limited to phisical integration of new BCU's with existing NTAMC gateway. Please confirm. |  |  |  | The configuration/database modification works at existing gateway at respective s/s for integration of new BCU s covered under bidder’s scope. |  |  |
| A). 1x500MVA, 400/220kV ICT at Gazuwaka s/s |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Tender drawing & details |  |  |  |  |  |  |  |  |  |  |  | As per Tender drawing (SLD & GA) Main & Jack Bus are existing. Please confirm |  |  | Bidder to quote as per the requirement given in Technical Specification. |  |  |  |
|  |  |  |  |  |  | Existing Earthmat layout |  |  |  |  |  |  |  |  |  |  |  | Kindly provide the existing Earthmat spacing of the switchyard. |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |  |
|  |  |  |  |  |  | Stone spreding |  |  |  |  |  |  |  |  |  |  |  | We have not considered stone spreading in persent scope |  |  | Bidder to quote as per the BPS. |  |  |  |
|  |  |  |  |  |  | Existing Equipment rating |  |  |  |  |  |  |  |  |  |  |  | We have assumed that all Equipments rating shall be same to that of existing. |  |  | Bidder to quote as per the requirement given in Technical Specification. |  |  |  |
|  |  |  |  |  |  | Order of Prevail |  |  |  |  |  |  |  |  |  |  |  | In Case of any discrepancy between Price schedule, Section project & Tender drawing with Tech. Specification. Kindly confirm the Order of prevail for the qty. estimation. |  |  | In case of any descrepancy between BPS & Section project, BPS shall prevail. |  |  |  |
|  |  |  |  |  |  | 220 & 48V Battery & Charger |  |  |  |  |  |  |  |  |  |  |  | We presume that existing 220V & 48V battery & Charger have the sufficient capacity to present bay requirments. |  |  | Confirm |  |  |  |
|  |  |  |  |  |  | LT Switchgear (MSB,DCDB,ACDB,MLDB,ELDB) |  |  |  |  |  |  |  |  |  |  |  | We presume that existing LT Switchgear (ACDB, DCDB,MLDB,ELDB,MSB) have the sufficient capacity/Feeder for present bay requirments. |  |  | Please refer our earlier replies above for the similar clarification. |  |  |  |
|  |  |  |  |  |  | 500MVA Auto Transformer Tertiary Loading |  |  |  |  |  |  |  |  |  |  |  | We presume that there is no Tertiary loading in 500MVA Auto Transformer |  |  | Confirm. |  |  |  |
|  |  |  |  |  |  | Switchyard Panel Room/control room |  |  |  |  |  |  |  |  |  |  |  | We presume Switchyard panel room (SPR) is existing and it have sufficient space for persent panels. please confirm |  |  | Please refer our earlier replies above for the similar clarification. |  |  |  |
|  |  |  |  |  |  | Illumination system |  |  |  |  |  |  |  |  |  |  |  | Illumination System: – a) We have considered outdoor lighting scope for the present scope of bays only. Outdoor illumination required for future bays are excluded from our scope of supply & engineering. b) Outdoor lighting fixtures shall be provided on Gantries/Towers to meet the required lux level inside the switchyard. c) We have excluded street lighting. |  |  | Confirmed. |  |  |  |
|  |  |  |  |  |  | Cable trench |  |  |  |  |  |  |  |  |  |  |  | We have considered Cable Trench in switchyard area for bays under present scope of work. For Future area cable trench work is excluded from our scope. |  |  | Confirmed. |  |  |  |
|  |  |  |  |  |  | Lightning Protection |  |  |  |  |  |  |  |  |  |  |  | We presume that Lightning protection already exists in the extension area under present scope. Please confirm |  |  | There is one LM present near the area of ICT-3. The same may be used for DSLP. |  |  |  |
|  |  |  |  |  |  | Visual Monitoring System |  |  |  |  |  |  |  |  |  |  |  | We presume Visual monitoring system (VMS) is not in present scope of work. Please confirm |  |  | Confirmed. |  |  |  |
|  |  |  |  |  |  | Existing CRP, SAS & Telecom system |  |  |  |  |  |  |  |  |  |  |  | Kindly clarify the following: i) Exisiting Main-I and II and backup relay make & model. ii) Exisiting SAS & CRP make and model. iii) Confirmation of all required ports availablitiy in SAS/Gateway for scope system data integration wih existing system. iv) Kindly confirm the Communication protocol for relays within the substations and Remotre substations. v) Kindly Confirm all exisiting relays are communicable type numerical relays. vi) Bus bar protection: Kindly confirm exisiting bus bar protection is compatible for scope bays inclusion. vii) Kindly confirm Type of bus bar protection scheme i.e centralised or decentralised. viii) Telecom system: Kindly Confirm that .Exisitng telecom system suitable for data integration and transfer of scope bays data |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |  |
| B). 400 Bay Extension at Hosur Substation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Tender drawing & details |  |  |  |  |  |  |  |  | As per Tender drawing (SLD & GA) 400kV Main Bus & Jack bus are existing. Please confirm |  |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |  |
|  |  |  |  |  |  | Stone spreding |  |  |  |  |  |  |  |  | We have not considered stone spreading in future bay area. |  |  |  |  |  | Bidder to quote as per BPS. |  |  |  |
|  |  |  |  |  |  | Existing Equipment rating |  |  |  |  |  |  |  |  | We have assumed that all Equipments rating shall be same to that of existing. |  |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |  |
|  |  |  |  |  |  | Order of Prevail |  |  |  |  |  |  |  |  | In Case of any discrepancy between Price schedule, Section project & Tender drawing with Tech. Specification. Kindly confirm the Order of prevail for the qty. estimation. |  |  |  |  |  | In case of any descrepancy between BPS & Section project, BPS shall prevail. |  |  |  |
|  |  |  |  |  |  | 220 & 48V Battery & Charger |  |  |  |  |  |  |  |  | We presume that existing 220V & 48V battery & Charger have the sufficient capacity to present bay requirments. |  |  |  |  |  | Confirmed. |  |  |  |
|  |  |  |  |  |  | LT Switchgear (MSB,DCDB,ACDB,MLDB,ELDB) |  |  |  |  |  |  |  |  | We presume that existing LT Switchgear (ACDB, DCDB,MLDB,ELDB,MSB) have the sufficient capacity/Feeder for present bay requirments. |  |  |  |  |  | Please refer our earlier replies above for the clarification. |  |  |  |
|  |  |  |  |  |  | Switchyard Panel Room/control room |  |  |  |  |  |  |  |  | We presume Switchyard panel room (SPR) is existing and it have sufficient space for present panels. please confirm |  |  |  |  |  | Please refer our earlier replies above for the similar clarification. |  |  |  |
|  |  |  |  |  |  | Illumination system |  |  |  |  |  |  |  |  | Illumination System: – a) We have considered outdoor lighting scope for the present scope of bays only. Outdoor illumination required for future bays are excluded from our scope of supply & engineering. b) Outdoor lighting fixtures shall be provided on Gantries/Towers to meet the required lux level inside the switchyard. c) We have excluded street lighting. |  |  |  |  |  | Confirmed |  |  |  |
|  |  |  |  |  |  | Cable trench |  |  |  |  |  |  |  |  | We have considered Cable Trench in switchyard area for bays under present scope of work. For Future area cable trench work is excluded from our scope. |  |  |  |  |  | Confirmed |  |  |  |
|  |  |  |  |  |  | Lightning Protection |  |  |  |  |  |  |  |  | We presume that Lightning protection already exists in the extension area under persent scope. Plese confirm |  |  |  |  |  | Refer S.NO 02 of Amendment 1 (Part 2) |  |  |  |
|  |  |  |  |  |  | Visual Monitoring System |  |  |  |  |  |  |  |  | We presume Visual monitoring system (VMS) is not in present scope of work. Please confirm |  |  |  |  |  | Confirmed. |  |  |  |
|  |  |  |  |  |  | Existing CRP, SAS & Telecom system |  |  |  |  |  |  |  |  | Kindly clarify the following: i) Exisiting Main-I and II and backup relay make & model. ii) Exisiting SAS & CRP make and model. iii) Confirmation of all required ports availablitiy in SAS/Gateway for scope system data integration wih existing system. iv) Kindly confirm the Communication protocol for relays within the substations and Remotre substations. v) Kindly Confirm all exisiting relays are communicable type numerical relays. vi) Bus bar protection: Kindly confirm exisiting bus bar protection is compatible for scope bays inclusion. vii) Kindly confirm Type of bus bar protection scheme i.e centralised or decentralised. viii) Telecom system: Kindly Confirm that .Exisitng telecom system suitable for data integration and transfer of scope bays data |  |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |  |
|  |  |  |  |  |  | 1X125MVAR Reactor |  |  |  |  |  |  |  |  | We have not considered any cabling, clamps & connector, earthing ETC. for 125MVAR Bus Reactor. Please confirm |  |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |  |
|  |  |  |  |  |  | 400kV Bay Extension at Madhugiri (AIS) Substation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Tender drawing & details |  |  |  |  |  |  |  |  | As per Tender drawing (SLD & GA) 400kV Main Bus & Jack bus are existing. Please confirm |  |  |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |
|  |  |  |  |  |  | Order of Prevail |  |  |  |  |  |  |  |  | In Case of any discrepancy between Price schedule, Section project & Tender drawing with Tech. Specification. Kindly confirm the Order of prevail for the qty. estimation. |  |  |  |  |  |  | In case of any discrepancy between BPS & Section project, BPS shall prevail. |  |  |
|  |  |  |  |  |  | 220 & 48V Battery & Charger |  |  |  |  |  |  |  |  | We presume that existing 220V & 48V battery & Charger have the sufficient capacity to present bay requirments. |  |  |  |  |  |  | Confirmed |  |  |
|  |  |  |  |  |  | LT Switchgear (MSB,DCDB,ACDB,MLDB,ELDB) |  |  |  |  |  |  |  |  | We presume that existing LT Switchgear (ACDB, DCDB,MLDB,ELDB,MSB) have the sufficient capacity/Feeder for present bay requirments. |  |  |  |  |  |  | Please refer our earlier replies above for the clarification. |  |  |
|  |  |  |  |  |  | Switchyard Panel Room/control room |  |  |  |  |  |  |  |  | We presume Switchyard panel room (SPR) is existing and it have sufficient space for persent panels. please confirm |  |  |  |  |  |  | Please refer our earlier replies above for the clarification. |  |  |
|  |  |  |  |  |  | Illumination system |  |  |  |  |  |  |  |  | Illumination System: – a) We have considered outdoor lighting scope for the present scope of bays only. Outdoor illumination required for future bays are excluded from our scope of supply & engineering. b) Outdoor lighting fixtures shall be provided on Gantries/Towers to meet the required lux level inside the switchyard. c) We have excluded street lighting. |  |  |  |  |  |  | Confirmed |  |  |
|  |  |  |  |  |  | Cable trench |  |  |  |  |  |  |  |  | We have considered Cable Trench in switchyard area for bays under present scope of work only |  |  |  |  |  |  | Confirmed |  |  |
|  |  |  |  |  |  | Lightning Protection |  |  |  |  |  |  |  |  | We presume that Lightning protection already exists in the extension area under persent scope. Plese confirm |  |  |  |  |  |  | Refer S.NO 04 of Amendment 1 (Part 2) |  |  |
|  |  |  |  |  |  | Visual Monitoring System |  |  |  |  |  |  |  |  | We presume Visual monitoring system (VMS) is not in present scope of work. Please confirm |  |  |  |  |  |  | Confirmed |  |  |
|  |  |  |  |  |  | Existing CRP, SAS & Telecom system |  |  |  |  |  |  |  |  | Kindly clarify the following: i) Exisiting Main-I and II and backup relay make & model. ii) Exisiting SAS & CRP make and model. iii) Confirmation of all required ports availablitiy in SAS/Gateway for scope system data integration wih existing system. iv) Kindly confirm the Communication protocol for relays within the substations and Remotre substations. v) Kindly Confirm all exisiting relays are communicable type numerical relays. vi) Bus bar protection: Kindly confirm exisiting bus bar protection is compatible for scope bays inclusion. vii) Kindly confirm Type of bus bar protection scheme i.e centralised or decentralised. viii) Telecom system: Kindly Confirm that .Exisitng telecom system suitable for data integration and transfer of scope bays data |  |  |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  |  |  |  |  | 1X125MVAR Reactor |  |  |  |  |  |  |  |  | We have not considered any cabling, clamps & connector, earthing ETC. for 125MVAR Bus Reactor. Please confirm |  |  |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |
| D). 400kV Dharmapuri S/S Extn. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Tender drawing & details |  |  |  |  |  |  |  |  |  |  | As per Tender drawing (SLD & GA) 400kV Main Bus & Jack bus are existing. Please confirm |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |
|  |  |  |  |  |  | Order of Prevail |  |  |  |  |  |  |  |  |  |  | In Case of any discrepancy between Price schedule, Section project & Tender drawing with Tech. Specification. Kindly confirm the Order of prevail for the qty. estimation. |  |  |  |  | In case of any discrepancy between BPS & Section project, BPS shall prevail. |  |  |
|  |  |  |  |  |  | 220 & 48V Battery & Charger |  |  |  |  |  |  |  |  |  |  | We presume that existing 220V & 48V battery & Charger have the sufficient capacity to present bay requirments. |  |  |  |  | Confirmed |  |  |
|  |  |  |  |  |  | LT Switchgear (MSB,DCDB,ACDB,MLDB,ELDB) |  |  |  |  |  |  |  |  |  |  | We presume that existing LT Switchgear (ACDB, DCDB,MLDB,ELDB,MSB) have the sufficient capacity/Feeder for present bay requirments. |  |  |  |  | Please refer our earlier replies above for the clarification. |  |  |
|  |  |  |  |  |  | Switchyard Panel Room/control room |  |  |  |  |  |  |  |  |  |  | We presume Switchyard panel room (SPR) is existing and it have sufficient space for persent panels. please confirm |  |  |  |  | Please refer our earlier replies above for the clarification. |  |  |
|  |  |  |  |  |  | Illumination system |  |  |  |  |  |  |  |  |  |  | Illumination System: – a) We have considered outdoor lighting scope for the present scope of bays only. Outdoor illumination required for future bays are excluded from our scope of supply & engineering. b) Outdoor lighting fixtures shall be provided on Gantries/Towers to meet the required lux level inside the switchyard. c) We have excluded street lighting. |  |  |  |  | Confirmed |  |  |
|  |  |  |  |  |  | Cable trench |  |  |  |  |  |  |  |  |  |  | We have considered Cable Trench in switchyard area for bays under present scope of work only |  |  |  |  | Confirmed |  |  |
|  |  |  |  |  |  | Lightning Protection |  |  |  |  |  |  |  |  |  |  | We presume that Lightning protection already exists in the extension area under persent scope. Plese confirm |  |  |  |  | For Lightning protection (DSLP) calculation of present Bus Reactor bay shall be done by providing GI Earthwire at Existing Tower/Gantries. |  |  |
|  |  |  |  |  |  | Visual Monitoring System |  |  |  |  |  |  |  |  |  |  | We presume Visual monitoring system (VMS) is not in present scope of work. Please confirm |  |  |  |  | Confirmed |  |  |
|  |  |  |  |  |  | Existing CRP, SAS & Telecom system |  |  |  |  |  |  |  |  |  |  | Kindly clarify the following: i) Exisiting Main-I and II and backup relay make & model. ii) Exisiting SAS & CRP make and model. iii) Confirmation of all required ports availablitiy in SAS/Gateway for scope system data integration wih existing system. iv) Kindly confirm the Communication protocol for relays within the substations and Remotre substations. v) Kindly Confirm all exisiting relays are communicable type numerical relays. vi) Bus bar protection: Kindly confirm exisiting bus bar protection is compatible for scope bays inclusion. vii) Kindly confirm Type of bus bar protection scheme i.e centralised or decentralised. viii) Telecom system: Kindly Confirm that .Exisitng telecom system suitable for data integration and transfer of scope bays data |  |  |  |  | Bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  |  |  |  |  | 1X125MVAR Reactor |  |  |  |  |  |  |  |  |  |  | We have not considered any cabling, clamps & connector, earthing ETC. for 125MVAR Bus Reactor. Please confirm |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |
| E). 400kV Hiriyur S/S Extn. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Tender drawing & details |  |  |  |  |  |  |  |  |  |  |  |  | As per Tender drawing (SLD & GA) 400kV Main Bus & Jack bus are existing. Please confirm |  |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |
|  |  |  | Order of Prevail |  |  |  |  |  |  |  |  |  |  |  |  | In Case of any discrepancy between Price schedule, Section project & Tender drawing with Tech. Specification. Kindly confirm the Order of prevail for the qty. estimation. |  |  |  |  |  | In case of any descrepancy between BPS & Section project, BPS shall prevail. |  |  |
|  |  |  | 220 & 48V Battery & Charger |  |  |  |  |  |  |  |  |  |  |  |  | We presume that existing 220V & 48V battery & Charger have the sufficient capacity to present bay requirments. |  |  |  |  |  | Confirmed |  |  |
|  |  |  | LT Switchgear (MSB,DCDB,ACDB,MLDB,ELDB) |  |  |  |  |  |  |  |  |  |  |  |  | We presume that existing LT Switchgear (ACDB, DCDB,MLDB,ELDB,MSB) have the sufficient capacity/Feeder for present bay requirments. |  |  |  |  |  | Please refer our earlier replies above for the clarification. |  |  |
|  |  |  | Switchyard Panel Room/control room |  |  |  |  |  |  |  |  |  |  |  |  | We presume Switchyard panel room (SPR) is existing and it have sufficient space for persent panels. please confirm |  |  |  |  |  | Please refer our earlier replies above for the clarification. |  |  |
|  |  |  | Illumination system |  |  |  |  |  |  |  |  |  |  |  |  | Illumination System: – a) We have considered outdoor lighting scope for the present scope of bays only. Outdoor illumination required for future bays are excluded from our scope of supply & engineering. b) Outdoor lighting fixtures shall be provided on Gantries/Towers to meet the required lux level inside the switchyard. c) We have excluded street lighting. |  |  |  |  |  | Confirmed |  |  |
|  |  |  | Cable trench |  |  |  |  |  |  |  |  |  |  |  |  | We have considered Cable Trench in switchyard area for bays under present scope of work only |  |  |  |  |  | Confirmed |  |  |
|  |  |  | Lightning Protection |  |  |  |  |  |  |  |  |  |  |  |  | We presume that Lightning protection already exists in the extension area under persent scope. Plese confirm |  |  |  |  |  | Refer S.NO 06 of Amendment 01 (Part-2) |  |  |
|  |  |  | Visual Monitoring System |  |  |  |  |  |  |  |  |  |  |  |  | We presume Visual monitoring system (VMS) is not in present scope of work. Please confirm |  |  |  |  |  | Confirmed |  |  |
|  |  |  | Existing CRP, SAS & Telecom system |  |  |  |  |  |  |  |  |  |  |  |  | Kindly clarify the following: i) Exisiting Main-I and II and backup relay make & model. ii) Exisiting SAS & CRP make and model. iii) Confirmation of all required ports availablitiy in SAS/Gateway for scope system data integration wih existing system. iv) Kindly confirm the Communication protocol for relays within the substations and Remotre substations. v) Kindly Confirm all exisiting relays are communicable type numerical relays. vi) Bus bar protection: Kindly confirm exisiting bus bar protection is compatible for scope bays inclusion. vii) Kindly confirm Type of bus bar protection scheme i.e centralised or decentralised. viii) Telecom system: Kindly Confirm that .Exisitng telecom system suitable for data integration and transfer of scope bays data |  |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  |  | 1X125MVAR Reactor |  |  |  |  |  |  |  |  |  |  |  |  | We have not considered any cabling, clamps & connector, earthing ETC. for 125MVAR Bus Reactor. Please confirm |  |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |
|  |  |  | F). 400kV Pugalur S/S Extn. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Tender drawing & details |  |  |  |  |  |  |  |  |  |  |  |  | As per Tender drawing (SLD & GA) 400kV Main Bus & Jack bus are existing. Please confirm |  |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |
|  |  |  | 220 & 48V Battery & Charger |  |  |  |  |  |  |  |  |  |  |  |  | We presume that existing 220V & 48V battery & Charger have the sufficient capacity to present bay requirments. |  |  |  |  |  | Confirmed |  |  |
|  |  |  | LT Switchgear (MSB,DCDB,ACDB,MLDB,ELDB) |  |  |  |  |  |  |  |  |  |  |  |  | We presume that existing LT Switchgear (ACDB, DCDB,MLDB,ELDB,MSB) have the sufficient capacity/Feeder for present bay requirments. |  |  |  |  |  | Please refer our earlier replies above for the clarification. |  |  |
|  |  |  | Switchyard Panel Room/control room |  |  |  |  |  |  |  |  |  |  |  |  | We presume Switchyard panel room (SPR) is existing and it have sufficient space for persent panels. please confirm |  |  |  |  |  | Please refer our earlier replies above for the clarification. |  |  |
|  |  |  | Illumination system |  |  |  |  |  |  |  |  |  |  |  |  | Illumination System: – a) We have considered outdoor lighting scope for the present scope of bays only. Outdoor illumination required for future bays are excluded from our scope of supply & engineering. b) Outdoor lighting fixtures shall be provided on Gantries/Towers to meet the required lux level inside the switchyard. c) We have excluded street lighting. |  |  |  |  |  | Confirmed |  |  |
|  |  |  | Cable trench |  |  |  |  |  |  |  |  |  |  |  |  | We have considered Cable Trench in switchyard area for bays under present scope of work only |  |  |  |  |  | Confirmed |  |  |
|  |  |  | Lightning Protection |  |  |  |  |  |  |  |  |  |  |  |  | We presume that Lightning protection already exists in the extension area under persent scope. Plese confirm |  |  |  |  |  | Refer S.NO 08 of Amendment 01 (Part-2) |  |  |
|  |  |  | Visual Monitoring System |  |  |  |  |  |  |  |  |  |  |  |  | We presume Visual monitoring system (VMS) is not in present scope of work. Please confirm |  |  |  |  |  | Confirmed |  |  |
|  |  |  | Existing CRP, SAS & Telecom system |  |  |  |  |  |  |  |  |  |  |  |  | Kindly clarify the following: i) Exisiting Main-I and II and backup relay make & model. ii) Exisiting SAS & CRP make and model. iii) Confirmation of all required ports availablitiy in SAS/Gateway for scope system data integration wih existing system. iv) Kindly confirm the Communication protocol for relays within the substations and Remotre substations. v) Kindly Confirm all exisiting relays are communicable type numerical relays. vi) Bus bar protection: Kindly confirm exisiting bus bar protection is compatible for scope bays inclusion. vii) Kindly confirm Type of bus bar protection scheme i.e centralised or decentralised. viii) Telecom system: Kindly Confirm that .Exisitng telecom system suitable for data integration and transfer of scope bays data |  |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  |  | 1X125MVAR Reactor |  |  |  |  |  |  |  |  |  |  |  |  | We have not considered any cabling, clamps & connector, earthing ETC. for 125MVAR Bus Reactor. Please confirm |  |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |
|  |  |  | Order of Prevail |  |  |  |  |  |  |  |  |  |  |  |  | In Case of any discrepancy between Price schedule, Section project & Tender drawing with Tech. Specification. Kindly confirm the Order of prevail for the qty. estimation. |  |  |  |  |  | In case of any descrepancy between BPS & Section project, BPS shall prevail. |  |  |
| F). 400kV Pugalur HVDC (GIS) S/S Extn. For B/R-1&2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Eathhmat for GIS |  |  |  |  |  |  |  |  |  | We presume that earthmat for GIS already exists in the extension area under persent scope. Please confirm |  |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |
|  |  |  |  |  |  | 220 & 48V Battery & Charger |  |  |  |  |  |  |  |  |  | We presume that existing 220V & 48V battery & Charger have the sufficient capacity to present bay requirments. |  |  |  |  |  | Confirmed |  |  |
|  |  |  |  |  |  | LT Switchgear (MSB,DCDB,ACDB,MLDB,ELDB) |  |  |  |  |  |  |  |  |  | We presume that existing LT Switchgear (ACDB, DCDB,MLDB,ELDB,MSB) have the sufficient capacity/Feeder for present bay requirments. |  |  |  |  |  | Please refer our earlier replies above for the clarification. |  |  |
|  |  |  |  |  |  | Illumination system |  |  |  |  |  |  |  |  |  | Illumination System: – a) We have considered outdoor lighting scope for the present scope of bays only. Outdoor illumination required for future bays are excluded from our scope of supply & engineering. b) Outdoor lighting fixtures shall be provided on Gantries/Towers to meet the required lux level inside the switchyard. c) We have excluded street lighting. |  |  |  |  |  | Confirmed |  |  |
|  |  |  |  |  |  | Cable trench |  |  |  |  |  |  |  |  |  | We presume that cable trench for GIS already exists in the extension area under persent scope. Plese confirm |  |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |
|  |  |  |  |  |  | Lightning Protection |  |  |  |  |  |  |  |  |  | We presume that Lightning protection already exists in the extension area under persent scope. Plese confirm |  |  |  |  |  | Refer S.NO 09 of Amendment 01 (Part-2) |  |  |
|  |  |  |  |  |  | Visual Monitoring System |  |  |  |  |  |  |  |  |  | We presume Visual monitoring system (VMS) is not in present scope of work. Please confirm |  |  |  |  |  | Confirmed |  |  |
|  |  |  |  |  |  | Existing CRP, SAS & Telecom system |  |  |  |  |  |  |  |  |  | Kindly clarify the following: i) Exisiting Main-I and II and backup relay make & model. ii) Exisiting SAS & CRP make and model. iii) Confirmation of all required ports availablitiy in SAS/Gateway for scope system data integration wih existing system. iv) Kindly confirm the Communication protocol for relays within the substations and Remotre substations. v) Kindly Confirm all exisiting relays are communicable type numerical relays. vi) Bus bar protection: Kindly confirm exisiting bus bar protection is compatible for scope bays inclusion. vii) Kindly confirm Type of bus bar protection scheme i.e centralised or decentralised. viii) Telecom system: Kindly Confirm that .Exisitng telecom system suitable for data integration and transfer of scope bays data |  |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  |  |  |  |  | 1X125MVAR Reactor |  |  |  |  |  |  |  |  |  | We have not considered any cabling, clamps & connector, earthing ETC. for 125MVAR Bus Reactor. Please confirm |  |  |  |  |  | Bidder to quote as per requirement given in Tender documents. |  |  |
| H). 220kV Kochin s/s extn. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 220 & 48V Battery & Charger |  |  |  |  |  |  |  |  |  |  |  |  |  | We presume that existing 220V & 48V battery & Charger have the sufficient capacity to present bay requirments. |  |  |  |  |  | Confirmed |  |  |
|  |  | LT Switchgear (MSB, DCDB, ACDB, MLDB,ELDB) |  |  |  |  |  |  |  |  |  |  |  |  |  | We presume that existing LT Switchgear (ACDB, DCDB,MLDB,ELDB,MSB) have the sufficient capacity/Feeder for present bay requirments. |  |  |  |  |  | Confirmed |  |  |
|  |  | Illumination system |  |  |  |  |  |  |  |  |  |  |  |  |  | Illumination System: – a) We have considered outdoor lighting scope for the present scope of bays only. Outdoor illumination required for future bays are excluded from our scope of supply & engineering. b) Outdoor lighting fixtures shall be provided on Gantries/Towers to meet the required lux level inside the switchyard. c) We have excluded street lighting. |  |  |  |  |  | Confirmed |  |  |
|  |  | Cable trench |  |  |  |  |  |  |  |  |  |  |  |  |  | We have considered Cable Trench in switchyard area for bays under present scope of work only |  |  |  |  |  | Confirmed |  |  |
|  |  | Lightning Protection |  |  |  |  |  |  |  |  |  |  |  |  |  | We presume that Lightning protection already exists in the extension area under persent scope. Plese confirm |  |  |  |  |  | LMs are already existing in the 220kV Switchyard. Bidder to submit DSLP layout based on the existing layout during detailed Engineering |  |  |
|  |  | Visual Monitoring System |  |  |  |  |  |  |  |  |  |  |  |  |  | We presume Visual monitoring system (VMS) is not in present scope of work. Please confirm |  |  |  |  |  | Confirmed |  |  |
|  |  | Existing CRP, SAS & Telecom system |  |  |  |  |  |  |  |  |  |  |  |  |  | Kindly clarify the following: i) Exisiting Main-I and II and backup relay make & model. ii) Exisiting SAS & CRP make and model. iii) Confirmation of all required ports availablitiy in SAS/Gateway for scope system data integration wih existing system. iv) Kindly confirm the Communication protocol for relays within the substations and Remotre substations. v) Kindly Confirm all exisiting relays are communicable type numerical relays. vi) Bus bar protection: Kindly confirm exisiting bus bar protection is compatible for scope bays inclusion. vii) Kindly confirm Type of bus bar protection scheme i.e centralised or decentralised. viii) Telecom system: Kindly Confirm that .Exisitng telecom system suitable for data integration and transfer of scope bays data |  |  |  |  |  | Existing Scheme is of GE make (distributed type duplicate bus bar protection). Details shall be provided during detailed Engineering. Bidder to quote as per BPS |  |  |
|  |  | Line side string Hardware |  |  |  |  |  |  |  |  |  |  |  |  |  | We are not considered the line side (220kV) String Hardware & insulator for present scope of work. |  |  |  |  |  | Transmission line side tension insulator strings for the line termination is also under the scope of this specification. |  |  |
|  |  | Stone spreding |  |  |  |  |  |  |  |  |  |  |  |  |  | We have not considered stone spreading in future bay area. |  |  |  |  |  | Item for stone spreading is already included in BPS. However,Stone spreading in switchyard area shall be decided during detailed engineering |  |  |
|  |  | Order of Prevail |  |  |  |  |  |  |  |  |  |  |  |  |  | In Case of any discrepancy between Price schedule, Section project & Tender drawing with Tech. Specification. Kindly confirm the Order of prevail for the qty. estimation. |  |  |  |  |  | In case of any descrepancy between BPS & Section project, BPS shall prevail. |  |  |
|  |  | I). 400kV Kozhikoda s/s extn. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Existing Plan & Section |  |  |  |  |  |  |  |  |  |  |  |  |  | Kindly provide the existing Plan & Section drawing of the switchyard. |  |  |  |  |  | Drawings enclosed |  |  |
|  |  | Existing Earthmat layout |  |  |  |  |  |  |  |  |  |  |  |  |  | Kindly provide the existing Earthmat Layout |  |  |  |  |  | Drawing enclosed |  |  |
|  |  | 220 & 48V Battery & Charger |  |  |  |  |  |  |  |  |  |  |  |  |  | We presume that existing 220V & 48V battery & Charger have the sufficient capacity to present bay requirments. |  |  |  |  |  | Confirmed |  |  |
|  |  | LT Switchgear (MSB,DCDB,ACDB,MLDB,ELDB) |  |  |  |  |  |  |  |  |  |  |  |  |  | We presume that existing LT Switchgear (ACDB, DCDB,MLDB,ELDB,MSB) have the sufficient capacity/Feeder for present bay requirments. |  |  |  |  |  | Confirmed |  |  |
|  |  | Illumination system |  |  |  |  |  |  |  |  |  |  |  |  |  | Illumination System: – a) We have considered outdoor lighting scope for the present scope of bays only. Outdoor illumination required for future bays are excluded from our scope of supply & engineering. b) Outdoor lighting fixtures shall be provided on Gantries/Towers to meet the required lux level inside the switchyard. c) We have excluded street lighting. |  |  |  |  |  | Confirmed |  |  |
|  |  | Cable trench |  |  |  |  |  |  |  |  |  |  |  |  |  | We have considered Cable Trench in switchyard area for bays under present scope of work only |  |  |  |  |  | Confirmed |  |  |
|  |  | Lightning Protection |  |  |  |  |  |  |  |  |  |  |  |  |  | We presume that Lightning protection already exists in the extension area under persent scope. Plese confirm |  |  |  |  |  | Lightning protection to be achieved by Shield wire included in present scope. Bidder to provide the DSLP layout & Calculation |  |  |
|  |  | Visual Monitoring System |  |  |  |  |  |  |  |  |  |  |  |  |  | We presume Visual monitoring system (VMS) is not in present scope of work. Please confirm |  |  |  |  |  | Confirmed |  |  |
|  |  | Existing CRP, SAS & Telecom system |  |  |  |  |  |  |  |  |  |  |  |  |  | Kindly clarify the following: i) Exisiting Main-I and II and backup relay make & model. ii) Exisiting SAS & CRP make and model. iii) Confirmation of all required ports availablitiy in SAS/Gateway for scope system data integration wih existing system. iv) Kindly confirm the Communication protocol for relays within the substations and Remotre substations. v) Kindly Confirm all exisiting relays are communicable type numerical relays. vi) Bus bar protection: Kindly confirm exisiting bus bar protection is compatible for scope bays inclusion. vii) Kindly confirm Type of bus bar protection scheme i.e centralised or decentralised. viii) Telecom system: Kindly Confirm that .Exisitng telecom system suitable for data integration and transfer of scope bays data |  |  |  |  |  | Existing Scheme is of GE make (distributed type duplicate bus bar protection) . Details shall be provided during detailed Engineering. Bidder to quote as per BPS |  |  |
|  |  | Line side string Hardware |  |  |  |  |  |  |  |  |  |  |  |  |  | We are not considered the line side (220kV) String Hardware & insulator for present scope of work. |  |  |  |  |  | Transmission line side tension insulator strings for the line termination is also under the scope of this specification. |  |  |
|  |  | Stone spreading |  |  |  |  |  |  |  |  |  |  |  |  |  | We have not considered stone spreading in future bay area. |  |  |  |  |  | Item for stone spreading is already included in BPS. However,Stone spreading in switchyard area shall be decided during detailed engineering. |  |  |
|  |  | Order of Prevail |  |  |  |  |  |  |  |  |  |  |  |  |  | In Case of any discrepancy between Price schedule, Section project & Tender drawing with Tech. Specification. Kindly confirm the Order of prevail for the qty. estimation. |  |  |  |  |  | In case of any descrepancy between BPS & Section project, BPS shall prevail. |  |  |
|  |  | CIVIL WORK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | General |  |  |  |  |  |  |  |  |  |  |  |  |  | Kindly provide the Existing Layout, Plan & section for our reference |  |  |  |  |  | The details shall be provided to successful bidder during detailed engg. However, bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | General |  |  |  |  |  |  |  |  |  |  |  |  |  | Kindly confirm the distance of outfall for drainage system |  |  |  |  |  | Bidder shall quote as per BPS. The details of outfall points shall be provided during detailed engineering. |  |  |
|  |  | General |  |  |  |  |  |  |  |  |  |  |  |  |  | Please provide standard drawings of Cable Trench, Tower structure and drain |  |  |  |  |  | Refer Tender drawings. |  |  |
|  |  | Land Acquisition |  |  |  |  |  |  |  |  |  |  |  |  |  | We assume that Land has already been acquired by PGCIL. Please share the cordinates. |  |  |  |  |  | The scope of work is extension of POWERGRID existing Substation s. The co-ordinate shall be provided to successful bidder during detailed engg. |  |  |
|  |  | General |  |  |  |  |  |  |  |  |  |  |  |  |  | Please provide soil report of existing substation for quantity estimation work |  |  |  |  |  | Soil investigation report shall be provided to the successful bidder. However, the bidder is advised to vist the site to acquaint themeselves about the strata of soil. |  |  |
|  |  | General |  |  |  |  |  |  |  |  |  |  |  |  |  | We assume that approach road upto existing site is available and there is no requirement of strengthening of existing approach road, kindly confirm |  |  |  |  |  | Confirmed. |  |  |
|  |  | Dismantling work |  |  |  |  |  |  |  |  |  |  |  |  |  | Please provide the details of the dismantling work. If any |  |  |  |  |  | Bidder to quote as per TS & BPS |  |  |
|  |  | Section Project, 'Cl. 2.2.6, 3 Phase CB,ES & DS |  |  |  |  |  |  |  | Customer's Requirement: 3 Phase CB,ES & DS. |  |  |  |  |  | Bidder's Remark: We provide single phase CB, ES & DS. However our ES and DS mechanism is gang operated. Kindly accept the same. |  |  |  |  |  | Confirmed |  |  |
|  |  | Annexure, BOQ & Technical Specification, Spare parts |  |  |  |  |  |  |  | Customer's Requirement: N/A |  |  |  |  |  | Bidder's Remark: There are different lists for spare parts mentioned in Specification, Annexure and BOQ. Kindly specify which is to be considered. |  |  |  |  |  | All Mandatory spares mentioned in Technical specification, Annexure II and BOQ are to be considered by the bidder. |  |  |
|  |  | TS, 'Cl.5.8, Burn through time |  |  |  |  |  |  |  | Customer's Requirement: Under Cl., it is mentioned that material and thickness of the enclosure shall be such as to withstand an internal flash over without burn through for a period of 300 ms at rated short time withstand current |  |  |  |  |  | Bidder's Remarks: As per IEC 62271-203, Under table 4, it is clearly mentioned that for GIS with short circuit rating greater than or equal to 40kA rms duration of current shall be 0.3s (300 ms) with no fragmentation (but burn through is acceptable). Kindly confirm the same requirement as per IEC |  |  |  |  |  | Bidder to Quote as per The requirement of TS |  |  |
|  |  | TS, Cl.5.32, Alarm in LCC |  |  |  |  |  |  |  | Customer's Requirement: Alarm necessary to indicate deterioration of the gas insulating system. |  |  |  |  |  | Bidder's Remark: No such functions have been incorporated in LCC. Kindly provide us the detail information about what kind of deterioration of gas to be monitored then we can check & revert if possible. |  |  |  |  |  | The said clause pertains to the alarm for Gas Density in GIS compartment and for any other manufacturer recommended parameter of Gas if any |  |  |
|  |  | TS, Cl.5.39, Pressure Vessel code |  |  |  |  |  |  |  | Customer's Requirement: The enclosure shall be manufactured and tested according to the pressure vessel code (ASME/CENELEC code for pressure vessel). |  |  |  |  |  | Bidder's Remark: As material codes are country based codes. For presure vesssel code , We follow KS-D6008 with Equivalent EN code (ENAC-42100). Also we will conduct all pressure test for enclosures as per Cl. 6.103-IEC 62271-203:2011. Kindly confirm the same. |  |  |  |  |  | Bidder to Quote as per The requirement of TS |  |  |
|  |  | GSLD, Extension Link |  |  |  |  |  |  |  | Customer's Requirement: As per GSLD of existing GIS removable link is already shown. |  |  |  |  |  | Bidder's Remark: As per existing GSLD we understood that only interface module shall be considered in our scope as removable link is already considered in existing GIS. Kindly confirm the same. |  |  |  |  |  | Existing GIS Interface module details has been provided in Tender documents. Bidder scope is to do GIS extension as per requirement given in TS. |  |  |
|  |  | General (For All Extn. Substations) |  |  |  |  |  |  |  |  |  |  |  |  |  | This package contains extension of substations, in case existing cable trench is not having sufficient space for lying of present scope package cables, then new Cable trench shall be required to be constructed by Contractor. Please confirm that such additional cable trenches shall be paid as per corresponding individual civil line items in Schedule 3 of BPS. |  |  |  |  |  | Confirmed. |  |  |
|  |  | General (For All Extn. Substations) |  |  |  |  |  |  |  |  |  |  |  |  |  | This package contains extension of substations, Please provide distance between New Switchyard Panel room & Existing Control Room Building for present scope of work as per Section Project. |  |  |  |  |  | New Switchyard Panel room is applicable at Kozhikode S/s Extn. Balance SPR/CRB are existing. Bidder is advised to visit site as per clause no. 2.4 of section project. |  |  |
|  |  | General (For All Extn. Substations) |  |  |  |  |  |  |  |  |  |  |  |  |  | Shutdown whenever required at extension substations for carrying out present scope of work shall be provided by PGCIL. Please confirm. |  |  |  |  |  | Shutdown for execution of works under the present scope shall be arranged by the respective site as considered necessary. |  |  |
|  |  | General (For All Extn. Substations) |  |  |  |  |  |  |  |  |  |  |  |  |  | Please provide size & color of existing CRP panels. |  |  |  |  |  | The details shall be provided to successful bidder during detailed engg. |  |  |
|  |  | General (For All Extn. Substations) |  |  |  |  |  |  |  |  |  |  |  |  |  | Since present scope substations are existing hence we request PGCIL to provide soil investigation reports of all substations under present scope. |  |  |  |  |  | Please refer our earlier replies for the similar query. |  |  |
|  |  | General (For All Extn. Substations) |  |  |  |  |  |  |  |  |  |  |  |  |  | As per scope mentioned, cable sealing end to be provided for switchyard panel rooms of present scope bays however requirement seems to be technically acceptable where new switchyard panel rooms envisaged but seems difficult where switchyard panel room already exist for present scope bay hence we request power grid to remove cable sealing end system requirement for existing switchyard panel room wherein cable sealing end system not available. Kindly confirm |  |  |  |  |  | Cable sealing has been envisaged for any new entry into the Control room building/Switchyard panel room for the present + future(as per SLD) scope of cables (in case there is no space available in the existing entry). |  |  |
|  |  | General (For All Substations) |  |  |  |  |  |  |  |  |  |  |  |  |  | Interface panel requirement & quantities are not specified in section project and BPS. However Interface panels are required as per Sec CRP Rev-09. Please confirm the requirement and quantity of Interface panels. |  |  |  |  |  | Bidder to quote as per requirement specified in BPS. |  |  |
|  |  | General (For All Extn. Substations) |  |  |  |  |  |  |  |  |  |  |  |  |  | Please provide following drawings for Extension S/s 1) Existing SLD Drawing 2) Existing Plan Layout with Equipments & busbar connection. 3) Exisitng Section Layout 4) Existing Earthmat Layout 5) Existing Structure Plan & Section Layout 6) Existing Cable Trench Layout 7) Existing Outdoor Lighting Layout & Distribution diagram 8) Existing DSLP Layout 9) Existing Panel arrangement layout of Control Room building 10) Existing SAS Architecture diagram 11) Existing LT Board drawings (ACDB, DCDB, MLDB & ELDB) 12) Existing Busbar CRP drawing |  |  |  |  |  | Please refer our earlier replies for the similar query. |  |  |
|  |  | General (For All Extn. Substations) |  |  |  |  |  |  |  |  |  |  |  |  |  | Please provide details of Existing Busbar Protection scheme at Extn. S/s for augmentation scope as per section project |  |  |  |  |  | Details of existing Busbar Protection scheme at different Extn. S/s are already specified in section project. |  |  |
|  |  | General (For All Extn. Substations) |  |  |  |  |  |  |  |  |  |  |  |  |  | Please provide details of Existing Substation Automation System at Extn. S/s for augmentation scope as per section project |  |  |  |  |  | Details of existing SAS (where ever applicable) at different Extn. S/s are already specified in section project. |  |  |
|  |  | General (For All Extn. Substations) |  |  |  |  |  |  |  |  |  |  |  |  |  | We presume that sufficient feeders from Exisitng LT Boards are available for present scope of work as per Section Project at Extn. Substations. |  |  |  |  |  | Please refer our earlier replies for the similar query. |  |  |
|  |  | General (For All Extn. Substations) |  |  |  |  |  |  |  |  |  |  |  |  |  | We shall consider 25mm/kV as creepage distance for all Substations assocaited with SS22 package except Gazuwaka S/s. Please confirm. |  |  |  |  |  | Confirmed. For Gazuwaka creepage distance shall be considered as 31mm/KV. Bidder to quote accordingly. |  |  |
|  |  | 220KV HV Power Cable and Termination |  |  |  |  |  |  |  | i) Sch-1 item no. 80,81,66, 67 ii) Section Project - 2.2.7-j) |  |  |  |  |  | We understand that the Single Core Single Run of 220kV Cable shall be used for each phase. Kindly specify the Size of the Cable |  |  |  |  |  | Please refer our earlier replies for the similar query. |  |  |
|  |  | 220KV HV Power Cable and Termination |  |  |  |  |  |  |  | i) Sch-1 item no. 81,67 ii)Technical Specification, EHC Cable, Clause No. 1.16 |  |  |  |  |  | Please confirm whether accessories such as SVL, Link Box, earth cable etc. need to be considered under this item or not. |  |  |  |  |  | Confirmed. Accessories such as SVL, Link Box, earth cable etc. are to be considered under said item. |  |  |
|  |  | Bus Work |  |  |  |  |  |  |  | Sch-1 & Sch-3 |  |  |  |  |  | We presume that only tapping from the existing Main Buses are in the scope of the bidder. |  |  |  |  |  | Extension of Bus has been envisaged for Cochin substation extension only (as already indicated in BPS). For all other substations, tapping is to be done from existing main buses under present scope. |  |  |
|  |  | Fire Protection System : HVW Spray & Hydrant System |  |  |  |  |  |  |  | Sch-1 & Sch-3 |  |  |  |  |  | We understand that HVW Spray System are intended for proposed 125MVAR Reactors and 500MVA ICT only and the HVW Spray system shall be connected to the existing Hydrant System for this Purpose. No additional Hydrant system need to be considered for the proposed Extended Bays of 400kV & 220kV. Kindly clarify the scope of work. |  |  |  |  |  | Please refer our earlier replies for the similar query. |  |  |
|  |  | Fire Protection System : HVW Spray & Hydrant System |  |  |  |  |  |  |  | Sch-1 & Sch-3 |  |  |  |  |  | We understand the capacity of the existing Hydrant System is designed to connect the proposed HVW Spray and associated additional System, and thus no further modification in the equipment (pump, motors, engine driven DG etc.) of the pump house is required and the same is not under bidder's scope. |  |  |  |  |  | Please refer our earlier replies for the similar query. |  |  |
|  |  | Test Certificates |  |  |  |  |  |  |  | Tender Submission |  |  |  |  |  | Kindly accept that the Test Certificates of individual Equipments as per tender can be submitted during detailed engineering after the award. |  |  |  |  |  | Bidder to quote as per tender documents. |  |  |
|  |  | GTP |  |  |  |  |  |  |  | Tender Submission |  |  |  |  |  | Kindly accept that the GTP of individual Equipments as per tender can be submitted during detailed engineering after the award. |  |  |  |  |  | Bidder to quote as per tender documents. |  |  |