# SECTION –PROJECT

Table of Contents

- GENERAL	2

  - Preamble	2

- INTENT OF SPECIFICATION	2

- SCOPE OF WORK	2

- LOCATION OF THE SUBSTATION	5

- SCHEDULE OF QUANTITIES	5

- BASIC REFERENCE DRAWINGS	5

- DIFFERENT SECTIONS OF TECHNICAL SPECIFICATION	5

- MANDATORY SPARES	6

- SPECIAL TOOLS AND TACKLES	6

- FACILITIES TO BE PROVIDED BY THE EMPLOYER	6

- SPECIFIC REQUIREMENT	7

List of Annexures:

| Annexure – I | Break-up of Mandatory Spares (for LS/Lot items) |
| --- | --- |

Technical Specification, Section – Project	{Rev. 01}	Page 1 of 7

Retrofitting of  the 220 kV Switchyard equipments and  control & protection system of 400/220kV Mandola Substation with Substation Automation System and Control & Protection System

SECTION- PROJECT

### GENERAL

### Preamble

Power Grid Corporation of India Ltd. (POWERGRID), a Govt. of India Enterprise is responsible for bulk Power transmission of electrical energy from various Central Govt. Power Projects to various utilities/beneficiaries and interconnecting regional grids, operating and maintaining the National electrical grid of India. It is established with mandate of "We will become a Global Transmission Company with Dominant Leadership in Emerging Power Markets with World Class Capabilities by:

- World Class: Setting superior standards in capital project management and operations for the industry and ourselves.

- Global: Leveraging capabilities to consistently generate maximum value for all stakeholders in India and in emerging and growing economies.

- Inspiring, nurturing and empowering the next generation of professionals.

- Achieving continuous improvements through innovation and state of the art technology.

- Committing to highest standards in health, safety, security and environment.”

as its mission.

  - POWERGRID is retrofitting the 220 kV Switchyard equipments and  control & protection system of 400/220kV Mandola Substation with Substation Automation System and Control & Protection System.

The following sections would cover the scope of work and other relevant details.

### INTENT OF SPECIFICATION

  - The specification includes design, engineering, manufacture, fabrication, testing at manufacturers works, supply including transportation & insurance, unloading at site, storage, erection, testing and commissioning at site of switchyard equipments and Control and relay panels and dismantling of existing  switchyard equipments to retrofit the existing 220 kV Switchyard on turnkey basis at 400/220kV Mandola substation, as required.

  - It is the intent of this specification to describe primary features, materials, and design & performance requirements and to establish minimum standards for the work. The specification is not intended to specify the complete details of various practices of manufactures/ bidders, but to specify the requirements with regard to performance, durability and satisfactory operation under the specified site conditions.

### SCOPE OF WORK

The scope of this specification broadly covers the following:

| 1. | Substation Name | 400/220 kV Mandola SS |
| --- | --- | --- |
|  | Voltage Level | 220 kV |
|  | Bus-Switching Scheme | Double Main & Transfer (DMT) |
|  | Fault level | 50 kA/1 sec |
|  | Retrofitting of 220 kV Switchyard | Retrofitting of 220 kV Switchyard equipments and control & protection system of 8 no line bays,2 no Bus Coupler bays,2 no Bus sectionaliser bays,4 no ICT LV bays |

3.1 The detailed scope of work of the substation package is brought out in subsequent clauses of this section.

3.1.1 Design, engineering, manufacture, testing at manufacture’s work, supply including transportation & insurance, unloading, storage, erection, testing and commissioning of following equipment and items complete in    all respect:

a) 220 kV Air Insulated Switchgear : 220 kV Circuit Breakers (including support structure), Isolators, Current Transformers, Surge Arresters, CVTs.

Retrofitting additionally includes –

- Dismantling of the existing switchyard equipments and shifting from switchyard to store.

- Dismantling of existing CRP panels from control room and shifting from switchyard to store.

- Dismantling of Erection Hardware for 220kV layout (Double Main and Transfer Scheme)-Line Bays, Transformer Bay, Transfer Bus Coupler Bay, Bus Coupler Bay.

- Isolation and dismantling of old control and power cables.

b)Control, Relay & Protection System:

i) Complete relay and protection system for the following bays as per Section– Control and Relay panels -

- 8 no 220 kV Lines

- 2 no Bus Coupler bays

- 2 no Bus Sectionaliser bays

- 2 no Transfer bus coupler bays

- 4 no ICT LV bays

ii)  Augmentation of the 220 kV busbar system- POWERGRID Mandola is equipped with M/s  Hitachi Make   Distributed Busbar Protection System -Type:REB 500 for 220 kV .

- Peripheral   units  for the proposed  220 kV  bays  are mounted  in the existing relay panels and Central units  are  mounted in busbar  protection  panels which is kept in Control Room.

- Present Scope shall cover shifting of the Busbar relay panel from Control Room to SPR and peripheral units from existing panels to present bays panels, including necessary modifications, wiring/ cabling etc and commissioning for completion of the bus bar protection scheme. Augmentation of Busbar protection for 25 MVAr Bus Reactor bay 206 will also be included.

- Any modification required in the existing protection scheme is also included in the present scope. Items & components as required, for completion of 220 kV bus bar augmentation for 220KV bays under present scope shall be provided & bidder to consider the cost of the above under respective BPS items in Installation schedule of BPS.

iii) At present there is 1 no switchyard panel room in 220 kV switchyard accommodating CRP panels of 25 MVAr Bus reactor(Bay 206).  220kV CRP panels to be supplied under present scope shall be kept in new switchyard panel room to be constructed under present scope.

iv) The retrofitting additionally includes:

      - Supply, Laying & termination of new control cables between all Primary Equipment up to CRP and From CRP to Control room.

      - Supply, Laying & termination of new DC power cables from DCDB to New Control, Protection & Automation Panels, DTPC/PLCC and from the new Control Protection Panels to the Bay equipments.

      - Supply and installation of Junction Boxes/ marshalling Boxes as per BoQ and TS and rewiring the existing cables emanating from CT/CVT secondary boxesand CB/Isolator MBs .

      - DTPC(Valiant make) panels for the 8 no Lines are kept in control room.Present scope will include shifting of the DTPC panels from control room to SPR, including necessary modifications, wiring/ cabling etc and commissioning for completion of the line protection protection.

v) Before commencing the replacement of the existing system C&P system, the new IEC 61850 based Control & Protection system shall be installed and commissioned in the SPR room along with all IEDs and will be subjected to testing, validation & verification. Once the overall system is found to be satisfactory, the existing C&P replacement process shall be started.

c) Substation Automation System- For 220kV Mandola substation, IEC 61850 based Sub-station automation system including hardware and software for Local HMI system, Gateway etc. for local as well as for remote control along with associated equipment for following bays (as per Technical Specification, Section - Substation Automation System)-

- 8 no 220 kV Lines

- 2 no Bus Coupler bays

- 2 no Bus Sectionaliser bays

- 2 no Transfer bus coupler bays

- 4 no ICT LV bays

- 1 no  Bus Reactor Bay

The necessary interface equipment and integration work at existing substation for transferring data to NTAMC, Backup NTAMC, RTAMC for Remote operation and to RLDC (RSCC) /NLDC (for supervision) through optical fibre based SDH communication link is also under present scope. SAS panels shall be placed in 400/220kV Control Room. The communication link along with SDH panel upto SDH port shall be provided by POWERGRID.

d)1.1 kV grade Power & Control cables (and special cables, if any) along with complete accessories including cabling from Bay Marshalling Box to bay kiosks /Relay panel room /control room.. Methodology for supply, installation & sizing of cables shall be as per Annexure-S1 of Specific requirement, Rev 08 enclosed at Annexure-III.

e) Erection Hardware: This item of BPS includes clamps & connectors for all bay equipments, conductor, aluminum tubes, Bus bar and earthing materials, Bay marshalling box, spacers, cable sealing arrangement, insulating mats, cable supporting angles/channels, Cable pull pit, Cable trays & covers, Guy arrangement (including insulators and hardware), Junction box, buried cable trenches/pipes for equipment & lighting etc. as required. Erection Hardware for 220kV layout will include-Insulator strings, Disc Insulators, Hardware, conductor, Al tube, bus-bar materials, cable trays, Bay MB, clamps, spacers, connectors including equipment connectors, Junction box, earthwire, earthing material risers, auxiliary earthmat(excluding main earth mat) buried cable trenches/pipe,equipment & lighting, all accessories etc. Terminal connectors,Bay Marshalling Box,CVT &CT junction boxes will be included under erection hardware for respective bays

f) Insulator Strings And Associated Hardware: Insulator strings and associated hardware fittings under present scope shall be provided by the contractor as per Bid Price Schedule (BPS)

g) Smoke detection, Fire alarm & Annunciation system for switchyard panel room as per technical specifications is included in present scope and integrated with SAS/IED. Portable fire extinguisher (CO2 type) of 4.5kg for switchyard panel room shall be provided as per bid proposal sheets (BPS) under present scope

h) Air Conditioning System (As per BPS): Air Conditioning System for Switchyard Panel Rooms.

i) The work to be done under this specification shall include all labour, plant, equipment, material and performance of all work necessary for the complete installation and commissioning of switchyard. All apparatus, appliances, material and labour etc. not specifically mentioned or included, but are necessary to complete the entire work or any portion of the work in compliance with the requirements implied in this specification is deemed to be included in the scope of contractor.

j) Before proceeding with the work for this project, the Contractor shall fully familiarize himself with the site conditions and General arrangements & scheme etc. Though the Employer shall endeavor to provide the information, it shall not be binding for the Employer to provide the same. The bidders are advised to visit the substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy. The bidder shall be fully responsible for providing all equipment, materials, system and services specified or otherwise which are required to complete the successful commissioning, operation & maintenance of this project in all respects. All materials required for the Civil and construction/installation work shall be supplied by the Contractor. The cement and steel shall also be supplied by the Contractor. The complete design (unless specified otherwise in specification elsewhere) and detailed engineering shall be done by the Contractor based on conceptual tender drawings, enclosed in the bidding document.

k) The Contractor shall also be responsible for the overall co-ordination with internal/external agencies, project management, training of Employer's manpower, loading, unloading, handling, moving to final destination for successful erection, testing and commissioning of the system.

l) Any other items not specifically mentioned in the specification but which are required for erection, testing and commissioning and satisfactory operation of this system are deemed to be included in the scope of the specification unless specifically excluded elsewhere. The contractor shall arrange all T&P (such as necessary supports, cranes, ladders, platforms etc.) for erection, testing & commissioning of the system at his own cost. Further, all consumables, wastage and damages shall be to the account of holder.

m) Employer has standardized its technical specification for various equipment and works for different voltage levels. Items, which are not applicable for the scope of this package as per schedule of quantities described in BPS, the technical specification for such items should not be referred to.

n) Any other equipment/material required to complete the specified scope.

3.1.2 Design, engineering, manufacture, testing and supply including transportation & insurance, storage and testing at site of mandatory spares as per Bid Price Schedule (BPS).

3.1.3 CIVIL WORK

A. CIVIL WORKS & SUPPORT STRUCTURE:

I. CIVIL WORKS: BASED ON POWERGRID SUPPLIED DRAWINGS-

a) Switchyard Panel Room

b) Cable Trenches: Cable trenches including cable trenches  along with covers including road/rail crossing, sump pits, culverts etc. shall be constructed as per POWERGRID standard drawings provided in tender.

i). However, Cable trench layout shall be prepared by vendor for approval of POWERGRID based on the cable trench sections available in Tender Drawings.

ii). Mode of measurement: Cable Trenches shall be measured in running meters. The rate shall include the cost of all works such as excavation, PCC, RCC, Reinforcement Steel, Miscellaneous Structural Steel, inserts, embedment etc. Cable Trench together with its cover shall be measured in running meter for payment purpose.

II. CIVIL WORKS: BASED ON DESIGNS, ARCHITECTURAL, STRUCTURAL, FOUNDATION DRAWINGS TO BE DEVELOPED BY THE CONTRACTOR-

a) Foundation for switchyard equipments, bay marshalling boxes, panels and control cubicles wherever required. The cost of these foundations shall be deemed to be included in erection/installation of corresponding item/ equipment of BPS.If any modification in the existing foundation of the equipments is required same shall be deemed to be included in erection.

III LATTICE AND PIPE STRUCTURES (GALVANIZED):

a) Lattice and Pipe structures (galvanized): Equipment support structures shall be provided as per employer’s drawing. The existing equipment support structures are envisaged to be utilized for installation of switchyard equipment.

b) Single line diagram/ Fabrication Drawings of equipment support structures shall be provided by POWERGRID during detailed Engineering stage except for those structures that are in the scope of contractor. All other details such as proto, BOM etc. shall be developed by the contractor.

### LOCATION OF THE SUBSTATION

The location of sub-stations is as under:

| S. No. | Name of substation | Name of State | Nearest rail Station |
| --- | --- | --- | --- |
| 1. | 400/220 kV Powergrid Sub Station,Loni-bhagpat road,Mandola,Ghaziabad Uttar Pradesh 201102 | Uttar Pradesh | Ghaziabad |

For design purposes, ambient temperature shall be considered as 50 degrees centigrade.

### SCHEDULE OF QUANTITIES

The requirement of various items /equipment are indicated in Bid price Schedules.

All equipment/items and for which quantities has been given in the BPS shall be payable on unit rate basis. During actual execution, any variation in such quantities shall be paid based on the unit rate under each item incorporated in the letter of award.

Wherever the quantities of items/works are indicated in Lot/Set/LS, the bidder is required to estimate the quantity required for entire execution and completion of works and incorporate their price in respective Bid price schedules. For erection hardware items, Bidders shall estimate the total requirement of the works and indicate module-wise lump sum price bay wise and include the same in relevant Bid price schedules. Any material/works for the modules not specifically mentioned in the description in BPS, as may be required shall be deemed to be included in the module itself.

No cost compensation shall be considered on account of “Set/LOT/LS” items in any case of

number of bays specified in section project remains unchanged

Bidder should include all such items in the bid proposal sheets, which are not specifically mentioned but are essential for the execution of the contract. Item which explicitly may not appear in various schedules and required for successful commissioning of substation shall be included in the bid price and shall be provided at no extra cost to Employer.

### BASIC REFERENCE DRAWINGS

400/220kV Mandola Substation has Air Insulated Substation bays. Single line diagrams are enclosed with the bid documents, which shall be referred to by the bidder during engineering.

### DIFFERENT SECTIONS OF TECHNICAL SPECIFICATION

For the purpose of present scope of work, technical specification (Vol. II) shall consist of following sections and they should be read in conjunction with each other.

| S. No. | Description | Revision |
| --- | --- | --- |
| 1 | Section – Project | Rev 00 |
| 2 | Section – General Technical Requirement | Rev 15 |

| 3 | Section – Power & Control Cable | Rev 06 |
| --- | --- | --- |
| 4 | Section-Switchgear- CB | Rev 11 |
| 5 | Section-Switchgear- ISO | Rev 12 |
| 6 | Section-Switchgear- Instrument Transformer | Rev 11 |
| 7 | Section-Switchgear- Surge Arrester | Rev 12 |
| 8 | Section-Fire Protection System | Rev 06 |
| 9 | Section-Air Conditioning System | Rev 04 |
| 10 | Section – Switchyard Erection | Rev 10 |
| 11 | Section- Structures | Rev 06 |
| 12 | Section – Civil Works | Rev 12 |
| 13 | Section – Control & Relay Panel | Rev 09 |
| 14 | Section – Substation Automation System | Rev 04 |
| 15 | Section – Digital Protection Coupler | - |

In case of any discrepancy between Section-PROJECT, Section-GTR and other technical specifications on scope of works, Section-PROJECT shall prevail over all other sections.

In case of any discrepancy between Section-GTR and individual sections for various equipment, requirement of individual equipment section shall prevail.

### MANDATORY SPARES

The prices of mandatory spares shall be given by the Bidder in the relevant schedule of BPS and shall be considered for evaluation of bid. It shall not be binding on the Employer to procure all of these mandatory spares.

The bidder is clarified that no mandatory spares shall be used during the commissioning of the equipment. Any spares required for commissioning purpose shall be arranged by the Contractor. The unutilized spares if any brought for commissioning purpose shall be taken back by the contractor.

Wherever spares in BPS/Technical Specification has been specified as “each type/each rating/each type & rating”: If the offered spare/spares is sufficient to replace the respective main equipment of all types/ratings, then such offered spare/spares shall be acceptable. It implies that common spare/spare set fulfilling the spare requirement of all types/ratings shall also be acceptable, provided it is configurable at site itself without special assistance of OEM.

Mandatory Spares, wherever mentioned, are envisaged for the equipment/items being supplied under the main equipment heads under present scope meeting the requirements of Technical Specifications. The component/sub-component of an equipment/item specified in BPS under Mandatory Spare, which is not applicable as per the offered design of respective main equipment, shall not be referred to.

### SPECIAL TOOLS AND TACKLES

The bidder shall include in his proposal the deployment of all special tools and tackles required for erection, testing, commissioning, operation and maintenance of equipment. The special tools and tackles shall only cover items which are specifically required for the equipment offered and are proprietary in nature. In addition to this, the Contractor shall also furnish a list of special tools and tackles for the various equipment in a manner to be referred by the Employer during the operation of these equipment. The scope of special tools and tackles are to be decided during detail Engineering and the list of special tools and tackles if any shall be finalized.

### FACILITIES TO BE PROVIDED BY THE EMPLOYER

- Employer shall make available the auxiliary HT power supplies from SEB/Distribution Company on chargeable basis at a single point in the Sub-station. The prevailing energy rates of the state shall be applicable. All further distribution from the same for construction and permanent auxiliary supply shall be made by the contractor. However, in case of failure of power due to any unavoidable circumstances, the contractor shall make his own necessary arrangements like diesel generator sets etc. at his own cost so that progress of work is not affected and Employer shall in no case be responsible for any delay in works because of non-availability of power.

- Employer shall make available construction water supply at a single point in the substation. All further distribution for the same shall be made by the Contractor. In case of non-availability or inadequate availability of water for construction work, the contractor shall make his own arrangement at his own cost and the Employer shall in no case be responsible for any delay in works because of non-availability or inadequate availability of water.

### SPECIFIC REQUIREMENT

- Contractor shall provide detailed shutdown plan well in advance so that Shutdown can be arranged by POWERGRID.

- Contractor shall submit all drawings for approval

- The specific requirements as mentioned at C/ENGG/SPEC/SEC-PROJECT/SPECIFIC REQUIREMENT Rev. No 08 shall be referred for specified scope of work. Any discrepancy between clause 9.0 Section PROJECT and Annex-II on scope of works, the requirement stipulated at clause 9.0 of section project shall prevail.

- The Contractor shall be responsible to select and verify the route, mode of transportation and make all necessary arrangement with the appropriate authorities for the transportation of the equipment. The dimension of the equipment shall be such that when packed for transportation, it will comply with the requirements of loading and clearance restrictions for the selected route.

- The bidder shall be responsible for safety of human and equipment during the working. It will be the responsibility of the Contractor to co-ordinate and obtain Electrical Inspector's clearance before commissioning. Any additional items, modification due to observation of such statutory authorities shall be provided by the Contractor at no extra cost to the Employer.

- Erection, Testing and Commissioning of equipments, Relay & protection panels and sub-station automation system shall be done by the contractor under the supervision of respective equipment manufacturers. Such supervision charges shall be included by the bidder in the erection charges for the respective equipment in the BPS.

- In Section-GTR and other technical specifications, the word ‘Purchaser’ and/or ‘Owner’ may be read as ‘Employer’.