| Sr. No | Clause No. & Existing Specification/section of the bidding documents | Existing provisions | Amended provisions |
| --- | --- | --- | --- |
| 1 | Cl No 1.4 of SECTION-VII B (VOLUME-II), Rev 4 of Technical Specification | The calculations for Ampacity shall generally be based on IEEE Standard 738:2012 in SI units except otherwise specified herein. For calculation of the radial temperature gradient within the conductor, effective thermal conductivity (kth) shall be considered as 1 watt/m-°C. Further, conductor sag at designed maximum temperature shall be calculated considering temperature of core corresponding to the designed maximum temperature of conductor shall be calculated, irrespective of the magnitude of radial temperature gradient. | The calculations for Ampacity shall generally be based on IEEE Standard 738:2023 in SI units except otherwise specified herein. For calculation of the radial temperature gradient within the conductor, effective thermal conductivity (kth) shall be considered as 1 watt/m-°C. Further, conductor sag at designed maximum temperature shall be calculated considering temperature of core corresponding to the designed maximum temperature of conductor, irrespective of the magnitude of radial temperature gradient. |
| 2 | Cl No 2.14.2 of SECTION-VII B (VOLUME-II), Rev 4 of Technical Specification | 2.14 Standards 2.14.1 The conductor shall conform to the following Indian /International Standards, which shall mean latest revisions, with amendments/changes adopted and published, unless specifically stated otherwise in the Specification. Sl. No; Indian Standard; Title; International Standard. 1; IS 209: 1992; Specification for Zinc. ….; …; …; ……. 18; IEEE Standard for Calculating the Current-Temperature Relationship of Bare Overhead Conductors; IEEE 738:2012. | 2.14 Standards 2.14.1 The conductor shall conform to the following Indian/ International Standards, which shall mean latest revisions, with amendments/changes adopted and published, unless specifically stated otherwise in the Specification. Sl.No; Indian Standard; Title; International Standard. 1; IS 209: 1992; Specification for Zinc. ….; …; …; ……. 18; IEEE Standard for Calculating the Current-Temperature Relationship of Bare Overhead Conductors; IEEE 738:2023. |
| 3 | Cl.18 of Annexure-A of SECTION-VII B (VOLUME-II), Rev 4 of Technical Specification | 18 Bending Test on Composite Core (as Type Test) Bending test on composite core before stranding shall be performed as per ASTM B987/B987M-17 on composite core samples taken from composite core at conductor manufacturing unit before stranding of conductor. Alternatively, supplier may carry out bending test on composite core before stranding on the samples taken at the core manufacturing unit, from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Bending test on composite core shall also be performed as per ASTM B987/ B987M-17 on composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: For high strength grade composite core: 60 times the diameter of composite core. For Extra high strength grade composite core: 70 times the diameter of composite core. | 18 Bending Test on Composite Core (as Type Test) Bending test on composite core before stranding shall be performed as per ASTM B987/B987M-20 on composite core samples taken from composite core at conductor manufacturing unit before stranding of conductor. Alternatively, supplier may carry out bending test on composite core before stranding on the samples taken at the core manufacturing unit, from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Bending test on composite core shall also be performed as per ASTM B987/ B987M-20 on composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: For high strength grade composite core: 60 times the diameter of composite core. For Extra high strength grade composite core: 70 times the diameter of composite core. |
| 4 | Cl.33 of Annexure-A of SECTION-VII B (VOLUME-II), Rev 4 of Technical Specification | 33 Bending test on Composite Core (as Acceptance test) Bending test on composite core shall be performed as per ASTM B987/ B987M-17 on composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: 1) For high strength grade composite core: 60 times the diameter of composite core. 2) For Extra high strength grade composite core: 70 times the diameter of composite core. | 33 Bending test on Composite Core (as Acceptance test) Bending test on composite core shall be performed as per ASTM B987/ B987M-20 on composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: 1) For high strength grade composite core: 60 times the diameter of composite core. 2) For Extra high strength grade composite core: 70 times the diameter of composite core. |
| 5 | Technical Specification Section VII B Volume-II Rev 4 (March’2024) Cl 2.1.1 (I) and Cl 2.2 (u) | 2.1.1 Type Tests on Stranded Conductor/ Core …..…….. - On complete Conductor ........... ......... l); Salt Spray Test (applicable for composite core conductor not conforming to ASTM B987); Annexure- A. 2.2 Acceptance Tests .................. u); Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductor conforming to ASTM B987); ASTM B987. | 2.1.1 Type Tests on Stranded Conductor/ Core …..…….. - On complete Conductor ........... ......... l); Salt Spray Test (applicable for composite core conductor not conforming to ASTM B987); Annexure- A. 2.2 Acceptance Tests .................. u); Galvanic Protection Barrier Layer Thickness test on composite core; ASTM B987 or any other published national or international standards. |
| 6 | Technical Specification Section VII B Volume-II Rev 4 Annexure-A | Cl.11 Salt Spray Test The test shall be performed as per ASTM B117 on 3 samples of conductor, each 1 m in length. …………………………………………………………………………………………………………………… …………………………………………. The individual strands of aluminum/ aluminum alloy and the composite core shall retain 95% of the strength guaranteed | Deleted |
| 7 | SECTION-VII B HTLS CONDUCTOR, STANDARD SPECIFICATION OF TRANSMISSON LINE (SECTION-HTLS CONDUCTOR), Volume-II | Existing file namely ‘07_3 Section VII B HTLS Conductor Rev-4(March'2024)’ is stand replaced with new file namely, 07_3 Section VII B HTLS Conductor Rev-5(Sept'2024), which is enclosed herewith. |  |