| Sr. No | Clause No. & Existing Specification | Existing Specification | Clarification / Change in Specification requested | POWERGRID Clarification |
| --- | --- | --- | --- | --- |
| 1 | Cl No 1.4 of SECTION-VII B (VOLUME-II), Rev 4 of Technical Specification | The calculations for Ampacity shall generally be based on IEEE Standard 738:2012 in SI units except otherwise specified herein. For calculation of the radial temperature gradient within the conductor, effective thermal conductivity (kth) shall be considered as 1 watt/m-°C. Further, conductor sag at designed maximum temperature shall be calculated considering temperature of core corresponding to the designed maximum temperature of conductor shall be calculated, irrespective of the magnitude of radial temperature gradient. | Request for modification & amendment as per latest standard. The calculations for Ampacity shall generally be based on IEEE Standard 738:2023 in SI units except otherwise specified herein. For calculation of the radial temperature gradient within the conductor, effective thermal conductivity (kth) shall be considered as 1 watt/m-°C. Further, conductor sag at designed maximum temperature shall be calculated considering temperature of core corresponding to the designed maximum temperature of conductor shall be calculated, irrespective of the magnitude of radial temperature gradient. | Bidders may refer to Amendment-I |
| 2 | Cl. No. 1.9.2 SECTION-VII B (VOLUME-II), Rev-4 of Technical Specification | 1.9.2 Core 1.9.2.1 The core wire strand(s) shall be of galvanized steel/ Invar wires/ or Zinc-5% ………………………………………………………………… ……………………….However, in no case, the guaranteed values for torsion & elongation of Steel/ Invar core of the offered HTLS Conductor shall be less than as indicated below: Minimum No. of twists in gauge length equal to 100 times the dia. of wire which the strand can withstand in the torsion test (before stranding) * 12 Minimum elongation (%) of the core strand (after stranding) for a gauge length of 250 mm (at break) 1.5 | Kindly amend the torsional & elongations requirements for galvanized steel/ Invar wires/Cladded steel or Zinc-5% as per latest standard IEC 63248. | Bidder to follow the provisions mentioned in TS. |
| 3 | Cl.18 of Annexure-A of SECTION-VII B (VOLUME-II), Rev 4 of Technical Specification | Bending test on composite core (acceptance test and type test) Bending test on composite core shall also be performed as per ASTM B987/ B987M-17 | Pls. modify as latest standard Bending test on composite core shall also be performed as per ASTM B987-20 | Bidders may refer to Amendment-I |
| 4 | Cl.2.0 SECTION-VII B (VOLUME-II), Rev 4 of Technical Specification | 2.1.1 Type Tests on Stranded Conductor/ Core i) On complete Conductor ........... ......... l) Salt Spray Test (applicable for composite core conductor not conforming to ASTM B987) 2.2 Acceptance Tests .................. u) Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductor conforming to ASTM B987) ASTM B987 and Cl. 11 Annexure – Salt spray tests. | As per the advisory of CEA, we request you to incorporate “Galvanic Protection Barrier Layer Thickness Test” for determining the efficiency of the galvanic protection layer on carbon fibre composite core to protect CFC against the Galvanic corrosion (please refer the attached CEA advisory). We hence request to remove the salt spray test clause wherever applicable as specified. | Bidders may refer to Amendment-I |
| 5 | A) For 400Kv D/C Somanahalli-Bidadi TL: B)For 400Kv S/C Maheswaram(PG) Hyderabad | Sag for ruling span at minimum temp (0 deg C) and no wind condition (m) - ≥ 9.67 | Kindly modify as mentioned below, Sag for ruling span at minimum temp (0 deg C) and no wind condition (m) - ≥ 9.60 mtr. | Bidder to follow the provisions mentioned in TS. |
| 6 | A) For 400Kv D/C Somanahalli-Bidadi TL: B) For 400Kv S/C Maheswaram(PG)-Hyderabad TL: | Tower spotting data for 400 kV TL | Request to provide tower spotting data for A) For 400Kv D/C Somanahalli-Bidadi TL: B) For 400Kv S/C Maheswaram(PG)-Hyderabad TL: | Tower schedules of both the lines are attached. |
| 7 | List of special tools | Supply of one set of all the special tools & tackles required for stringing of the offered HTLS conductor. | Kindly share list of same. | List already mentioned in Sec-IVC Appendix IV |
| 8 | Technical Specification Section VII B Volume-II Rev 4 (March’2024) Cl 2.1.1 (I) and Cl 2.2 (u) | 2.1.1 Type Tests on Stranded Conductor/ Core …..…….. - On complete Conductor ........... ......... l); Salt Spray Test (applicable for composite core conductor not conforming to ASTM B987); Annexure-A. 2.2 Acceptance Tests .................. u); Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductor conforming to ASTM B987); ASTM B987. | As per Guidelines of CEA, we request your good office to incorporate “Galvanic Protection Barrier Layer Thickness Test” for determining the efficacy of the galvanic protection layer on the carbon fiber composite core to protect CFC against the galvanic corrosion (please refer the attached CEA Guideline). We would like to bring to your kind notice that “Galvanic Protection Barrier Layer Thickness Test” is one of the mandatory tests as per the procedure laid down in the ASTM B987 and in any case “salt spray test; shall not be used as a substitute for “Galvanic Protection Barrier Layer Thickness Test” as per the guidelines given by CEA. | Kindly refer Amendment-I |
| 9 | SECTION-VII B Cl No 1.4 of | The calculations for Ampacity shall generally be based on IEEE Standard 738:2012 in SI units except otherwise specified herein. For calculation of the radial temperature gradient within the conductor, effective thermal conductivity (kth) shall be considered as 1 watt/m-°C. Further, conductor sag at designed maximum temperature shall be calculated considering temperature of core corresponding to the designed maximum temperature of conductor shall be calculated, irrespective of the magnitude of radial temperature gradient. | We insist to change and modify as per latest standard. The calculations for Ampacity shall generally be based on IEEE Standard 738:2023 in SI units except otherwise specified herein. For calculation of the radial temperature gradient within the conductor, effective thermal conductivity (kth) shall be considered as 1 watt/m-°C. Further, conductor sag at designed maximum temperature shall be calculated considering temperature of core corresponding to the designed maximum temperature of conductor shall be calculated, irrespective of the magnitude of radial temperature gradient. | Bidders may refer to Amendment-I |
| 10 | Cl. No. 1.9.2 SECTION-VII B (VOLUME-II), Rev-4 of Technical Specification | 1.9.2 Core 1.9.2.1 The core wire strand(s) shall be of galvanized steel/ Invar wires/ or Zinc-5% ………………………………………………………………… ……………………….However, in no case, the guaranteed values for torsion & elongation of Steel/ Invar core of the offered HTLS Conductor shall be less than as indicated below: Minimum No. of twists in gauge length equal to 100 times the dia. of wire which the strand can withstand in the torsion test (before stranding) * 12 Minimum elongation (%) of the core strand (after stranding) for a gauge length of 250 mm (at break) 1.5 | We insist to change requirement of torsional & elongations for galvanized steel/ Invar wires/Cladded steel or Zinc-5% as per latest standard IEC 63248. | Bidder to follow the provisions mentioned in TS. |
| 11 | Cl.2.0 SECTION-VII B (VOLUME-II), Rev 4 of Technical Specification | 2.1.1 Type Tests on Stranded Conductor/ Core i) On complete Conductor ........... ......... l) Salt Spray Test (applicable for composite core conductor not conforming to ASTM B987) 2.2 Acceptance Tests .................. u) Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductor conforming to ASTM B987) ASTM B987 and Cl. 11 Annexure – Salt spray tests. | We hereby request to remove the salt spray test clause wherever applicable. With reference to the advisory of CEA, we insist you to incorporate “Galvanic Protection Barrier Layer Thickness Test” to determine the efficiency of the galvanic protection layer over carbon fibre composite core to protect Core against the Galvanic Corrosion (please refer the attached CEA advisory). | Bidders may refer to Amendment-I |
| 12 | Cl.18 of Annexure-A of SECTION-VII B (VOLUME-II), Rev 4 of Technical Specification | Bending test on composite core (acceptance test and type test) Bending test on composite core shall also be performed as per ASTM B987/ B987M-17 | We insist to modify to the latest standard Bending test on composite core shall also be performed as per ASTM B987-20 | Bidders may refer to Amendment-I |
| 13 | SECTION-I A (VOLUME-II), Rev 9 A) For 400Kv D/C Somanahalli-Bidadi TL, B)For 400Kv S/C Maheswaram(PG)-Hyderabad TL, | Sag for ruling span at minimum temp (0 deg C) and no wind condition (m) - ≥ 9.67 | Kindly modify as mentioned below, Sag for ruling span at minimum temp (0 deg C) and no wind condition (m) - ≤ 9.67 mtr | Bidder to follow the provisions mentioned in TS. |
| 14 | List of special tools | Supply of one set of all the special tools & tackles required for stringing of the offered HTLS conductor. | Please share bifurcation of sets or List of Equipment which are to be supplied for stringing of the offered HTLS Conductor | List already mentioned in Sec-IVC Appendix IV of TS. |
| 15 | SECTION-VII B Cl No 1.4 of | The calculations for Ampacity shall generally be based on IEEE Standard 738:2012 in SI units except otherwise specified herein. For calculation of the radial temperature gradient within the conductor, effective thermal conductivity (kth) shall be considered as 1 watt/m-°C. Further, conductor sag at designed maximum temperature shall be calculated considering temperature of core corresponding to the designed maximum temperature of conductor shall be calculated, irrespective of the magnitude of radial temperature gradient. | We insist to change and modify as per latest standard. The calculations for Ampacity shall generally be based on IEEE Standard 738:2023 in SI units except otherwise specified herein. For calculation of the radial temperature gradient within the conductor, effective thermal conductivity (kth) shall be considered as 1 watt/m-°C. Further, conductor sag at designed maximum temperature shall be calculated considering temperature of core corresponding to the designed maximum temperature of conductor shall be calculated, irrespective of the magnitude of radial temperature gradient. | Bidders may refer to Amendment-I |