## Technical
Clarification No 01 (Technical) dated 16.06.2026 Package RCP-01 for Retrofit of existing conventional control and protection system with new IEC 61850 Process Bus based Control and Protection System at 400/220 Hissar S/s and 400kV Ballabhgarh S/s; Specification No(s).: CC/NT/W-MISC/DOM/A04/26/01660
SI.No | Volume/Section | Clause No. | Description | Bidder's Query | POWERGRID's Reply
1 | Technical Specification, Section – Project {Rev. 00} | Sheet no 5 of 15, CL C, iii. MODIFICATION OF EXISTING CRP: | For bays under present scope, PMU IEDs are already existing in a separate panel. Refer Annexure IV for Existing PMU details. Required modification in wiring of analog and digital signals to existing PMU is included under present scope. | As understood that Existing PMU's are already under operational in Separate Panel and no further modification of wiring is required inside panel. However, New CT & PT cable need to be layed and terminated in PMU Panel located in control room from outdoor SGMU Panel. Please confirm our understanding is correct. | Confirmed. Present scope also include wiring of Binary inputs required for PMU operations
2 | Technical Specification, Section – Project {Rev. 00} | Sheet no 7 of 15, CL 2.1.2,a) Retrofit at Ballabhgarh Substation | The 220kV Busbar is available at BBMB SAMAYPUR switchyard | As understood that 220kV Busbar Protection is available in Samaypur switchyard. However, Shifting, erection, installation, testing and commissioning of existing 220kV Busbar Protection Panel at 220kV Balabhgarh Ss is not envigased under bidder scope. Please confirm. | Bidder understanding is in order
3 | Technical Specification, Section – Project {Rev. 00} | Sheet no 8 of 15, CL 2.1.2,a) Retrofit at Ballabhgarh Substation | Existing 220kV bus bar protection is installed at BBMB switchyard. All busbar/LBB signals required from 220kV yard for control and protection of 400/220kV Transformer shall be wired upto DIT panel provided for the respective Transformer. Also, all signals required to be wired to 220kV busbar/LBB panels including intertrips etc. shall be made available at DIT panels of the respective ICT and wired upto respective 220kV CRP panels in the BBMB yard. Accordingly, additional cards required for same shall be provided in the DIT Panels of the ICT bay | a) Please provide the existing Busbar Protection Relay Details.( Make and Model). b) Please confirm that existing Busbar protection relay is suitable for accommodate 220kV ICT -4 Bays. | Details shall be provided during execution stage. However replacement of 220kV bus bar protection is not envisaged in the present scope of work
4 | Technical Specification, Section – Project {Rev. 00} | Sheet no 13 of 15, CL 7, SPECIFIC REQUIREMENT | Before commencing the replacement of the existing system, the new IEC 61850 Process Bus based Control & Protection system shall be installed and commissioned with all Process Level IEDs and will be subjected to testing, validation & verification. Once the overall system is found to be satisfactory, the replacement process shall be started. | Existing Control Room doesn’t have enough space to install new process bus protection panel. Hence, Based on shutdown plan CRP Panel, SGMU, CT & VT Jucntion Box and Cabling works will be initated. Please accept. | Necessary vacant space shall be intimated by POWERGRID during detailed engineering.
5 | Technical Specification, Section – Project {Rev. 00} | Sheet no 10 of 15, CL 2.1.4, | All materials required for the Civil and construction /installation work shall be supplied by the Contractor. The cement and steel shall also be supplied by the Contractor. | Going forward to your PGCIL confirmation ; (A) We understand that civil works in the existing control room building i.e. removal of tiles, modification in the existing base frame for mounting CRP, PMU,PLCC panels, cutting the groove on the floor, re-fixing of the tiles and restoration of the tiles back to orignal position will be executed by PGCIL. After the clear front is provided by PGCIL , the bidder will be responsible to mount the CRP panels / PMU panels / PLCC panels and complete the installation, testing & commissioning works. We wish to request PGCIL to confirm the plan / program of completion of these works so that installation scheduel can be prepared and submitted by bidder for approval for seamless execution of works at site. (B) The civil foundation for SGCMU / DIR / DIT alongwith supply & setting up of anchor plates, anchor bolts & fastners , base frame will be executed by PGCIL and the bidder will be responsible for mounting & fixing the MU, DIR, DIT panels on these foundations in the switchyard. | A. Bidder understanding is in order. Plan and program of work shall be provided during the execution stage. B. Bidder understanding is in order. Howevel Pnael details along with loading etc. shall be provided by bidder for design of Civil foundation.
6 | Technical Specification, Section – Project {Rev. 00} |  |  | Earthing materials supply & installation work for SGCMU, DIR, DIT : PGCIL will supply & install the earthing materials like Earth risers, Electrode, Clamps/ Connectors, GI strip/ flats, chamber cover, nut/ bolts and washers , test link as the same is not asked by PGCIL in Bid Price Schedule and scope of work. The design calculations will also be performed by PGCIL based on Earth Resistivity report. | Confirmed
7 | Technical Specification - Sub-station Automation System Rev 04A |  | No. of MUs shall be such that failure of any one Merging unit shall not cause failure of a protection function in both Main-I and Main-II protection systems. | To meet this requirement , Generally in Normal condition: Main-1 IED shall be subscribed with SV values published by MU-1 and MU-2. The same logic for main-2 IED will be followed. In such condition, MU-1 failed to publish SV then Main-I IED will detect the loss of SV and will switch-over to take reference of MU-2 SV which is already subscribed in Main-1 IED. The same logic will be followed in Main-2 IED. With the above, technical specification requirement will be achieved. Please accept. | Failure of single MU shall not cause failure of protection function in both Main I and Main II Protection relays. Change over to SV Stream from another MU is not envisaged..
8 | Technical Specification - Sub-station Automation System Rev 04A |  | IED devices should have the capability to be time synchronized via IEEE 1588v2 (Precision Time Protocol – PTP). No separate cable is envisaged for time synchronization purpose. Ethernet based Data Network which will be used for SMV transmission shall also be used for time synchronization purpose. | As understood that IED and Mus are time synchronized via PTP protcol. SNMP, SNTP, PPS protcols are not allowed for time synchronization. Please confirm our understanding is correct. | IEDs in process bus shall be necessarily synchronised with PTP. Devices in station bus may be synchronised with PTP/SNTP as per TS.
9 | Technical Specification - Sub-station Automation System Rev 04A |  | Approved Make of Ethernet Switches for Process Bus Substation. | For Process Bus application, Approved make of Network switch is only Ruggeddcom / Belden. Please confirm. | Bidder to quote as per bidding document.
10 | Technical Specification - Control and Relay Panel Rev 09A |  |  | Considering the criticality of the LBB function, we propose implementing the LBB protection as an inbuilt feature within the Main‑I and Main‑II merging units (MUs) along with back up o/c and E/f feature , rather than using a standalone LBB relay dependent on sampled value subscription. Under all conditions, both merging units will have hardwired CT inputs and operate independently, if required the same LBB function will be enabled in main protection relay as a back up. Kindly accept the proposal. | Bidder to quote as per bidding document.
11 | Section Project Scope of work | 2 Scope of work | Storage and erection | Space available inside the control room can be utilized for storing the control and relay panel . Please confirm. We request PGCIL to consider erection in their scope of work . | Bidder to quote as pe bidding document. Kindly refer to CL.9. 12 and 13 of Revised Section project Rev 01 for provision of storage
12 | Section Project Scope of work | c. MODIFICATION OF EXISTING CRP: | i) Dismantling of the existing energy meter | We request PGCIL to consider the dismantling and mounting of the energy meter in their scope.The compatibility to use the TVM device in the existing out door environment to be ensured by PGCIL. | Bidder to quote as per bidding document.
13 | Section Project Scope of work | c. MODIFICATION OF EXISTING CRP: | ii) Shifting of existing CSD Device | As CSD is a breaker device we request PGCIL to make necessary modification /Changes done directly by the respective breaker manufacturer . The compatibility to use the CSD device in the existing out door environment to be ensured by PGCIL. | Bidder to quote as per bidding document.
14 | Section Project Scope of work | c. MODIFICATION OF EXISTING CRP: | iii) PMU modification | Hope CT and PT to be connected to the PMU device from the switchyard , whether the existing cable to be retained for this scope , else new cable to be laid . | New Cable shall be provided for CT & PT of PMU device. Cable for BI/BO also required.
15 | Section Project Scope of work |  |  | Our understanding is that scope related to Dismantle of old Panels shall be in the scope of PGCIL. Kindly confirm. | Dismantling of existing panel is not envisaged under present scope
16 | Section Project Scope of work |  | Existing Cable remove scope clarity | We understand that “ dismantling of old cable will be done by PGCIL” and the same will be done bay wise after commissioning by Power Grid Plz confirm. Bidder scope shall only be related to FO cable will be laid over and above the existing control cable . Please confirm. | Dismantling of old cables is not envisaged under present scope. The supply, laying & termination of new control, power & FO cable (and special cables, if any) applicable under the scope of work shall be covered under the bidder's scope of work.
17 | Section Project Scope of work |  | Storage and erection | Space available inside the control room can be utilized for storing the control and relay panel – plz confirm . | Bidder to quote as pe bidding document. Kindly refer to CL.7) 12 and 13 of Section project for provision of storage
18 | Section Project Scope of work |  |  | Since bay wise commissioning will be performed , we request PGCIL to consider per man-days commissioning charge in the price schedule which will be beneficial to both GE as well as to Power Grid. | Bidder to quote as per bidding document.
19 | Section Project Scope of work |  | Missing FO cable quantity | Request Powergrid to share the quantity of FO cable in line with as shared for power cable. | Cost of FO cable is deemed to be included in overall SAS cost of the respective substation
20 | Section Project Scope of work |  | Material Delivery/Shut Down | 1. Please confirm whether shutdown will be provided in one go or it will be in scattered manner ( DIA wise ) . if it is in scattered manner please share the detailed shutdown plan / priority bays planning. 2. Please also confirm whether Shutdown/shutdowns shall be on fixed particular dates for or It will be on basis of rediness of materials & site activity in line with L-2. 3. Inline to the above mentioned points , whether panels can be delivered in multiple lots else we need to deliver in a single lot. | 1. Shutdown of elements shall be provided on availability basis. The shutdown plan shall be provided during the execution stage 2. Shall be confirmed during execution stage. 3. Provisions of Bidding Documents shall prevail.
21 | Section Project Scope of work | General | EHS | Cables in the trench have to be laid on live cables. Thus, person has to go inside the trench for laying some cables. Kindly confirm PGCIL will give Shutdown while laying the cables or some other safety measures have to be implemented for the same. Accrdingly you are requested to change the Terminology in the tender documents and Price schedules | Bidder to quote as per bidding document
22 | Price Schedule | General -Meerut station & Mandola | BOQ, Capex, O&M | Price Schedule has been segragated as BOQ , CAPEX and O&M , on what basic it has been segragated clarity required . | Bidder to quote as per bidding document
23 | Section Project Scope of work | ` | No variation shall be admissible on account of Installation of Cables/supply and installation of associated accessories, irrespective of variation (either positive or negative) in supply quantity of Cable specified in BPS | We request PGCIL to reconsider this clause and to do necessary claim if in case additional cable required during comissioning. | Bidder to quote as per bidding document
24 | Section Project Scope of work | SPECIFIC EXCLUSIONS | Civil work | Hope necessary floor cutting to place the new panels in the existing control room will be arranged by PGCIL . | Bidder understanding is in order
25 | Section Project Scope of work | SPECIFIC EXCLUSIONS | Civil work | Hope minor civil work if requried in the control room once after panel errection to be performed by PGCIL . | Bidder to quote as per bidding document
26 | Section Project Scope of work |  | Scope of work | Whether we need to remove all the existing panels else only few panels will be removed to accommodate our present scope , in that case covering of floor with tiles may not be required. | Dismantling of existing panels are not included in the scope of work.
27 | Section Project Scope of work |  | Scope of work | It is understood that “ dismantling of cable will be done by PGCIL” and the same will be done bay wise after commissioning by Power Grid -Plz confirm | Any dismantling of Control & POWER cable is not envisaged under present scope. However necessary removal & installation of cables from Primary equipment as envisaged under present scope is in bidder's scope.
28 | General | General | Medical resources availability during deputation of commissioning engineers | As all these Sites are PGCIL owned, we request PGCIL to make its Site medical facilities and resources available to Seller personnel who need medical attention. | Bidder to quote as per bidding document.
29 | General | General | Hazardous Materials | If GE encounters Hazardous Materials in PGCIL’s equipment or at the Site that require special handling or disposal, GE is not obligated to continue work affected by the hazardous conditions. In such an event, PGCIL shall eliminate the hazardous conditions in accordance with applicable laws and regulations so that GE’s work under the Contract may safely proceed, and GE shall be entitled to an equitable adjustment of the price and schedule to compensate for any increase in GE’s cost of, or time required for, performance of any part of the work. PGCIL shall properly store, transport and dispose of all Hazardous Materials introduced, produced or generated in the course of GE’s work at the Site. | Bidder to quote as per bidding document.
30 | General | General | Supplier/contractor rights to stop work is missing | Supplier/contractor may suspend performance or evacuate its personnel, at any time, without liability, if it reasonably believes its personnel are at risk. Supplier/contractor shall not be responsible to dispose of any toxic substances, hazardous substances, batteries or hazardous waste encountered at site unless produced or brought on site by Supplier/contractor it self during the performance of the PO. | Bidder to quote as per bidding document.
31 | Section Project Scope of work | General | EHS | As per our Global directive, we need the distance of the nearest speciality/super speciality hospitals from the site location where the GE engineers shall be working under the present scope of contract. Kindly provide the same. | Please refer clause 1.5 of Section project wherein it is mentioned that “The bidders are advised to visit the substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy prior to bid.”
32 | Section Project Scope of work | General | EHS | 1) Please confirm that first aid facility & ambulance is available at site and in case of emergency same shall be available for bidder representative working at site. 2) Please confirm that details of hospital available near site. | Bidder to quote as per bidding document.
33 | Section Project Scope of work |  | Scope of work | Since bay wise commissioning will be performed , in that case per man-days commissioning charge will be quoted which will be beneficial to both Bidder as well as to Power Grid. | Bidder to quote as per bidding document
34 | Section Project Scope of work |  | Scope of work | After digital s/s, there will be 2 SAS systems. As per PGCIL site / Engg, 2 SAS solution need to implemented. As there is NO interface between 2 systems control uniqueness can not be maintaned however as confirmed by the PGCIL site engineer it will be handled via operation SOP. Reporting to NTAMC & RLDC will be done separately . | Co-ordination between different SAS such that only one equipment is operated at a time shall be finalised during detailed engineering
35 | Section Project Scope of work |  | Scope of work | it is understood from the survey that NO space available in the existing Cable trays in control room area, this has to be handled by providing additional supports hope it is under PGCIL scope . | Laying of cable i.e. in existing trench or new trench etc shall be finalised during detailed engineering.
36 | Section Project Scope of work |  | Scope of work | Hope only the shifting of the meters from the existign panel to the newely supplied MU Panel will be in bidder's cope , and ncessary online integration and sending date to the remote RLDC will be in PGCIL scope, please confirm . | After shifting of the meters, restoration of original connection for data transfer is included under present scope.
37 | Section Project Scope of work |  | Scope of work | Auxiliary system is excluded in the scope, but as per site requirement it may be required , hence request PGCIL to take care if requried at the later stage . | Bidder to quote as per bidding document
38 | Section Project Scope of work |  | Scope of work | For mandola station : Bus & Line Seiries Reactors have GIS modules. Hope the existing LCC bays will be dismantled and control will be from the newwely supplied BCU , please confirm . | Mandola SS is not covered under subject scope of work.
39 | General |  | Yard Space for SGMU Panels | It is understood that SGMU/SGCMU panels shall be installed in the switchyard near respective bays. Kindly confirm that identified locations, foundations, mounting structures, and accessibility for these panels shall be provided by the Owner. Any civil works such as foundation construction, trench extension, or structural modifications, if required, shall be under Owner’s scope unless specifically defined in BOQ. | Confirmed
40 | General |  | Cable Trenches / Cable Vault Availability | Kindly confirm that adequate space in existing cable trenches/cable vaults shall be available for routing of new control, power and communication cables under the present scope. In case of inadequate space, congestion, or requirement of new trench/cable vault construction/modification, the same shall be in Owner’s scope. | Confirmed
41 | General |  | Cable Routing & Crossing | Please confirm that all cable routing paths from switchyard to control room and between bays are accessible and available without major civil constraints. Any requirement of: Road cutting Trench crossing HDD / ducting RCC trench modification Shall be considered under Owner’s scope unless explicitly mentioned. | Confirmed
42 | General |  | Cable Entry & Termination Provisions | Kindly confirm that sufficient cable entry provisions (openings) are available in existing panels, junction boxes and control room entry points. Any modification required in existing panels/buildings for cable entry shall be in Owner’s scope. | Provisions of Bidding Documents shall prevail.
43 | General |  | DC System Availability | Kindly confirm availability of adequate spare feeders and capacity in existing DCDB for feeding new Control, Protection, SAS and SGMU panels. In case augmentation is required, the same shall be under Owner’s scope . | Confirmed
44 | General |  | Cable trenches occupied full/partial | It is observed that the existing cable trays for OFC routing paths, trays, and ducts are largely occupied/full. Any requirement of additional cable tray, supports, new trench/duct/tray installation, o rmodifications for routing of new OFC cables shall be in PGCIL's scope. | Confirmed
45 | General |  | Cable removal | Kindly clarify the scope regarding existing contol/power cables whether existing cables shall be removed by PGCIL or new cables shall laid over/alongside existing cables. In case removal is required, the same is excluded from GEV's scope. | New cable shall be laid over/along side of existing cable. Dismantling of existing cable is not envisaged under present scope.
46 | General |  | Panel configuration | Kindly clarify the panel configuration requirment per bay under present scope. It is proposed to accommodate Main 1, Main 2 & BCU in a single panel per bay (separate panel for Tie bays). Please confirm if this arrangement is acceptable, or if separate panels are required for Main-1 and Main-2 protections. | No. of Panels may be optimized for Process Bus based substations. However, IEDs of different feeders shall not be placed in the same panel
47 | General |  | Panel dimension | Kindly specify if thers is any restriction on height/dimension for SGCMU panels to be installed in the switchyard. Also confirm any requirements related to Mounting/Foundation height, clearances from primary equipment. | Height of the panel shall meet the minimum phase to earth clearance from the charged objects. Outdoor Panels shall be erected such that a minimum height of 1000mm is maintained between FGL & bottom of the Panel.
48 | General |  | Water logging/drainage issue | Any requirement for drainage improvement due to water logging shall be under PGCIL scope. | Confirmed
49 | General |  | Panel removal | It is understood that removal/dismantling of existing CRP shall be carried out by the PGCIL. Kindly confirm that dismantling, shifting and transporation if removed panels shall be under PGCIL scope. | Confirmed
50 | General |  | PMU panel | As per understanding, the existing PMU panels shall be retained under present scope. Only modification of wiring is envisaged. No replacement or re laying of existing cables connected to panels required.Hope our understanding is correct . | Bidder understanding is in order. However new CT and PT cable and cable for BI/BO need to be layed from Switchyard to PMU panel
51 | General |  | LCC panel clarification | Some bays are GIS type. Kindly clarify the scope regarding existing LCC panels. Whether LCC panels are to be retained as is or dismantaled and removed. If retained, kindly clarify interface requirements with new SAS/SGCMU system. | Existing LCC panels shall be retained. Interface requirements shall be finalised during detailed engineering
52 | General |  | Additional bays at Ballabgarh | It is observed that 2 Nos. of additional bays at ballabgarh substation have been recently commissioned, which are not covered in the BOQ. The scope of work is limited to the bays defined in BOQ, and these additional bays are excluded from present scope. | Bidder to quote as per bidding document.
53 | General |  | Islanding panel at Mandola | It is observed that an Island panel at Mandola Substation is presently not in operation and is not included in the BOQ. The scope of work is limited to the bays defined in BOQ, and these additional bays are excluded from present scope. | Mandola SS is not covered under subject scope of work.
54 | Section Project Scope of work | General | Scope of work | We understand that BUS VT analog PT inputs can be taken in any one of the Bay merging units and a dedicated Merging Unit is not needed for gathering the BUS VT input | Confirmed
55 | Section Project Scope of work | General | Scope of work | intertripping between different voltage levels (400KV and 220KV) will be hardwired. Please confirm the same. | Bidder to quote as per bidding document
56 | Section Project Scope of work | General | Scope of work | We understand that Supply of RTCC relay/Panel is not in present scope. Kindly Confirm | Supply of RTCC panels is not in the scope of work. However, Two Nos. of Redbox shall be provided for integrating Transformer and Reactor Monitoring equipment and digital RTCC relays with station bus. Integration of existing IEC 61850 compliant Transformer and Reactor Monitoring equipment (like DGA, ODS, FOTS etc.) and Digital RTCC relays with New SAS shall be covered under scope of work. Kindly refer to Cl. 2.1.1 (a) & 2..1.2 (a) of Section project
57 | Section Project Scope of work | General | Scope of work | We understand that all the analog and digital inputs from Bushing CVTs/CTs and LA will be brought to the MU cum SCU Main-1 and Main-2. No separate MU or and SCU will be placed near the CVT or an LA. Kindly confirm. | Bidder to quote as per bidding document
58 | Section Project Scope of work | General | Scope of work | We understand that all the field signals shall be redundant and will be wired to both MU cum SCU Main-1 and main-2. In case some signals are intended to be redundant and some non-redundant then please share their quantity for each typical. | Field signals shall be wired to both SGC /MU I and II (as per TS) .Signal list shall be finalised during detailed engineering.
59 | Section Project Scope of work | General | Scope of work | We understand that no contactor/CMR shall be provided for routing a field signal to 2x SGC cum MU. 2 separate contacts shall be provided for all the signals from the respective equipment junction/marshalling box. Kindly confirm. | Wiring to SGC MU shall be finalised during detailed engineering
60 | Section Project Scope of work | General | Scope of work | It is understood that Main-1 and Main-2 protection IEDs for transformer and reactor protection can be of same make with different hardware platform. Kindly confirm | For Transformer and reactor protection, the IEDs can be of same make and Platform
61 | Section Project Scope of work | General | Scope of work | Kinldy confirm whether we can propose HDPE pipe for FO cable , kindly confirm . | Bidder to quote as per bidding document
62 | Section Project Scope of work | General | Scope of work | We understand that during shifting/commissioning of any existing equipment/system that fails during establishing the communication, Bidder shall not be held responsible for the said failure and replacement of the faulty system/devices of the existing system shall be in the scope of Employer. Kindly confirm | Bidder’s understanding is correct.
63 | Section Project Scope of work | General | Scope of work | For Ballabhgarh - line differential relay to be supplied at the remote end and necessary SAS integration to be performed , please note the existing SAS at the remote end is NR Electric and presently they have limited their operation in India , hence request PGCIL to reconsider this integration scope, better to consider this in PGCIL scope . | Bidder to quote as per bidding document
64 | Section Project Scope of work | General | Scope of work | It is understood that all new panels shall be installed in existing control room building in Hissar station . Kindly confirm the adequate space, floor loading capacity, panel mouting arrangements, cable entry provisions (Floor/Trench/top) shall be made available by PGCIL | Confirmed
65 | Section Project Scope of work | General | Scope of work | It is understood that 2 Nos. of bays at Hisar Substation are planned for commissioning shortly and are not included in the BOQ. The scope of work is limited to the bays defined in BOQ, and these additional bays are excluded from present scope. | Bidder to quote as per bidding document.
66 | Section Project Scope of work | Specific Exclusion | Cable Sealing is missing in specific Exclusion of Mandola substation | Kindly add the same in the Mandola substation as well. | Mandola SS is not covered under subject scope of work.
67 | Section Project Scope of work |  | Integration of existing Auxiliary BCU in new SAS in both Hisar and ballabhgarh | Please share the make and complete model of existing Auxliary BCU. | Details of Auxiliary BCU at Ballabhgarh S/s & Hissar S/s Make: ALSTOM, Model : C264
68 | Section Project Scope of work Annexure-IV | 2.2.2.f | As details Provided in Annexure-IV, Protection couplers for some of the bays under present scope are existing. Same may be integrated with new protection panels being supplied under present scope as per requirement of the scheme. Cost of the same shall be deemed to be included in the cost of the CRP panels. As per Annexure IV S.No. Details of existing DTPC (Make & Bay No.) to be integrated in process bus scheme Ballabgarh- a) 1 Nos, Hitach NSD 70 towards Agra b) 2 Nos, Hitach NSD 70 towards Tughlakabad-1&2 c) Existing PLCC shall be used towards Maharani Bagh d) 6 Nos. Valiant Make towards Kanpur-1,2, 3 (2 nos, in each line) Hissar- 6 Nos. Alstom DIP towards Bhiwani-1,2 &3 and Moga-1,2&3 (1 channel each) Existing PLCC shall be used for other lines. | 1. As per details of existing DTPC's, PLCC provided for integration we understand existing DTPC (Hitachi NSD 70, Valiant Make & Alstom DIP) towards Agra, Tughlakabad-1&2, Kanpur-1,2,3 , Bhiwani-1,2,3 and Moga-1,2&3 are non IEC61850 Complaint & hence same cannot be integrated with new IEC 61850 Process bus based CRP system. 2. Please provide details of existing PLCC's with make & Model a) at Ballabgarh towards Maharani Bagh. Why existing PLCC details are provided under existing DTPC's to be intergarted in new process bus based CRP system, whether existing PLCC's are to be replaces with new DPC. b) at Hissar S/S towards other lines (other than Bhiwani-1,2,3 and Moga-1,2&3) PLCC being non IEC61850 compliant these PLCC's are not possible to be integrate with new IEC 61850 Process bus based CRP system. 3. Please confirm that these existing PLCC's Analog Protection Couplers & DTPC's on above lines will be interfaced with new CRP panel after removing from existing CR Panel through available control cable. KIndly confirm that existing PLCC & DTPC's are not be interfaced with new process bus based scheme. Also confirm that existing DPC's are already integrated with available FOTE system Also re-configuration of existing PLCC's & DTPC's (if required) will be arranged by Purchaser. Please confirm | 1. Non-compliant existing DTPCs / PLCCs to be integrated with New CRP system through Hard wiring 2 & 3: Detail of existing PLCC (make & model) shall be provided during detailed engineering. Retrofitting of existing PLCC (given in Sr No-3 of Annexure-IV of Section-Project) with new DTPC is not considered. Same to be integrated with New CRP system through Hard wiring. Re-configuration in FOTE is not in the scope of bidder
69 | Section Project Scope of work Annexure-IV | 2.2.2.f | As details Provided in Annexure-04, In bays where new digital protection coupler is envisaged as per BPS, Supply, installation, testing and commissioning of the Digital Protection Couplers (DPCs) shall be covered under present scope. The DPC shall be integrated with process bus through IEC 61850 GOOSE Messages. The new DPCs may be kept in CRP panels of the respective line or associated Tie bay being supplied under present scope. The GOOSE publish and subscribe capabilities of the DPCs shall be similar to those of other protection and control IEDs. Integration of the new DPC with the existing communication channel is also included under present scope. All converters required to interface DPC with existing channel shall also pe part of DPC. As per Annexure IV Number of DTPC channel with corresponding transmission line directions are provided as follows: Ballabgarh S/S - 22 Nos. (11 Ballabgarh, 11-REmote ENds (Both channels of Mainpuri-1&2, Gurgaon, Dadri, Nawada and one channel of Agra-1)) Hissar S/S- 16 (08- Hissar, 08-Remote End (Both channels of Bhiwadi-1, Fatehabad, Moga-1, BBMB Bhiwani) | 1. Specification of IEC61850 based DTPC's are not provided alongwith Tender documents. Please provide TS for offering compliant DTPC's (viz. number of ethernet port, communication interfaces, PTP/SNTP synchronisation, number of commands, Power supply, IEC61850 Edition etc...) 2. Connectivity with S/S IEC 61850 SAS based Ring switch will be on Electrical Interface or Optical Interface (Multimode 1310nm). Port availability in switch to be ensured. 3. Please confirm for remote end s/s scope of Ballabgarh S/S (Both channels of Mainpuri-1&2, Gurgaon, Dadri, Nawada and one channel of Agra-1)) & Hissar S/S- (Both channels of Bhiwadi-1, Fatehabad, Moga-1, BBMB Bhiwani). for IEC61850 Goose interfacing on existing CR panel. 4. Please confirm following: a. We understand new DTPC's will be integrated with process/station bus through IEC61850 Goose Messages.No Hard wiring/Interfacing of new IEC 61850 process bus based CR Panel with proposed new DPC through control cable required to be done only interfacing through goose messaging will be required. b. Purchase will arrange for SCD/ICD files for interfacing DPC with existing IEC 61850 IED's/relays. c. These DPC's are proposed to be installed in new CR Panels.In case of existing CR panels/PLCC/FOTE panels same shall be installed in existing panels. No new panel to be proposed for new DPC's. d. Proposed DPC's will be integrated with existing FOTE system through E1 interface. Configuration of E1 channel for interfacing DPC with existing SDH will be in scope of purchaser. | 1. Bidder to offer Digital Tele-Protection coupler as per Technical Specification of DTPC provided in Bidding Documents (Ref Annexure-S8 of Specific Req. rev 10) Moreover, the offered product should be suitable for integration in IEC61850 based Process bus system 2. Bidder to quote as per Bidding documents 3. For remote end, new DTPC is to be integrated with existing CRP through Hard wiring 4. (a) Confirmed. However the Power supply to new DTPC as per Bidding documents shall be ensured by the bidder. (b) Bidder scope includes all the works associated for interfacing DPC with existing IEC 61850 IED's/relays. (c) Bidder understanding is generally in order. (d) Confirmed
70 | Section Project Scope of work Annexure-IV | 4. Details of existing PMU (Make & Bay No) to be integrated in Process Bus Based. | Existing PMU MICOM P847 to be integrated in Process bus scheme | Existing PMU MICOM P847 is old supplied relay which is not Process bus compliant. Please clarify the detailed scope of work which is PGCIL is expecting to do in case existing relays are not integrated in Process bus scheme. | Please refer 2.2.1 c (iii) & 2.2.2 c (iii) wherein it is mentioned that “For bays under present scope, PMU IEDs are already existing in a separate panel. Refer Annexure IV for Existing PMU details. Required modification in wiring of analog and digital signals to existing PMU is included under present scope.”
71 | 1.0 Section_Project_RCP-01 | 2.1.1. a 2.1.2. a | Integration of existing Station Auxiliary BCU to new SAS is also under present scope. | We understand that existing Aux. BCU is communicable & IEC 61850 compliant with FO ports. Kindly confirm. | Bidder to quote as per bidding documents.
72 | 1.0 Section_Project_RCP-01 | 2.1.1. b Pg. No. 8/15 | Supply, erection, testing, commissioning, and integration with SAS (M/s NR Electric make) is included. | We understand that existing panel is having sufficient space to mount the line differential relay and accessories. Kindly confirm. | Confirmed
73 | 1.0 Section_Project_RCP-01 | 2.1.1. b Pg. No. 8/15 | Supply, erection, testing, commissioning, and integration with SAS (M/s NR Electric make) is included. | We understand that existing NR Electric make SAS is suitable to cater present supplied Line differential relays without any upgradation of hardware & software. Any upgradation work in existing SAS is excluded from the bidder's scope. Kindly confirm. | Bidder scope is limited to the integration with existing SAS (M/s NR Electric make). However any upgradation work in the existing NR electric SAS is not envisaged in the scope of work.
74 | 1.0 Section_Project_RCP-01 | 2.1.1.c.i Pg. No. 5/15 2.1.2.c.i Pg. No. 9/15 | Shifting of all existing Energy Meters to the SGMU Panels in the switchyard. | Any integration/caliberation of Energy meter is excluded from bidder's scope. Kindly Confirm. Also, Request you to kindly provide Dimension details of existing meter. | Shifting and reinstallation of Energy meter is in present scope. Required details shall be provided during detailed Engineering.
75 | 1.0 Section_Project_RCP-01 | 2.1.1.c.iii Pg. No. 5/15 2.1.2.c.iii Pg. No. 9/15 | For bays under present scope, PMU IEDs are already existing in a separate panel. Refer Annexure IV for Existing PMU details. Required modification in wiring of analog and digital signals to existing PMU is included under present scope. | Our scope is limite to wiring modification (wiring of analog & digital signals) only. Any configuration, integration is not in bidder's scope. | Bidder understanding is generally in order.
76 | 1.0 Section_Project_RCP-01 |  | DPC/PLCC | We understand that CRP, DPC and FOTE(SDH) cabinets will be placed in control room at SS hence E1 to FO converters are not necessary. However, we do not have information of the REMOTE stations. Are any of the remote stations kiosk based stations? If yes, provide details of such (kiosk based) substations and tentative distances between Kiosks and control room so that length of FO cable and no. of E1/FO converters can be considered. | As per clause 1.5 of Section Projects, bidders are advised to visit the substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy prior to bid.
77 | 1.0 Section_Project_RCP-01 | 2.1.4 Pg. No. 10/15 | All materials required for the Civil and construction/installation work shall be supplied by the Contractor. The cement and steel shall also be supplied by the Contractor. | We understand that any civil (minor/major) work is not in bidder's scope. Hence, Mentioned clause "SECTION PROJECT Clause 3.3 and Provided document "5_Civil Works Rev 11A" is not applicable for this tender. Kindly confirm. Also, we understand that Foundation shall be constructed by PGCIL/Employer for mounting CT-CVT MB/SGC cum MU Panels and CRP/SAS (if required). Kindly Confirm. | Confirmed
78 | 1.0 Section_Project_RCP-01 | 2.1.6 Pg. No. 11/15 | Training of Employer's manpower | There is no line item in Customer's price schedule regarding Traings. Hence, we have not consider any training in our scope. | Bidder to quote as per bidding document
79 | 1.0 Section_Project_RCP-01 | 7.2 Pg. No. 13/15 | Before commencing the replacement of the existing system, the new IEC 61850 Process Bus based Control & Protection system shall be installed and commissioned in the available space of control room along with all Process Level IEDs and will be subjected to testing, validation & verification. Once the overall system is found to be satisfactory, the replacement process shall be started. | We understand that new building for Control room (Ballabhgarh) is to be constructed by PGCIL. Any dismantling/shifting of existing panels to new Building shall be in PGCIL scope. Kindly confirm. | Bidder understanding is in order
80 | 5.0 Section CRP rev. 09A | 20.5 21.9 |  | It is understood that Main-1 and Main-2 protection IEDs for transformer and reactor protection can be of same make and on same platform. Kindly confirm. | Confirmed
81 | 5.0 Section CRP rev. 09A | 28.17 | Each Fault recorder shall have its own time generator and the clock of the time generator shall be such that the drift is limited to +0.5 seconds/day, if allowed to run without synchronisation. Further, Fault recorder shall have facility to synchronise its time generator from Time Synchronisation Equipment having output of following types: • Voltage signal: (0-5V continuously settable, with 50m Sec. minimum pulse duration) • Potential free contact (Minimum pulse duration of 50 m Sec.) • IRIG-B • RS232C • SNTP • IEEE 1588 PTP | We understand that, since separate Disturbace recorder is not applicable for 400kV & 220kV Line bays. Hence, mentioned clasu and item is not applicable for this tender. Kindly confirm. | Confirmed, However inbuilt fault recorder shall be provided in Main-I & Main-II IEDs.
82 | 6.0 Section-Sub-station Automation_Rev04A | 4.1.6 Pg. No. 17/40 | Firewall and Router | Kindly confirm which spec to be followed for Firewall: "6.0 Section-Sub-station Automation_Rev04A clause 4.1.6" Or Annexure_SAS_X: NextGen Firewall | Please Refer Amendment-1
83 | 6.0 Section-Sub-station Automation_Rev04A | 2.2 Pg. No. 37/40 | The fibre optic cables shall be run in G. I. conduit pipes. | We understand that instead of GI pipe, we can propose HDPE pipe for FO cable run. Kindly accept. | Bidder may quote as per provision of biding documents
84 | 6.0 Section-Sub-station Automation_Rev04A | 18.0 Pg. No. 37/40 | Additional station level equipment (for sub-station where new SAS is envisaged) i) Jump Server as per Annexure SAS_XIII ii) NTAMC remote console as per Annexure_SAS XIV | We understand that mentioned clause is not applicable for this process bus project. Kindly confirm. | Jump server and NTAMC remote console is included under present scope
85 | Annexure-V | 1 | CSD | Kindly provide the make/Model of existing CSD. | Required details shall be provided during detailed engineering
86 | Annexure-V | 1 | CSD | Kindly confirm the existing CSDs are communicable. Lso confirm the compliant protocol and communication ports. | Required details shall be provided during detailed engineering
87 | Annexure-V | 1 | CSD | We understand that Supply of CSD is not in present scope. Kindly Confirm. | Confirmed
88 | Annexure-V | 2 | Details of New DTPC required as per BPS to be integrated in Process Bus Based Scheme. Ballabgarh: 22 Nos. (11 – Ballabgarh, 11– Remote end) Hissar: 16 Nos. (08 – Hissar, 08 – remote end) | As per the section project new supplied DPC shall be mounted in CRP. Kindly confirm whether new panel shall be supplied for remote end DPC or same will be retrofitted in existing CRP. | For remote end, new DTPC can be mounted in existing PLCC/DTPC Panels and to be integrated with existing CRP through Hard wiring
89 | Price schedule for Ballabhgarh & Hissar | Sch-1 | Time Synchronization Equipment | Kindly clarify the mentioned 5 nos. qty. We understand that total 2 nos. GPS will be sufficient for the complete substation. | Bidder to quote as per BPS
90 | Price schedule for Ballabhgarh & Hissar | Sch-1 | 400 KV SGC/MU PANELS | As there is clearly defined SGC/MU panels for the bays. Hence, we understand that BUS VT analog PT inputs can be taken in any one of the Bay merging units and a dedicated Merging Unit is not needed for gathering the BUS VT inputs. | Confirmed
91 |  | Scope |  | We understand that Supply of RTCC relay/Panel is not in present scope. Kindly Confirm. | Confirmed
92 |  | General |  | Intertripping between different voltage levels (400KV and 220KV) will be hardwired. Please confirm the same. | Bidder to quote as per provision of bidding documents
93 |  | General |  | We understand that all the field signals shall be redundant and will be wired to both MU cum SCU Main-1 and main-2. In case some signals are intended to be redundant and some non-redundant then please share their quantity for each typical. | Bidder to quote as per provision of bidding documents
94 |  | General |  | We understand that no contactor/CMR shall be provided for routing a field signal to 2x SGC cum MU. 2 separate contacts shall be provided for all the signals from the respective equipment junction/marshalling box. Kindly confirm. | Bidder to quote as per provision of bidding documents
95 |  | General |  | We understand that there are no spare ICT or Rectors in any of the voltage level. Hence CT switching shall not be applicable at any voltage level. Kindly confirm. | Confirmed
96 | General | Storage |  | Kindly confirm the availability of Closed Storage for Panels and other equipments. | Bidder to quote as per provision of bidding documents
97 | General | Order of precedence |  | We understand in case of any ambiguity between requirement of price schedule and requirement stated elsewhere in any other tender document including section project, the requirement of price schedule shall prevail. Please confirm our understanding. | Please refer FAQ sl no A.1.1i n specific requirement (Annexure III) of section project
98 | General | General |  | We understand that during shifting/commissioning of any existing equipment/system that fails during establishing the communication, Bidder shall not be held responsible for the said failure and replacement of the faulty system/devices of the existing system shall be in the scope of Employer. Kindly confirm. | Confirmed
99 | General | General |  | During shifting & Integration job, any equipment/system that shall be required to be Re-integrated into SAS/system and the same if in Warranty, Employer shall employ the respective OEM as required during successful commissioning of the same. | Bidder to quote as per provisions of bidding documents
100 | General | General |  | We understand that any dismantling of existing Panels, removing of existing cables are excluded from bidder's scope as same is not mentioned in SECTION PROJECT. Kindly confirm. | Please refer reply to similar query above
101 | Price Schedule | Cable | 1.1kV grade Power Cables (PVCinsulated)along withlugs,glands,straight joints &accessories,etc. | Request you to kindly provide following data :- 1. Existing Cable Schedule. 2. Cable Routing 3. Substation layout 4. Earthing cable requirement 7. Quantity and type of cable if any other cable to be supplied. | Required details shall be provided during detailed engineering
102 | Price Schedule | Cable | Cable BOQ | If Cable length increase shall have additional cost and time impact. Kindly confirm the unit Quoted Pirces or revised pirces applicable. | Bidder may quote as per provision of bidding documents.
103 | BOQ | "Power and Control Cables" |  | BOQ mentions Quantities of power and control cables. Do these quantitites included the power/control cable requirement for the remote end DPC's also. Kindly confirm. | Bidder to quote as per bidding document
104 | Sw. yard plan and section details |  |  | Kindly share the complete layout for respective substation | Required details shall be provided during detailed engineering. However, Bidder is requested to visit site as per Cl. 1.5 of section project
105 | Section Project | clause no. 1.4 | Additional item if any | Understand that the present scope is BOQ based. Kindly mention the additional item (if any) which are not covered in BOQ. | Bidder to quote as per bidding document
106 | Existing make |  |  | Kindly share the existing make of Circuit Breaker and CSD. | Required details shall be provided during detailed engineering
107 | Price Schedule |  | FO cables and other item | There is good quantity of FO cable, Pipes and accessoies are not appearing the BOQ. Request you to mention the required item in the BOQ | Cost of FO, PVC pipes, GI pipes etc. are deemed to included in SAS cost
108 | General : FO cable | General | Laying of FO cables | Understand that separate pipes are not required for armoured FO cable | Bidder to quote as per provision of bidding documents.
109 | General : Scope | General | Testing of existing equipment | We understand that testing of existing equipment are not in present scope | Confirmed
110 | General : FO cable laying method | General | Laying method of FO cable | Understand that main and reurndent FO cable shall be laid in same pipe (if pipe is required) | Main and redundant FO cable shall be laid in different G I conduit pipes.
111 | Appendix – 2 |  | Price adjustment | We understand that Price adjustment is applicable for LV Cable and Installation works without any caping | Bidder to quote as per provision of bidding documents.
112 | Retrofit of control and protection system RCP-01 Technical Specification, Section – Project |  | f. TELE PROTECTION EQUIPMENT: As details Provided in Annexure-04, Protection couplers for some of the bays under present scope are existing. Same may be integrated with new protection panels being supplied under present scope as per requirement of the scheme. Cost of the same shall be deemed to be included in the cost of the CRP panels. As details Provided in Annexure-IV, In bays where new digital protection coupler is envisaged as per BPS, Supply, installation, testing and commissioning of the Digital Protection Couplers (DPCs) shall be covered under present scope. The DPC shall be integrated with process bus through IEC 61850 GOOSE Messages. The new DPCs may be kept in CRP panels of the respective line or associated Tie bays being supplied under present scope. The GOOSE publish and subscribe capabilities of the DPCs shall be similar to those of other protection and control IEDs. Integration of the new DPC with the existing communication channel is also included under present scope. All converters required to interface DPC with existing channel shall also pe part of DPC. | a. kindly clarify new DPC required with Goose interface or Contact transfer based interface, also confirm remote end relay also is with Goose interface. b. request you to kindly any type of work in existing system, since it is from different OEM and support also may not be available. | a Please refer reply to similar query above b. Bidder to quote as per provision of bidding documents
113 | Annexure-II Spare list |  |  | DPC spare is not mentioned, please add in price schedule If required | Bidder to quote as per provision of BPS
114 | Annexure_III SPECIFIC REQUIREMENT’S (Section- Project) C/ENGG/SPEC/SEC-PROJECT/SPECIFIC REQUIREMENT REV NO 10 |  | The DPC can be housed either in offered Control & Protection Panel / PLCC Panel or in separate panel. Generally SDH Equipment are placed in communication room of Control room where as DPC is placed in panel room. The connection between SDH equipment and each DPC shall be through Optical fiber. Necessary cables, converter(s) for converting E1 signal to optical fiber at both ends (at Panel Room as well as at Control room) along with FODP shall be in the scope of the contractor | Kindly confirm following :- a. New cabinet required for DPC or space shall be provided to mount DPC in existing cabinet. b. Distance between DPC and SDH at each station. c. Distance between DPC and Distance relay at each station. | a. Please refer reply to similar query above b & c :- Please refer clause 1.5 of Section project wherein it is mentioned that “The bidders are advised to visit the substation sites and acquaint themselves with the topography,infrastructure and also the design philosophy prior to bid.”
115 | Annexure-IV RCP_01 Ballabgarh |  | 2.Details of New DTPC required as per BPS to be integrated in Process Bus Based Scheme. 22 (11 – Ballabgarh, 11– Remote end) Both channels of 400kV Ballabgarh-Mainpuri-1 & 2, Gurgaon, Dadri, Nawada and One Channel of Agra - 1 3. Details of existing DTPC (Make & Bay No) to be integrated in Process Bus Based Scheme. 1 nos. Hitachi NSD 70 Agra 2 nos. Hitachi NSD 70 (One for each Line) Tughlakabad-1 & 2 Existing PLCC shall be Used. Maharani bagh 6 nos. Valiant Make Kanpur-1,2,3 (2 nos. valiant in each line) | a. Quantity mentioned in BOQ and quantity mentioned in annexure is different. b. Quantity of new DTPC not matching with line details provided for new DTPC. c. kindly exclude any type of work in existing system. | A&B. Kindly refer amendment 1 C: Bidder to quote as per provisions of bidding documents.
116 | Annexure-IV RCP_01 Hissar |  | 2.Details of New DTPC required as per BPS to be integrated in Process Bus Based Scheme. 16 (08 – Hissar, 08 – remote end) 400kV Hissar-Bhiwadi-1, Hissar-Fatehabad, Hissar-Moga-1, Hissar-BBMB Bhiwani 3. Details of existing DTPC (Make & Bay No) to be integrated in Process Bus Based Scheme. 6 nos. Alstom e-terra gridcom DIP One channel each for Bhiwani-1,2 & 3 and Moga-1,2&3. Existing PLCC shall be used for other lines. | a. Quantity mentioned in BOQ and quantity mentioned in annexure is different. b. Quantity of new DTPC not matching with line details provided for new DTPC. c. kindly exclude any type of work in existing system. | Bidder to quote as per provisions of bidding documents.
117 | Annexure - S8 : Specification of Digital Protection coupler |  |  | Specification is of normal DPC without Goose, where as relay is process bus based for local end, kindly clarify medium of communication between relay and DPC at local end and remote ends. | Please refer reply to similar query above
118 | 3. Details of existing DTPC (Make & Bay No) to be integrated in Process Bus Based Scheme. |  |  | We understand all existing PLCC and DPC is with contact transfer based interface for Relay trip communication, also Goose is not supported in major existing equipment, hence kindly let us know solution desired for connecting existing equipment with relay, can we provide contact transfer based interface in relay for PLCC and DPC communication? | Please refer reply to similar query above